## BIL VDC_1
Libellés | Description | Type | Cablé | Nature | Zone | Subsys | PCP | Ast. | Unit | Conv | Min | Max | Low1 | High1 | Low2 | High2 | Equal | Psec | Aut. | Inhibited (YES/NO) | Repos | Imp. | Group | AutCmd | Precondition | Dead Band Value | Dead Band Perc | Alarm Persist Value (sec) | Op | FORM | Calc | MasterAl | DRIVER | Acq Cycle (ms) | Validity | Syno | Node | Origin | FieldID | SlaveID | Field Function | FieldReg | FieldBIT | FEReg | FEBIT | FEIndex ADS | FEOffset ADS | FEBIT ADS | FE Module | FE PIN | DATA TYPE | VALUE | Commenti/note | CL8 | TP REF
ZJT6103CA | COMMANDE ACTIVER/DESACTIVER RESET FRONTAL SLAVE - U8(2),ACTIVER RESET(0) / U8(2),DESACTIVER RESET(1) | CT | N | INT | 0 | Z | [26 empty] | NOT |  |  | VMC01 | VMC (Z) | BIL | 0 |  |  |  |  | 12314 | 0 | 16416 | 50 | 0 |  |  | U8 | 0
ZJT6103CM | COMMANDE ACTIVER/DESACTIVER RESET FRONTAL SLAVE - U8(2),ACTIVER RESET(0) / U8(2),DESACTIVER RESET(1) | CT | N | INT | 0 | Z | [26 empty] | NOT |  |  | VMC01 | VMC (Z) | BIL | 0 |  |  |  |  | 12314 | 0 | 16416 | 50 | 0 |  |  | U8 | 1
ZJF9103 | BIL BIL PLC_Master | CR | N | INT | 0 | Z | [26 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12289 | 0 | 16416 | 0 | 0 |  |  |  | UINT |  | variabile letta dallo SCADA per stabilire chi è master
ZJM9103CM | BIL CMD MODE OPE. VMC FRONTAUX - U16(4), MANUAL(1) / U16(4), AUTO(2) | CT | N | INT | 0 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12290 | 0 | 16416 | 2 | 0 |  |  |  | UINT | 1 | comando scritto dallo SCADA che descrive la modalità di funzionamento manuale
ZJM9103CA | BIL CMD MODE OPE. VMC FRONTAUX - U16(4), MANUAL(1) / U16(4), AUTO(2) | CT | N | INT | 0 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12290 | 0 | 16416 | 2 | 0 |  |  |  | UINT | 2 | comando scritto dallo SCADA che descrive la modalità di funzionamento automatica
ZJN9103COM | BIL CMD BASCULAMENT VMC FRONTAUX | CT | N | INT | 0 | Z | [12 empty] | Z | NO |  |  |  |  | ZJM9103 ('Manual') | [7 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12291 | 0 | 16416 | 4 | 0 |  |  |  | UINT | 1 | comando inviato dall'operatore tramite SCADA = 1 plc master
ZJN9103COS | BIL CMD BASCULAMENT VMC FRONTAUX | CT | N | INT | 0 | Z | [12 empty] | Z | NO |  |  |  |  | ZJM9103 ('Manual') | [7 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12291 | 0 | 16416 | 4 | 0 |  |  |  | UINT | 2 | comando inviato dall'operatore tramite SCADA = 2 plc slave
ZJG9103 | BIL plc2_heartbeat | CR | N | INT | 0 | Z | [26 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12292 | 0 | 16416 | 6 | 0 |  |  |  | BOOL |  | Varaibile collegata all'heartbeat del secondo PLC. In condizioni nominali deve variare tra 1 e 0.
ZJK9103 | BIL PLC_Forced | CR | N | INT | 0 | Z | [26 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12293 | 0 | 16416 | 8 | 0 |  |  |  | UINT |  | variabile scritta dallo SCADA per forzare il plc a master
ZJL9103 | BIL PLC_Master_Name | MA | N | INT | 0 | Z | [26 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12294 | 0 | 16416 | 10 | 0 |  |  |  | STRING(12) |  | nome del PLC master
ZJR9103 | BIL PLC_Number | MA | N | INT | 0 | Z | [26 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12301 | 0 | 16416 | 24 | 0 |  |  |  | STRING(10) |  | variabile che identifica il nome del PLC
ZJM9103 | BIL PLC_Op_Mode | AL | N | INT | 0 | Z | [9 empty] | x==1 |  |  | Z | [13 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12301 | 0 | 16416 | 24 | 0 |  |  |  | UINT |  | variabile che se pari a 1 indica modalità manuale, se 2 modalità automatica, precond per be master/slave
ZJM9103 | BIL PLC_Op_Mode | AL | N | INT | 0 | Z | [9 empty] | x==1 |  |  | Z | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12301 | 0 | 16416 | 24 | 0 |  |  |  | UINT |  | variabile che se pari a 1 indica modalità manuale, se 2 modalità automatica, precond per be master/slave
ZJP9103 | BIL Master_PLC_Status | AL | N | INT | 0 | Z |  | R | [10 empty] | Z | [13 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12302 | 0 | 16416 | 26 | 0 |  |  |  | BOOL |  | variabile booleana che identifica lo stato del PLC corrente
ZJS9103 | BIL Slave_PLC_Status | AL | N | INT | 0 | Z |  | R | [10 empty] | Z | [13 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12303 | 0 | 16416 | 28 | 0 |  |  |  | BOOL |  | variabile booleana che identifica lo stato dell'altro PLC
ZJX9103 | BIL Keep_alive | CR | N | INT | 0 | Z | [26 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12311 | 0 | 16416 | 44 | 0 |  |  |  | UINT |  | variabile che indica se il PLC è freezato o sta funzionando
SFE94010D | BIL ByPass Feu Bicolore Hall Intégration Niv. 0 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 0 | 16416 | 222 | 0 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 1 | 16416 | 222 | 1
SFE94020D | BIL ByPass Feu Bicolore Hall Intégration Niv. 1 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 2 | 16416 | 222 | 2 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 3 | 16416 | 222 | 3
SFE94030D | BIL ByPass Feu Bicolore Hall Intégration Niv. 2 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 4 | 16416 | 222 | 4 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 5 | 16416 | 222 | 5
SFE94040D | BIL ByPass Feu Bicolore Hall Intégration Niv. 3 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 6 | 16416 | 222 | 6 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 7 | 16416 | 222 | 7
SFE94050D | BIL ByPass Feu Bicolore Hall Intégration Niv. 4 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 8 | 16416 | 223 | 0 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 9 | 16416 | 223 | 1
SFE94060D | BIL ByPass Feu Bicolore Hall Intégration Niv. 5 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 10 | 16416 | 223 | 2 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 11 | 16416 | 223 | 3
SFE94070D | BIL ByPass Feu Bicolore Hall Intégration Niv. 6 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 12 | 16416 | 223 | 4 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 13 | 16416 | 223 | 5
SFE94080D | BIL ByPass Feu Bicolore Hall Intégration Niv. 7 | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12400 | 14 | 16416 | 223 | 6 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12400 | 15 | 16416 | 223 | 7
SFE92512D | BIL ByPass Feu Bicolore Hall Intégration Niv. 25.120 (VEGA C) | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12401 | 0 | 16416 | 224 | 0 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12401 | 1 | 16416 | 224 | 1
SFE92792D | BIL ByPass Feu Bicolore Hall Intégration Niv. 27.920 (VEGA C) | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12401 | 2 | 16416 | 224 | 2 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12401 | 3 | 16416 | 224 | 3
SFE93332D | BIL ByPass Feu Bicolore Hall Intégration Niv. 33.320 (VEGA C) | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12401 | 4 | 16416 | 224 | 4 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12401 | 5 | 16416 | 224 | 5
SFE93682D | BIL ByPass Feu Bicolore Hall Intégration Niv. 36.820 (VEGA C) | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12401 | 6 | 16416 | 224 | 6 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12401 | 7 | 16416 | 224 | 7
SFE94082D | BIL ByPass Feu Bicolore Hall Intégration Niv. 40.820 (VEGA E) | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12401 | 8 | 16416 | 225 | 0 |  |  | BITVAL
VALIDITY | VALIDITY |  |  |  | 0 | [38 empty] | 12401 | 9 | 16416 | 225 | 1
SFE94457D | BIL ByPass Feu Bicolore Hall Intégration Niv. 44.570 (VEGA E) | CR | N | INT | 0 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12401 | 10 | 16416 | 225 | 2 |  |  | BITVAL
VALIDITY | VALIDITY | [42 empty] | 12401 | 11 | 16416 | 225 | 3
SCE94001CQMM | BIL CDE SON MODULé ALERT EVACUATION CENTRALE BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 0 | 16416 | 422 | 0 | EL2869_M013 | 1 | U8 | 1 | calling MG90
| Not Used | CT | O | FIL | 4 | S | [13 empty] | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 1 | 16416 | 422 | 1 | EL2869_M013 | 1 | U8 | 2 | calling MG90
SCE94001CQCM | BIL CDE SON CONTINU ALERT EVACUATION CENTRALE BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 2 | 16416 | 422 | 2 | EL2869_M013 | 2 | U8 | 4 | calling MG90
SCE94001CQA | BIL CDE ARRET SON ALERT EVACUATION CENTRALE BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 3 | 16416 | 422 | 3 | EL2869_M013 | 2 | U8 | 8 | calling MG90
SFE92512CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 25120 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 4 | 16416 | 422 | 4 | EL2869_M013 | 3 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 5 | 16416 | 422 | 5 | N/A | N/A | U8 | 32
SFE92512CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 25120 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 6 | 16416 | 422 | 6 | EL2869_M013 | 4 | U8 | 64 | calling MG91
SFE92512CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 25120 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 7 | 16416 | 422 | 7 | EL2869_M013 | N/A | U8 | 128 | calling MG91
SFE92792CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 27920 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 8 | 16416 | 423 | 0 | EL2869_M013 | 5 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 9 | 16416 | 423 | 1 | N/A | N/A | U8 | 2
SFE92792CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 27920 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 10 | 16416 | 423 | 2 | EL2869_M013 | 6 | U8 | 4 | calling MG91
SFE92792CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 27920 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 11 | 16416 | 423 | 3 | EL2869_M013 | N/A | U8 | 8 | calling MG91
SFE93332CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 33320 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 12 | 16416 | 423 | 4 | EL2869_M013 | 7 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 13 | 16416 | 423 | 5 | N/A | N/A | U8 | 32
SFE93332CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 33320 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 14 | 16416 | 423 | 6 | EL2869_M013 | 8 | U8 | 64 | calling MG91
SFE93332CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 33320 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12500 | 15 | 16416 | 423 | 7 | EL2869_M013 | N/A | U8 | 128 | calling MG91
SFE93682CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 36820 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 0 | 16416 | 424 | 0 | EL2869_M013 | 9 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 1 | 16416 | 424 | 1 | N/A | N/A | U8 | 2
SFE93682CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 36820 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 2 | 16416 | 424 | 2 | EL2869_M013 | 10 | U8 | 4 | calling MG91
SFE93682CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 36820 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 3 | 16416 | 424 | 3 | EL2869_M013 | N/A | U8 | 8 | calling MG91
SFE94082CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 40820 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 4 | 16416 | 424 | 4 | EL2869_M013 | 11 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 5 | 16416 | 424 | 5 | N/A | N/A | U8 | 32
SFE94082CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 40820 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 6 | 16416 | 424 | 6 | EL2869_M013 | 12 | U8 | 64 | calling MG91
SFE94082CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 40820 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 7 | 16416 | 424 | 7 | EL2869_M013 | N/A | U8 | 128 | calling MG91
SFE94457CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 44570 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 8 | 16416 | 425 | 0 | EL2869_M013 | 13 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 9 | 16416 | 425 | 1 | N/A | N/A | U8 | 2
SFE94457CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 44570 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 10 | 16416 | 425 | 2 | EL2869_M013 | 14 | U8 | 4 | calling MG91
SFE94457CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 44570 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 11 | 16416 | 425 | 3 | EL2869_M013 | N/A | U8 | 8 | calling MG91
SFE9001CRM | CDE FEUX ROUGE ACCESS BIL - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 12 | 16416 | 425 | 4 | EL2869_M013 | 15 | U8 | 16
SFE9001CRA | CDE FEUX ROUGE ACCESS BIL - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 13 | 16416 | 425 | 5 | EL2869_M013 | 15 | U8 | 32
SFE9002COM | CDE FEUX ORANGE ACCESS BIL - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 14 | 16416 | 425 | 6 | EL2869_M013 | 16 | U8 | 64
SFE9002COA | CDE FEUX ORANGE ACCESS BIL - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12501 | 15 | 16416 | 425 | 7 | EL2869_M013 | 16 | U8 | 128
SFE94010CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 0 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 0 | 16416 | 426 | 0 | EL2869_M014 | 1 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 1 | 16416 | 426 | 1 | N/A | N/A | U8 | 2
SFE94010CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 0 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 2 | 16416 | 426 | 2 | EL2869_M014 | 2 | U8 | 4 | calling MG91
SFE94010CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 0 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 3 | 16416 | 426 | 3 | EL2869_M014 | N/A | U8 | 8 | calling MG91
SFE94020CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 1 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 4 | 16416 | 426 | 4 | EL2869_M014 | 3 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 5 | 16416 | 426 | 5 | N/A | N/A | U8 | 32
SFE94020CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 1 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 6 | 16416 | 426 | 6 | EL2869_M014 | 4 | U8 | 64 | calling MG91
SFE94020CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 1 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 7 | 16416 | 426 | 7 | EL2869_M014 | N/A | U8 | 128 | calling MG91
SFE94030CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 2 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 8 | 16416 | 427 | 0 | EL2869_M014 | 5 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 9 | 16416 | 427 | 1 | N/A | N/A | U8 | 2
SFE94030CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 2 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 10 | 16416 | 427 | 2 | EL2869_M014 | 6 | U8 | 4 | calling MG91
SFE94030CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 2 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 11 | 16416 | 427 | 3 | EL2869_M014 | N/A | U8 | 8 | calling MG91
SFE94040CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 3 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 12 | 16416 | 427 | 4 | EL2869_M014 | 7 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 13 | 16416 | 427 | 5 | N/A | N/A | U8 | 32
SFE94040CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 3 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 14 | 16416 | 427 | 6 | EL2869_M014 | 8 | U8 | 64 | calling MG91
SFE94040CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 3 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12502 | 15 | 16416 | 427 | 7 | EL2869_M014 | N/A | U8 | 128 | calling MG91
SFE94050CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 4 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 0 | 16416 | 428 | 0 | EL2869_M014 | 9 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 1 | 16416 | 428 | 1 | N/A | N/A | U8 | 2
SFE94050CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 4 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 2 | 16416 | 428 | 2 | EL2869_M014 | 10 | U8 | 4 | calling MG91
SFE94050CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 4 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 3 | 16416 | 428 | 3 | EL2869_M014 | N/A | U8 | 8 | calling MG91
SFE94060CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 5 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 4 | 16416 | 428 | 4 | EL2869_M014 | 11 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 5 | 16416 | 428 | 5 | N/A | N/A | U8 | 32
SFE94060CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 5 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 6 | 16416 | 428 | 6 | EL2869_M014 | 12 | U8 | 64 | calling MG91
SFE94060CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 5 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 7 | 16416 | 428 | 7 | EL2869_M014 | N/A | U8 | 128 | calling MG91
SFE94070CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 6 BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 8 | 16416 | 429 | 0 | EL2869_M014 | 13 | U8 | 1 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 9 | 16416 | 429 | 1 | N/A | N/A | U8 | 2
SFE94070CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 6 BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 10 | 16416 | 429 | 2 | EL2869_M014 | 14 | U8 | 4 | calling MG91
SFE94070CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 6 BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 11 | 16416 | 429 | 3 | EL2869_M014 | N/A | U8 | 8 | calling MG91
SFE94080CQRM | CDE FEUX ROUGE HALL INTéGRATION NIV. 7 BIL - U8(2),MARCHE(16) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 12 | 16416 | 429 | 4 | EL2869_M014 | 15 | U8 | 16 | calling MG91
| Not Used | [17 empty] | S | NO | [15 empty] | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 13 | 16416 | 429 | 5 | N/A | N/A | U8 | 32
SFE94080CQOM | CDE FEUX ORANGE HALL INTéGRATION NIV. 7 BIL - U8(2),MARCHE(64) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 14 | 16416 | 429 | 6 | EL2869_M014 | 16 | U8 | 64 | calling MG91
SFE94080CQA | CDE ARRET FEUX HALL INTéGRATION NIV. 7 BIL - U8(2),ARRET(128) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12503 | 15 | 16416 | 429 | 7 | EL2869_M014 | N/A | U8 | 128 | calling MG91
SFE9003CVM | CDE FEUX VERT ACCESS BIL - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12504 | 0 | 16416 | 430 | 0 | EL2869_M015 | 1 | U8 | 1
SFE9003CVA | CDE FEUX VERT ACCESS BIL - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12504 | 1 | 16416 | 430 | 1 | EL2869_M015 | 1 | U8 | 2
SFE9004CCM | CDE FEUX ROUGE CLIGNOTANT ACCESS BIL - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12504 | 2 | 16416 | 430 | 2 | EL2869_M015 | 2 | U8 | 4
SFE9004CCA | CDE FEUX ROUGE CLIGNOTANT ACCESS BIL - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12504 | 3 | 16416 | 430 | 3 | EL2869_M015 | 2 | U8 | 8
SST9001CF | CDE BARRIERE ACCESS BIL - U8(2),FERMATURE (16) / U8(2),OUVERTURE(32) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12504 | 4 | 16416 | 430 | 4 | EL2869_M015 | 3 | U8 | 16
SST9001CO | CDE BARRIERE ACCESS BIL - U8(2),FERMATURE (16) / U8(2),OUVERTURE(32) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12504 | 5 | 16416 | 430 | 5 | EL2869_M015 | 3 | U8 | 32
SPAFCT0001 | BIL SPARE FIL DIGITAL OUTPUT 0001 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 6 | 16416 | 430 | 6 | EL2869_M015 | 4 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 7 | 16416 | 430 | 7 | N/A | N/A | U8 | 128
SPAFCT0002 | BIL SPARE FIL DIGITAL OUTPUT 0002 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 8 | 16416 | 431 | 0 | EL2869_M015 | 5 | U8 | 1
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 9 | 16416 | 431 | 1 | N/A | N/A | U8 | 2
SPAFCT0003 | BIL SPARE FIL DIGITAL OUTPUT 0003 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 10 | 16416 | 431 | 2 | EL2869_M015 | 6 | U8 | 4
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 11 | 16416 | 431 | 3 | N/A | N/A | U8 | 8
SPAFCT0004 | BIL SPARE FIL DIGITAL OUTPUT 0004 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 12 | 16416 | 431 | 4 | EL2869_M015 | 7 | U8 | 16
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 13 | 16416 | 431 | 5 | N/A | N/A | U8 | 32
SPAFCT0005 | BIL SPARE FIL DIGITAL OUTPUT 0005 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 14 | 16416 | 431 | 6 | EL2869_M015 | 8 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12504 | 15 | 16416 | 431 | 7 | N/A | N/A | U8 | 128
SPAFCT0006 | BIL SPARE FIL DIGITAL OUTPUT 0006 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 0 | 16416 | 432 | 0 | EL2869_M015 | 9 | U8 | 1
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 1 | 16416 | 432 | 1 | N/A | N/A | U8 | 2
SPAFCT0007 | BIL SPARE FIL DIGITAL OUTPUT 0007 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 2 | 16416 | 432 | 2 | EL2869_M015 | 10 | U8 | 4
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 3 | 16416 | 432 | 3 | N/A | N/A | U8 | 8
SPAFCT0008 | BIL SPARE FIL DIGITAL OUTPUT 0008 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 4 | 16416 | 432 | 4 | EL2869_M015 | 11 | U8 | 16
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 5 | 16416 | 432 | 5 | N/A | N/A | U8 | 32
SPAFCT0009 | BIL SPARE FIL DIGITAL OUTPUT 0009 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 6 | 16416 | 432 | 6 | EL2869_M015 | 12 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 7 | 16416 | 432 | 7 | N/A | N/A | U8 | 128
SPAFCT0010 | BIL SPARE FIL DIGITAL OUTPUT 0010 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 8 | 16416 | 433 | 0 | EL2869_M015 | 13 | U8 | 1
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 9 | 16416 | 433 | 1 | N/A | N/A | U8 | 2
SPAFCT0011 | BIL SPARE FIL DIGITAL OUTPUT 0011 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 10 | 16416 | 433 | 2 | EL2869_M015 | 14 | U8 | 4
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 11 | 16416 | 433 | 3 | N/A | N/A | U8 | 8
SPAFCT0012 | BIL SPARE FIL DIGITAL OUTPUT 0012 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 12 | 16416 | 433 | 4 | EL2869_M015 | 15 | U8 | 16
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 13 | 16416 | 433 | 5 | N/A | N/A | U8 | 32
SPAFCT0013 | BIL SPARE FIL DIGITAL OUTPUT 0013 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 14 | 16416 | 433 | 6 | EL2869_M015 | 16 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12505 | 15 | 16416 | 433 | 7 | N/A | N/A | U8 | 128
SPAFCT0014 | BIL SPARE FIL DIGITAL OUTPUT 0014 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [15 empty] | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12506 | 0 | 16416 | 434 | 0 | EL2869_M016 | 1 | U8 | 1
| Not Used | [17 empty] | S | NO | [15 empty] | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12506 | 1 | 16416 | 434 | 1 | N/A | 1 | U8 | 2
SPAFCT0015 | BIL SPARE FIL DIGITAL OUTPUT 0015 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [15 empty] | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12506 | 2 | 16416 | 434 | 2 | EL2869_M016 | 2 | U8 | 4
| Not Used | [17 empty] | S | NO | [15 empty] | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 12506 | 3 | 16416 | 434 | 3 | N/A | 2 | U8 | 8
SPAFCT0016 | BIL SPARE FIL DIGITAL OUTPUT 0016 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12506 | 4 | 16416 | 434 | 4 | EL2869_M016 | 3 | U8 | 16
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12506 | 5 | 16416 | 434 | 5 | N/A | 3 | U8 | 32
SPAFCT0017 | BIL SPARE FIL DIGITAL OUTPUT 0017 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12506 | 6 | 16416 | 434 | 6 | EL2869_M016 | 4 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12506 | 7 | 16416 | 434 | 7 | N/A | 4 | U8 | 128
SSP94001C10MM | CDE SON MODULé SIRèNE ALERT BIL - U8(2),MARCHE(1) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 8 | 16416 | 435 | 0 | EL2869_M016 | 5 | U8 | 1
| Not Used | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12506 | 9 | 16416 | 435 | 1 | EL2869_M016 | 5 | U8 | 2
SSP94001C20CM | CDE SON CONTINU SIRèNE ALERT BIL - U8(2),MARCHE(4) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 10 | 16416 | 435 | 2 | EL2869_M016 | 6 | U8 | 4
SSP94001C20A | CDE ARRET SON SIRèNE ALERT BIL - U8(2),ARRET(8) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 11 | 16416 | 435 | 3 | EL2869_M016 | 6 | U8 | 8
SST94002CF | CDE PORTE à COTE DU BIL - U8(2),FERMATURE (16) / U8(2),OUVERTURE(32) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 12 | 16416 | 435 | 4 | EL2869_M016 | 7 | U8 | 16
SST94002CO | CDE PORTE à COTE DU BIL - U8(2),FERMATURE (16) / U8(2),OUVERTURE(32) | CT | O | FIL | 4 | S | [12 empty] | S | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 13 | 16416 | 435 | 5 | EL2869_M016 | 7 | U8 | 32
ZJU9024CA | BIL CDE ENABLE +24VDC FEEDING - U8(2), ACTVER (64)/U8(2) DESACTIVER(128) | CT | O | FIL | 4 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 14 | 16416 | 435 | 6 | EL2869_M016 | 8 | U8 | 64
ZJU9024CM | BIL CDE ENABLE +24VDC FEEDING - U8(2), ACTVER (64)/U8(2) DESACTIVER(128) | CT | O | FIL | 4 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12506 | 15 | 16416 | 435 | 7 | EL2869_M016 | 8 | U8 | 128
ZJU9048CA | BIL CDE ENABLE +48VDC FEEDING - U8(2), ACTVER (1)/U8(2) DESACTIVER(2) | CT | O | FIL | 4 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12507 | 0 | 16416 | 436 | 0 | EL2869_M016 | 9 | U8 | 1
ZJU9048CM | BIL CDE ENABLE +48VDC FEEDING - U8(2), ACTVER (1)/U8(2) DESACTIVER(2) | CT | O | FIL | 4 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 12507 | 1 | 16416 | 436 | 1 | EL2869_M016 | 9 | U8 | 2
SPAFCT0018 | BIL SPARE FIL DIGITAL OUTPUT 0018 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 2 | 16416 | 436 | 2 | EL2869_M016 | 10 | U8 | 4
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 3 | 16416 | 436 | 3 | N/A | N/A | U8 | 8
SPAFCT0019 | BIL SPARE FIL DIGITAL OUTPUT 0019 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 4 | 16416 | 436 | 4 | EL2869_M016 | 11 | U8 | 16
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 5 | 16416 | 436 | 5 | N/A | N/A | U8 | 32
SPAFCT0020 | BIL SPARE FIL DIGITAL OUTPUT 0020 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 6 | 16416 | 436 | 6 | EL2869_M016 | 12 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 7 | 16416 | 436 | 7 | N/A | N/A | U8 | 128
SPAFCT0021 | BIL SPARE FIL DIGITAL OUTPUT 0021 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 8 | 16416 | 437 | 0 | EL2869_M016 | 13 | U8 | 1
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 9 | 16416 | 437 | 1 | N/A | N/A | U8 | 2
SPAFCT0022 | BIL SPARE FIL DIGITAL OUTPUT 0022 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 10 | 16416 | 437 | 2 | EL2869_M016 | 14 | U8 | 4
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 11 | 16416 | 437 | 3 | N/A | N/A | U8 | 8
SPAFCT0023 | BIL SPARE FIL DIGITAL OUTPUT 0023 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 12 | 16416 | 437 | 4 | EL2869_M016 | 15 | U8 | 16
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 13 | 16416 | 437 | 5 | N/A | N/A | U8 | 32
SPAFCT0024 | BIL SPARE FIL DIGITAL OUTPUT 0024 | CT | O | FIL | 4 | S | [12 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 14 | 16416 | 437 | 6 | EL2869_M016 | 16 | U8 | 64
| Not Used | [17 empty] | S | NO | [17 empty] | BIL | 12 |  |  |  |  | 12507 | 15 | 16416 | 437 | 7 | N/A | N/A | U8 | 128
ESY92012D | BIL Départ TGBT CAT3A | CR | O | FIL | 4 | E | [26 empty] | NOT |  |  | E90 | Energy TGBT et UPS (E) | BIL | 12 |  |  |  |  | 13289 | 0 | 16416 | 2000 | 0 | EL1134_M002 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13289 | 1 | 16416 | 2000 | 1
ESY92016D | BIL Départ TD CAT3 | CR | O | FIL | 4 | E | [26 empty] | NOT |  |  | E90 | Energy TGBT et UPS (E) | BIL | 12 |  |  |  |  | 13289 | 2 | 16416 | 2000 | 2 | EL1134_M002 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13289 | 3 | 16416 | 2000 | 3
ESY92014D | BIL Départ TGBT CAT3B | CR | O | FIL | 4 | E | [26 empty] | NOT |  |  | E90 | Energy TGBT et UPS (E) | BIL | 12 |  |  |  |  | 13289 | 4 | 16416 | 2000 | 4 | EL1134_M002 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13289 | 5 | 16416 | 2000 | 5
ESY94651D | BIL Départ TD CAT3 ESC | CR | O | FIL | 4 | E | [26 empty] | NOT |  |  | E90 | Energy TGBT et UPS (E) | BIL | 12 |  |  |  |  | 13289 | 6 | 16416 | 2000 | 6 | EL1134_M002 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13289 | 7 | 16416 | 2000 | 7
SCE94001D | BIL Défaut centrale | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13289 | 0 | 16416 | 2001 | 0 | EL1134_M003 | I1 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13289 | 9 | 16416 | 2001 | 1
SCE94001M | BIL Déclenchement evacuation en local | AL | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13289 | 10 | 16416 | 2001 | 2 | EL1134_M003 | I2 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13289 | 11 | 16416 | 2001 | 3
SCE94001DM | BIL Défaut carte son continu | CR | O | FIL | 4 | S | [12 empty] | S | [13 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13289 | 12 | 16416 | 2001 | 4 | EL1134_M003 | I3 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13289 | 13 | 16416 | 2001 | 5
SCE94001S | BIL Marche son modulé - AE | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13289 | 14 | 16416 | 2001 | 6 | EL1134_M003 | I4 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13289 | 15 | 16416 | 2001 | 7
SCE94001U | BIL Marche son continu - AR | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13290 | 0 | 16416 | 2002 | 0 | EL1134_M004 | I1 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13290 | 1 | 16416 | 2002 | 1
SSP94001QA | BIL Sirène Alerte Arrêt son | CR | O | FIL | 4 | S | [12 empty] | S | [13 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13290 | 2 | 16416 | 2002 | 2 | EL1134_M004 | I2 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13290 | 3 | 16416 | 2002 | 3
SSP94001D | BIL Sirène Alerte Défaut | AL | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13290 | 4 | 16416 | 2002 | 4 | EL1134_M004 | I3 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13290 | 5 | 16416 | 2002 | 5
SSP94001QC | BIL Sirène Alerte son continu | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13290 | 6 | 16416 | 2002 | 6 | EL1134_M004 | I4 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13290 | 7 | 16416 | 2002 | 7
SSP94001QM | BIL Sirène Alerte son modulé | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13290 | 8 | 16416 | 2003 | 0 | EL1134_M005 | I1 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13290 | 9 | 16416 | 2003 | 1
SCK94001W | BIL Central Détection Incendie Synthèse Alarmes | AL | O | FIL | 4 | S | [12 empty] | S | [13 empty] | NOT |  |  | DI94 | DETIN (DI) | BIL | 12 |  |  |  |  | 13290 | 10 | 16416 | 2003 | 2 | EL1134_M005 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13290 | 11 | 16416 | 2003 | 3
SCK94001D | BIL Central Détection Incendie Synthèse Dèfauts | AL | O | FIL | 4 | S | [12 empty] | S | [13 empty] | NOT |  |  | DI94 | DETIN (DI) | BIL | 12 |  |  |  |  | 13290 | 12 | 16416 | 2003 | 4 | EL1134_M005 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13290 | 13 | 16416 | 2003 | 5
SST94002O | BIL Porte à côté du SAS | CR | O | FIL | 4 | [27 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13290 | 14 | 16416 | 2003 | 6 | EL1134_M005 | I4 | BITVAL |  | calling MG90
VALIDITY | VALIDITY | [42 empty] | 13290 | 15 | 16416 | 2003 | 7
SDO9000D | BIL Central Détection Gas Synthèse Dèfauts | AL | O | FIL | 4 | S | [12 empty] | S | [13 empty] | NOT |  |  |  |  | BIL | 12 |  |  |  |  | 13291 | 0 | 16416 | 2004 | 0 | EL1134_M006 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13291 | 1 | 16416 | 2004 | 1
DG9000DMA | MASTER ALARM DETIN GAS BIL | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SDO9000D; SDO9000W | Y |  |  |  | DETIN DI BIL | Detection Incendie (DI) | BIL
SCK69000DMA | MASTER ALARM DETIN | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCK6000DMA; SCK9000DMA | Y |  |  |  | DETIN DI (group) | Detection Incendie (DI) | BIL
SFE94010M | BIL Feu Bicolore Hall Intégration Niv. 0 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 2 | 16416 | 2004 | 2 | EL1134_M006 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 3 | 16416 | 2004 | 3
SDO9000W | BIL Central Détection Gas Synthèse Alarmes | AL | O | FIL | 4 | S | [26 empty] | NOT |  |  |  | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 4 | 16416 | 2004 | 4 | EL1134_M006 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 5 | 16416 | 2004 | 5
SFE94011M | BIL Feu Bicolore Hall Intégration Niv. 0 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 6 | 16416 | 2004 | 6 | EL1134_M006 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 7 | 16416 | 2004 | 7
SFE94020M | BIL Feu Bicolore Hall Intégration Niv. 1 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 8 | 16416 | 2005 | 0 | EL1134_M007 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 9 | 16416 | 2005 | 1
SFE94030M | BIL Feu Bicolore Hall Intégration Niv. 2 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 10 | 16416 | 2005 | 2 | EL1134_M007 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 11 | 16416 | 2005 | 3
SFE94021M | BIL Feu Bicolore Hall Intégration Niv. 1 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 12 | 16416 | 2005 | 4 | EL1134_M007 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 13 | 16416 | 2005 | 5
SFE94031M | BIL Feu Bicolore Hall Intégration Niv. 2 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13291 | 14 | 16416 | 2005 | 6 | EL1134_M007 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13291 | 15 | 16416 | 2005 | 7
SFE94040M | BIL Feu Bicolore Hall Intégration Niv. 3 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 0 | 16416 | 2006 | 0 | EL1134_M008 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 1 | 16416 | 2006 | 1
SFE94050M | BIL Feu Bicolore Hall Intégration Niv. 4 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 2 | 16416 | 2006 | 2 | EL1134_M008 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 3 | 16416 | 2006 | 3
SFE94041M | BIL Feu Bicolore Hall Intégration Niv. 3 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 4 | 16416 | 2006 | 4 | EL1134_M008 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 5 | 16416 | 2006 | 5
SFE94051M | BIL Feu Bicolore Hall Intégration Niv. 4 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 6 | 16416 | 2006 | 6 | EL1134_M008 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 7 | 16416 | 2006 | 7
SFE94060M | BIL Feu Bicolore Hall Intégration Niv. 5 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 8 | 16416 | 2007 | 0 | EL1134_M009 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 9 | 16416 | 2007 | 1
SFE94070M | BIL Feu Bicolore Hall Intégration Niv. 6 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 10 | 16416 | 2007 | 2 | EL1134_M009 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 11 | 16416 | 2007 | 3
SFE94061M | BIL Feu Bicolore Hall Intégration Niv. 5 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 12 | 16416 | 2007 | 4 | EL1134_M009 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 13 | 16416 | 2007 | 5
SFE94071M | BIL Feu Bicolore Hall Intégration Niv. 6 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13292 | 14 | 16416 | 2007 | 6 | EL1134_M009 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13292 | 15 | 16416 | 2007 | 7
SFE94080M | BIL Feu Bicolore Hall Intégration Niv. 7 Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 0 | 16416 | 2008 | 0 | EL1134_M010 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 1 | 16416 | 2008 | 1
SSP94001C10M | Son Modulé Sirène ALERT BIL | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 2 | 16416 | 2008 | 2 | EL1134_M010 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 3 | 16416 | 2008 | 3
SFE94081M | BIL Feu Bicolore Hall Intégration Niv. 6 Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 4 | 16416 | 2008 | 4 | EL1134_M010 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 5 | 16416 | 2008 | 5
SSP94001C20M | Son Continu Sirène ALERT BIL | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 6 | 16416 | 2008 | 6 | EL1134_M010 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 7 | 16416 | 2008 | 7
SFE92501M | BIL Feu Bicolore Hall Intégration Niv 25.120_R | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 8 | 16416 | 2009 | 0 | EL1134_M011 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 9 | 16416 | 2009 | 1
SFE92701M | BIL Feu Bicolore Hall Intégration Niv 27.120_R | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 10 | 16416 | 2009 | 2 | EL1134_M011 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 11 | 16416 | 2009 | 3
SFE92502M | BIL Feu Bicolore Hall Intégration Niv 25.120_O | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 12 | 16416 | 2009 | 4 | EL1134_M011 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 13 | 16416 | 2009 | 5
SFE92702M | BIL Feu Bicolore Hall Intégration Niv 27.120_O | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13293 | 14 | 16416 | 2009 | 6 | EL1134_M011 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13293 | 15 | 16416 | 2009 | 7
SFE93301M | BIL Feu Bicolore Hall Intégration Niv 33.120_R | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 0 | 16416 | 2010 | 0 | EL1134_M013 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13294 | 1 | 16416 | 2010 | 1
SFE93601M | BIL Feu Bicolore Hall Intégration Niv 36.120_R | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 2 | 16416 | 2010 | 2 | EL1134_M013 | I2 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13294 | 3 | 16416 | 2010 | 3
SFE93302M | BIL Feu Bicolore Hall Intégration Niv 33.120_O | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 4 | 16416 | 2010 | 4 | EL1134_M013 | I3 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13294 | 5 | 16416 | 2010 | 5
SFE93602M | BIL Feu Bicolore Hall Intégration Niv 36.120_O | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 6 | 16416 | 2010 | 6 | EL1134_M013 | I4 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13294 | 7 | 16416 | 2010 | 7
SFE94001M | BIL Feu Bicolore Hall Intégration Niv 40.120_R | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG90 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 8 | 16416 | 2011 | 0 | EL1134_M014 | I1 | BITVAL |  | calling MG91
VALIDITY | VALIDITY | [42 empty] | 13294 | 9 | 16416 | 2011 | 1
SFE94401M | BIL Feu Bicolore Hall Intégration Niv 44.120_R | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 10 | 16416 | 2011 | 2 | EL1134_M014 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13294 | 11 | 16416 | 2011 | 3
SFE94002M | BIL Feu Bicolore Hall Intégration Niv 40.120_O | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 12 | 16416 | 2011 | 4 | EL1134_M014 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13294 | 13 | 16416 | 2011 | 5
SFE94402M | BIL Feu Bicolore Hall Intégration Niv 44.120_O | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13294 | 14 | 16416 | 2011 | 6 | EL1134_M014 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13294 | 15 | 16416 | 2011 | 7
SFE9001M | BIL Feu Barrière Access Rouge | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13295 | 0 | 16416 | 2012 | 0 | EL1134_M015 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 1 | 16416 | 2012 | 1
SFE9003M | BIL Feu Barrière Access Vert | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13295 | 2 | 16416 | 2012 | 2 | EL1134_M015 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 3 | 16416 | 2012 | 3
SFE9002M | BIL Feu Barrière Access Orange | CR | O | FIL | 4 | S | [26 empty] | NOT |  |  | MG91 | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13295 | 4 | 16416 | 2012 | 4 | EL1134_M015 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 5 | 16416 | 2012 | 5
SFE9004M | BIL Feu Barrière Access Rouge Clignotant | CR | O | FIL | 4 | S | [26 empty] | NOT | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13295 | 6 | 16416 | 2012 | 6 | EL1134_M015 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 7 | 16416 | 2012 | 7
SST9001F | BIL Feu Barrière Access Fermée | CR | O | FIL | 4 | S | [26 empty] | NOT | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13295 | 8 | 16416 | 2013 | 0 | EL1134_M016 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 9 | 16416 | 2013 | 1
SPAFCR0001 | BIL SPARE FIL DIGITAL INPUT 0001 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13295 | 10 | 16416 | 2013 | 2 | EL1134_M016 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 11 | 16416 | 2013 | 3
SST9001O | BIL Feu Barrière Access Ouverte | CR | O | FIL | 4 | S | [26 empty] | NOT | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13295 | 12 | 16416 | 2013 | 4 | EL1134_M016 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 13 | 16416 | 2013 | 5
SPAFCR0002 | BIL SPARE FIL DIGITAL INPUT 0002 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13295 | 14 | 16416 | 2013 | 6 | EL1134_M016 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13295 | 15 | 16416 | 2013 | 7
SPAFCR0003 | BIL SPARE FIL DIGITAL INPUT 0003 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 0 | 16416 | 2014 | 0 | EL1134_M017 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 1 | 16416 | 2014 | 1
SPAFCR0005 | BIL SPARE FIL DIGITAL INPUT 0005 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 2 | 16416 | 2014 | 2 | EL1134_M017 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 3 | 16416 | 2014 | 3
SPAFCR0004 | BIL SPARE FIL DIGITAL INPUT 0004 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 4 | 16416 | 2014 | 4 | EL1134_M017 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 5 | 16416 | 2014 | 5
SPAFCR0006 | BIL SPARE FIL DIGITAL INPUT 0006 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 6 | 16416 | 2014 | 6 | EL1134_M017 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 7 | 16416 | 2014 | 7
SPAFCR0007 | BIL SPARE FIL DIGITAL INPUT 0007 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 8 | 16416 | 2015 | 0 | EL1134_M018 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 9 | 16416 | 2015 | 1
SPAFCR0009 | BIL SPARE FIL DIGITAL INPUT 0009 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 10 | 16416 | 2015 | 2 | EL1134_M018 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 11 | 16416 | 2015 | 3
SPAFCR0008 | BIL SPARE FIL DIGITAL INPUT 0008 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 12 | 16416 | 2015 | 4 | EL1134_M018 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 13 | 16416 | 2015 | 5
SPAFCR0010 | BIL SPARE FIL DIGITAL INPUT 0010 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13296 | 14 | 16416 | 2015 | 6 | EL1134_M018 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13296 | 15 | 16416 | 2015 | 7
SPAFCR0011 | BIL SPARE FIL DIGITAL INPUT 0011 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 0 | 16416 | 2016 | 0 | EL1134_M019 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 1 | 16416 | 2016 | 1
SPAFCR0013 | BIL SPARE FIL DIGITAL INPUT 0013 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 2 | 16416 | 2016 | 2 | EL1134_M019 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 3 | 16416 | 2016 | 3
SPAFCR0012 | BIL SPARE FIL DIGITAL INPUT 0012 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 4 | 16416 | 2016 | 4 | EL1134_M019 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 5 | 16416 | 2016 | 5
SPAFCR0014 | BIL SPARE FIL DIGITAL INPUT 0014 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 6 | 16416 | 2016 | 6 | EL1134_M019 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 7 | 16416 | 2016 | 7
SPAFCR0015 | BIL SPARE FIL DIGITAL INPUT 0015 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 8 | 16416 | 2017 | 0 | EL1134_M020 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 9 | 16416 | 2017 | 1
SSST94002O | Porte à coté du BIL Ouverte | CR | O | FIL | 4 | S | [26 empty] | NOT | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 10 | 16416 | 2017 | 2 | EL1134_M020 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 11 | 16416 | 2017 | 3
SPAFCR0016 | BIL SPARE FIL DIGITAL INPUT 0016 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 12 | 16416 | 2017 | 4 | EL1134_M020 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 13 | 16416 | 2017 | 5
SPAFCR0017 | BIL SPARE FIL DIGITAL INPUT 0017 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13297 | 14 | 16416 | 2017 | 6 | EL1134_M020 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13297 | 15 | 16416 | 2017 | 7
SPAFCR0018 | BIL SPARE FIL DIGITAL INPUT 0018 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 0 | 16416 | 2018 | 0 | EL1134_M021 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 1 | 16416 | 2018 | 1
SPAFCR0020 | BIL SPARE FIL DIGITAL INPUT 0020 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 2 | 16416 | 2018 | 2 | EL1134_M021 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 3 | 16416 | 2018 | 3
SPAFCR0019 | BIL SPARE FIL DIGITAL INPUT 0019 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 4 | 16416 | 2018 | 4 | EL1134_M021 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 5 | 16416 | 2018 | 5
SPAFCR0021 | BIL SPARE FIL DIGITAL INPUT 0021 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 6 | 16416 | 2018 | 6 | EL1134_M021 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 7 | 16416 | 2018 | 7
SPAFCR0022 | BIL SPARE FIL DIGITAL INPUT 0022 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 8 | 16416 | 2019 | 0 | EL1134_M022 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 9 | 16416 | 2019 | 1
SPAFCR0024 | BIL SPARE FIL DIGITAL INPUT 0024 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 10 | 16416 | 2019 | 2 | EL1134_M022 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 11 | 16416 | 2019 | 3
SPAFCR0023 | BIL SPARE FIL DIGITAL INPUT 0023 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 12 | 16416 | 2019 | 4 | EL1134_M022 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 13 | 16416 | 2019 | 5
SPAFCR0025 | BIL SPARE FIL DIGITAL INPUT 0025 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13298 | 14 | 16416 | 2019 | 6 | EL1134_M022 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13298 | 15 | 16416 | 2019 | 7
SPAFCR0026 | BIL SPARE FIL DIGITAL INPUT 0026 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 0 | 16416 | 2020 | 0 | EL1134_M024 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 1 | 16416 | 2020 | 1
SPAFCR0028 | BIL SPARE FIL DIGITAL INPUT 0028 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 2 | 16416 | 2020 | 2 | EL1134_M024 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 3 | 16416 | 2020 | 3
SPAFCR0027 | BIL SPARE FIL DIGITAL INPUT 0027 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 4 | 16416 | 2020 | 4 | EL1134_M024 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 5 | 16416 | 2020 | 5
SPAFCR0029 | BIL SPARE FIL DIGITAL INPUT 0029 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 6 | 16416 | 2020 | 6 | EL1134_M024 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 7 | 16416 | 2020 | 7
SPAFCR0030 | BIL SPARE FIL DIGITAL INPUT 0030 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 8 | 16416 | 2021 | 0 | EL1134_M025 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 9 | 16416 | 2021 | 1
SPAFCR0032 | BIL SPARE FIL DIGITAL INPUT 032 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 10 | 16416 | 2021 | 2 | EL1134_M025 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 11 | 16416 | 2021 | 3
SPAFCR0031 | BIL SPARE FIL DIGITAL INPUT 031 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 12 | 16416 | 2021 | 4 | EL1134_M025 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 13 | 16416 | 2021 | 5
SPAFCR0033 | BIL SPARE FIL DIGITAL INPUT 033 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13299 | 14 | 16416 | 2021 | 6 | EL1134_M025 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13299 | 15 | 16416 | 2021 | 7
SPAFCR0034 | BIL SPARE FIL DIGITAL INPUT 034 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 0 | 16416 | 2022 | 0 | EL1134_M026 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 1 | 16416 | 2022 | 1
SPAFCR0036 | BIL SPARE FIL DIGITAL INPUT 036 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 2 | 16416 | 2022 | 2 | EL1134_M026 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 3 | 16416 | 2022 | 3
SPAFCR0035 | BIL SPARE FIL DIGITAL INPUT 035 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 4 | 16416 | 2022 | 4 | EL1134_M026 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 5 | 16416 | 2022 | 5
SPAFCR0037 | BIL SPARE FIL DIGITAL INPUT 037 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 6 | 16416 | 2022 | 6 | EL1134_M026 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 7 | 16416 | 2022 | 7
SPAFCR0038 | BIL SPARE FIL DIGITAL INPUT 038 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 8 | 16416 | 2023 | 0 | EL1134_M027 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 9 | 16416 | 2023 | 1
SPAFCR0040 | BIL SPARE FIL DIGITAL INPUT 040 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 10 | 16416 | 2023 | 2 | EL1134_M027 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 11 | 16416 | 2023 | 3
SPAFCR0039 | BIL SPARE FIL DIGITAL INPUT 039 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 12 | 16416 | 2023 | 4 | EL1134_M027 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 13 | 16416 | 2023 | 5
SPAFCR0041 | BIL SPARE FIL DIGITAL INPUT 041 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13300 | 14 | 16416 | 2023 | 6 | EL1134_M027 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13300 | 15 | 16416 | 2023 | 7
SPAFCR0042 | BIL SPARE FIL DIGITAL INPUT 042 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 0 | 16416 | 2024 | 0 | EL1134_M028 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 1 | 16416 | 2024 | 1
SPAFCR0044 | BIL SPARE FIL DIGITAL INPUT 044 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 2 | 16416 | 2024 | 2 | EL1134_M028 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 3 | 16416 | 2024 | 3
SPAFCR0043 | BIL SPARE FIL DIGITAL INPUT 043 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 4 | 16416 | 2024 | 4 | EL1134_M028 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 5 | 16416 | 2024 | 5
SPAFCR0045 | BIL SPARE FIL DIGITAL INPUT 045 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 6 | 16416 | 2024 | 6 | EL1134_M028 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 7 | 16416 | 2024 | 7
SPAFCR0046 | BIL SPARE FIL DIGITAL INPUT 046 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 8 | 16416 | 2025 | 0 | EL1134_M029 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 9 | 16416 | 2025 | 1
SPAFCR0048 | BIL SPARE FIL DIGITAL INPUT 048 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 10 | 16416 | 2025 | 2 | EL1134_M029 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 11 | 16416 | 2025 | 3
SPAFCR0047 | BIL SPARE FIL DIGITAL INPUT 047 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 12 | 16416 | 2025 | 4 | EL1134_M029 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 13 | 16416 | 2025 | 5
SPAFCR0049 | BIL SPARE FIL DIGITAL INPUT 049 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13301 | 14 | 16416 | 2025 | 6 | EL1134_M029 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13301 | 15 | 16416 | 2025 | 7
SPAFCR0050 | BIL SPARE FIL DIGITAL INPUT 050 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13302 | 0 | 16416 | 2026 | 0 | EL1134_M030 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 1 | 16416 | 2026 | 1
SPAFCR0052 | BIL SPARE FIL DIGITAL INPUT 052 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13302 | 2 | 16416 | 2026 | 2 | EL1134_M030 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 3 | 16416 | 2026 | 3
SPAFCR0051 | BIL SPARE FIL DIGITAL INPUT 051 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13302 | 4 | 16416 | 2026 | 4 | EL1134_M030 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 5 | 16416 | 2026 | 5
SPAFCR0053 | BIL SPARE FIL DIGITAL INPUT 053 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13302 | 6 | 16416 | 2026 | 6 | EL1134_M030 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 7 | 16416 | 2026 | 7
SPAFCR0054 | BIL SPARE FIL DIGITAL INPUT 054 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13302 | 8 | 16416 | 2027 | 0 | EL1134_M031 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 9 | 16416 | 2027 | 1
SPAFCR0056 | BIL SPARE FIL DIGITAL INPUT 056 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13302 | 10 | 16416 | 2027 | 2 | EL1134_M031 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 11 | 16416 | 2027 | 3
SPAFCR0055 | BIL SPARE FIL DIGITAL INPUT 055 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13302 | 12 | 16416 | 2027 | 4 | EL1134_M031 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 13 | 16416 | 2027 | 5
SPAFCR0057 | BIL SPARE FIL DIGITAL INPUT 057 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13302 | 14 | 16416 | 2027 | 6 | EL1134_M031 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13302 | 15 | 16416 | 2027 | 7
SPAFCR0058 | BIL SPARE FIL DIGITAL INPUT 058 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13303 | 0 | 16416 | 2028 | 0 | EL1134_M032 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 1 | 16416 | 2028 | 1
SPAFCR0060 | BIL SPARE FIL DIGITAL INPUT 060 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13303 | 2 | 16416 | 2028 | 2 | EL1134_M032 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 3 | 16416 | 2028 | 3
SPAFCR0059 | BIL SPARE FIL DIGITAL INPUT 059 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13303 | 4 | 16416 | 2028 | 4 | EL1134_M032 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 5 | 16416 | 2028 | 5
SPAFCR0061 | BIL SPARE FIL DIGITAL INPUT 061 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13303 | 6 | 16416 | 2028 | 6 | EL1134_M032 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 7 | 16416 | 2028 | 7
SPAFCR0062 | BIL SPARE FIL DIGITAL INPUT 062 | CR | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13303 | 8 | 16416 | 2029 | 0 | EL1134_M033 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 9 | 16416 | 2029 | 1
SPAFCR0064 | BIL SPARE FIL DIGITAL INPUT 064 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13303 | 10 | 16416 | 2029 | 2 | EL1134_M033 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 11 | 16416 | 2029 | 3
SPAFCR0063 | BIL SPARE FIL DIGITAL INPUT 063 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13303 | 12 | 16416 | 2029 | 4 | EL1134_M033 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 13 | 16416 | 2029 | 5
SPAFCR0065 | BIL SPARE FIL DIGITAL INPUT 065 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13303 | 14 | 16416 | 2029 | 6 | EL1134_M033 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13303 | 15 | 16416 | 2029 | 7
SPAFCR0066 | BIL SPARE FIL DIGITAL INPUT 066 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 0 | 16416 | 2030 | 0 | EL1134_M035 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 1 | 16416 | 2030 | 1
SPAFCR0068 | BIL SPARE FIL DIGITAL INPUT 068 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 2 | 16416 | 2030 | 2 | EL1134_M035 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 3 | 16416 | 2030 | 3
SPAFCR0067 | BIL SPARE FIL DIGITAL INPUT 067 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 4 | 16416 | 2030 | 4 | EL1134_M035 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 5 | 16416 | 2030 | 5
SPAFCR0069 | BIL SPARE FIL DIGITAL INPUT 069 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 6 | 16416 | 2030 | 6 | EL1134_M035 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 7 | 16416 | 2030 | 7
SPAFCR0070 | BIL SPARE FIL DIGITAL INPUT 070 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 8 | 16416 | 2031 | 0 | EL1134_M036 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 9 | 16416 | 2031 | 1
SPAFCR0072 | BIL SPARE FIL DIGITAL INPUT 072 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 10 | 16416 | 2031 | 2 | EL1134_M036 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 11 | 16416 | 2031 | 3
SPAFCR0071 | BIL SPARE FIL DIGITAL INPUT 071 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 12 | 16416 | 2031 | 4 | EL1134_M036 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 13 | 16416 | 2031 | 5
SPAFCR0073 | BIL SPARE FIL DIGITAL INPUT 073 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13304 | 14 | 16416 | 2031 | 6 | EL1134_M036 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13304 | 15 | 16416 | 2031 | 7
SPAFCR0074 | BIL SPARE FIL DIGITAL INPUT 074 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 0 | 16416 | 2032 | 0 | EL1134_M037 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 1 | 16416 | 2032 | 1
SPAFCR0076 | BIL SPARE FIL DIGITAL INPUT 076 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 2 | 16416 | 2032 | 2 | EL1134_M037 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 3 | 16416 | 2032 | 3
SPAFCR0075 | BIL SPARE FIL DIGITAL INPUT 075 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 4 | 16416 | 2032 | 4 | EL1134_M037 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 5 | 16416 | 2032 | 5
SPAFCR0077 | BIL SPARE FIL DIGITAL INPUT 077 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 6 | 16416 | 2032 | 6 | EL1134_M037 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 7 | 16416 | 2032 | 7
SPAFCR0078 | BIL SPARE FIL DIGITAL INPUT 078 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 8 | 16416 | 2033 | 0 | EL1134_M038 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 9 | 16416 | 2033 | 1
SPAFCR0080 | BIL SPARE FIL DIGITAL INPUT 080 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 10 | 16416 | 2033 | 2 | EL1134_M038 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 11 | 16416 | 2033 | 3
SPAFCR0079 | BIL SPARE FIL DIGITAL INPUT 079 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 12 | 16416 | 2033 | 4 | EL1134_M038 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 13 | 16416 | 2033 | 5
SPAFCR0081 | BIL SPARE FIL DIGITAL INPUT 081 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13305 | 14 | 16416 | 2033 | 6 | EL1134_M038 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13305 | 15 | 16416 | 2033 | 7
SPAFCR0082 | BIL SPARE FIL DIGITAL INPUT 082 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 0 | 16416 | 2034 | 0 | EL1134_M039 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 1 | 16416 | 2034 | 1
SPAFCR0084 | BIL SPARE FIL DIGITAL INPUT 084 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 2 | 16416 | 2034 | 2 | EL1134_M039 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 3 | 16416 | 2034 | 3
SPAFCR0083 | BIL SPARE FIL DIGITAL INPUT 083 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 4 | 16416 | 2034 | 4 | EL1134_M039 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 5 | 16416 | 2034 | 5
SPAFCR0085 | BIL SPARE FIL DIGITAL INPUT 085 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 6 | 16416 | 2034 | 6 | EL1134_M039 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 7 | 16416 | 2034 | 7
SPAFCR0086 | BIL SPARE FIL DIGITAL INPUT 086 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 8 | 16416 | 2035 | 0 | EL1134_M040 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 9 | 16416 | 2035 | 1
SPAFCR0088 | BIL SPARE FIL DIGITAL INPUT 088 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 10 | 16416 | 2035 | 2 | EL1134_M040 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 11 | 16416 | 2035 | 3
SPAFCR0087 | BIL SPARE FIL DIGITAL INPUT 087 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 12 | 16416 | 2035 | 4 | EL1134_M040 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 13 | 16416 | 2035 | 5
SPAFCR0089 | BIL SPARE FIL DIGITAL INPUT 089 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13306 | 14 | 16416 | 2035 | 6 | EL1134_M040 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13306 | 15 | 16416 | 2035 | 7
SPAFCR0090 | BIL SPARE FIL DIGITAL INPUT 090 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 0 | 16416 | 2036 | 0 | EL1134_M041 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 1 | 16416 | 2036 | 1
SPAFCR0092 | BIL SPARE FIL DIGITAL INPUT 092 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 2 | 16416 | 2036 | 2 | EL1134_M041 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 3 | 16416 | 2036 | 3
SPAFCR0091 | BIL SPARE FIL DIGITAL INPUT 091 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 4 | 16416 | 2036 | 4 | EL1134_M041 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 5 | 16416 | 2036 | 5
SPAFCR0093 | BIL SPARE FIL DIGITAL INPUT 093 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 6 | 16416 | 2036 | 6 | EL1134_M041 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 7 | 16416 | 2036 | 7
SPAFCR0094 | BIL SPARE FIL DIGITAL INPUT 094 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 8 | 16416 | 2037 | 0 | EL1134_M042 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 9 | 16416 | 2037 | 1
SPAFCR0096 | BIL SPARE FIL DIGITAL INPUT 096 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 10 | 16416 | 2037 | 2 | EL1134_M042 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 11 | 16416 | 2037 | 3
SPAFCR0095 | BIL SPARE FIL DIGITAL INPUT 095 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 12 | 16416 | 2037 | 4 | EL1134_M042 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 13 | 16416 | 2037 | 5
SPAFCR0097 | BIL SPARE FIL DIGITAL INPUT 097 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13307 | 14 | 16416 | 2037 | 6 | EL1134_M042 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13307 | 15 | 16416 | 2037 | 7
SPAFCR0098 | BIL SPARE FIL DIGITAL INPUT 098 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 0 | 16416 | 2038 | 0 | EL1134_M043 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 1 | 16416 | 2038 | 1
SPAFCR0100 | BIL SPARE FIL DIGITAL INPUT 100 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 2 | 16416 | 2038 | 2 | EL1134_M043 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 3 | 16416 | 2038 | 3
SPAFCR0099 | BIL SPARE FIL DIGITAL INPUT 099 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 4 | 16416 | 2038 | 4 | EL1134_M043 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 5 | 16416 | 2038 | 5
SPAFCR0101 | BIL SPARE FIL DIGITAL INPUT 101 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 6 | 16416 | 2038 | 6 | EL1134_M043 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 7 | 16416 | 2038 | 7
SPAFCR0102 | BIL SPARE FIL DIGITAL INPUT 102 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 8 | 16416 | 2039 | 0 | EL1134_M044 | I1 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 9 | 16416 | 2039 | 1
SPAFCR0104 | BIL SPARE FIL DIGITAL INPUT 104 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 10 | 16416 | 2039 | 2 | EL1134_M044 | I2 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 11 | 16416 | 2039 | 3
SPAFCR0103 | BIL SPARE FIL DIGITAL INPUT 103 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 12 | 16416 | 2039 | 4 | EL1134_M044 | I3 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 13 | 16416 | 2039 | 5
SPAFCR0105 | BIL SPARE FIL DIGITAL INPUT 105 | CR | O | FIL | 4 | [28 empty] | 10000 |  |  |  | BIL | 12 |  |  |  |  | 13308 | 14 | 16416 | 2039 | 6 | EL1134_M044 | I4 | BITVAL
VALIDITY | VALIDITY | [42 empty] | 13308 | 15 | 16416 | 2039 | 7
MG91DMA | BIL SYNTHESE DEFAUT AE/AR ET FEU BARRIERE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCE94001M; SSP94001D; SST94002O | Y |  |  |  | MG91 | Moyens Generaux (MG) | BIL
RPR94001 | BIL Pression AIR | MA | O | FIL | 4 | F | [26 empty] | POL | 2000 |  | MG92 BIL Mesures azote et air | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13500 | 0 | 16416 | 2422 | 0 | ELM3148_M011 | X1/1 (+) - X1/2 (-) | I32
OPR9400 | BIL Pompier Pression Eaux | MA | O | FIL | 4 | F | [26 empty] | POL | 2000 |  | MG92 BIL Mesures azote et air | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13502 | 0 | 16416 | 2426 | 0 | ELM3148_M011 | X2/1 (+) - X2/2 (-) | I32
HPR94001 | BIL Pression GHe | MA | O | FIL | 4 | F | [26 empty] | POL | 2000 |  | MG92 BIL Mesures azote et air | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13504 | 0 | 16416 | 2430 | 0 | ELM3148_M011 | X3/1 (+) - X3/2 (-) | I32
RQR94001 | BIL Pression AIR | MA | O | FIL | 4 | F | [26 empty] | POL | 2000 |  | MG92 BIL Mesures azote et air | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13506 | 0 | 16416 | 2434 | 0 | ELM3148_M011 | X4/1 (+) - X4/2 (-) | I32
HQR94001 | BIL DEBIT GHe | MA | O | FIL | 4 | F | [26 empty] | POL | 2000 |  | MG92 BIL Mesures azote et air | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13508 | 0 | 16416 | 2438 | 0 | ELM3148_M011 | X5/1 (+) - X5/2 (-) | I32
AQR94001 | BIL DEBIT GN2 | MA | O | FIL | 4 | F | [26 empty] | POL | 2000 |  | MG92 BIL Mesures azote et air | Moyens Generaux (MG) | BIL | 12 |  |  |  |  | 13510 | 0 | 16416 | 2442 | 0 | ELM3148_M011 | X6/1 (+) - X6/2 (-) | I32
SPAFMA0001 | BIL SPARE FIL ANALOG INPUT 0001 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13512 | 0 | 16416 | 2446 | 0 | ELM3148_M011 | X7/1 (+) - X7/2 (-) | I32
SPAFMA0002 | BIL SPARE FIL ANALOG INPUT 0002 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13514 | 0 | 16416 | 2450 | 0 | ELM3148_M011 | X8/1 (+) - X8/2 (-) | I32
SPAFMA0003 | BIL SPARE FIL ANALOG INPUT 0003 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13516 | 0 | 16416 | 2454 | 0 | ELM3148_M019 | X1/1 (+) - X1/2 (-) | I32
SPAFMA0004 | BIL SPARE FIL ANALOG INPUT 0004 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13518 | 0 | 16416 | 2458 | 0 | ELM3148_M019 | X2/1 (+) - X2/2 (-) | I32
SPAFMA0005 | BIL SPARE FIL ANALOG INPUT 0005 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13520 | 0 | 16416 | 2462 | 0 | ELM3148_M019 | X3/1 (+) - X3/2 (-) | I32
SPAFMA0006 | BIL SPARE FIL ANALOG INPUT 0006 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13522 | 0 | 16416 | 2466 | 0 | ELM3148_M019 | X4/1 (+) - X4/2 (-) | I32
SPAFMA0007 | BIL SPARE FIL ANALOG INPUT 0007 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13524 | 0 | 16416 | 2470 | 0 | ELM3148_M019 | X5/1 (+) - X5/2 (-) | I32
SPAFMA0008 | BIL SPARE FIL ANALOG INPUT 0008 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13526 | 0 | 16416 | 2474 | 0 | ELM3148_M019 | X6/1 (+) - X6/2 (-) | I32
SPAFMA0009 | BIL SPARE FIL ANALOG INPUT 0009 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13528 | 0 | 16416 | 2478 | 0 | ELM3148_M019 | X7/1 (+) - X7/2 (-) | I32
SPAFMA0010 | BIL SPARE FIL ANALOG INPUT 0010 | MA | O | FIL | 4 | [32 empty] | BIL | 12 |  |  |  |  | 13530 | 0 | 16416 | 2482 | 0 | ELM3148_M019 | X8/1 (+) - X8/2 (-) | I32
ZJM9103CM | BIL CMD MODE OPE. VMC FRONTAUX - U16(4), MANUAL(1) / U16(4), AUTO(2) | CT | N | INT | 0 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 13 |  |  |  |  | 12290 | 0 | 16416 | 2 | 0 |  |  | UINT | 1 | comando scritto dallo SCADA che descrive la modalità di funzionamento manuale
ZJM9103CA | BIL CMD MODE OPE. VMC FRONTAUX - U16(4), MANUAL(1) / U16(4), AUTO(2) | CT | N | INT | 0 | Z | [12 empty] | Z | NO | [12 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12290 | 0 | 16416 | 2 | 0 |  |  | UINT | 2 | comando scritto dallo SCADA che descrive la modalità di funzionamento automatica
ZJN9103COM | BIL CMD BASCULAMENT VMC FRONTAUX | CT | N | INT | 0 | Z | [12 empty] | Z | NO |  |  |  |  | ZJM9103 ('Manual') | [7 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12291 | 0 | 16416 | 4 | 0 |  |  | UINT | 1 | comando inviato dall'operatore tramite SCADA = 1 plc master
ZJN9103COS | BIL CMD BASCULAMENT VMC FRONTAUX | CT | N | INT | 0 | Z | [12 empty] | Z | NO |  |  |  |  | ZJM9103 ('Manual') | [7 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12291 | 0 | 16416 | 4 | 0 |  |  | UINT | 2 | comando inviato dall'operatore tramite SCADA = 2 plc slave
ZJL9103 | BIL PLC_Master_Name | MA | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12295 | 0 | 16416 | 12 | 0 |  |  | STRING(12) |  | nome del PLC master
ZJM9103 | BIL PLC_Op_Mode | AL | N | INT | 0 | Z | [9 empty] | x==1 |  |  | Z | [13 empty] | NOT | 2000 |  |  |  | BIL | 0 |  |  |  |  | 12301 | 0 | 16416 | 24 | 0 |  |  | UINT |  | variabile che se pari a 1 indica modalità manuale, se 2 modalità automatica, precond per be master/slave
ZJP9103 | BIL Master_PLC_Status | AL | N | INT | 0 | Z |  | R | [10 empty] | Z | [13 empty] | NOT | 2000 |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12302 | 0 | 16416 | 26 | 0 |  |  | BOOL |  | variabile booleana che identifica lo stato del PLC corrente
ZJS9103 | BIL Slave_PLC_Status | AL | N | INT | 0 | Z |  | R | [10 empty] | Z | [13 empty] | NOT | 2000 |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12303 | 0 | 16416 | 28 | 0 |  |  | BOOL |  | variabile booleana che identifica lo stato dell'altro PLC
ZJR9103 | BIL PLC_Number | MA | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 0 |  |  |  |  | 12304 | 0 | 16416 | 30 | 0 |  |  | STRING(10) |  | variabile che identifica il nome del PLC
ZJF9103 | BIL BIL PLC_Master | CR | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  |  |  | BIL | 12 |  |  |  |  | 12289 | 0 | 16416 | 0 | 0 |  |  | UINT |  | variabile letta dallo SCADA per stabilire chi è master
ZJG9103 | BIL plc2_heartbeat | CR | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  |  |  | BIL | 12 |  |  |  |  | 12292 | 0 | 16416 | 6 | 0 |  |  | BOOL |  | variabile che se uguale a true indica un malfunzionamento del secondo plc
ZJJ9103 | BIL plc1_heartbeat | CR | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  |  |  | BIL | 12 |  |  |  |  | 12293 | 0 | 16416 | 8 | 0 |  |  | BOOL |  | variabile che se uguale a true indica un malfunzionamento del primo plc
ZJK9103 | BIL PLC_Forced | CR | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  |  |  | BIL | 12 |  |  |  |  | 12294 | 0 | 16416 | 10 | 0 |  |  | UINT |  | variabile scritta dallo SCADA per forzare il plc a master
ZJM9103 | BIL PLC_Op_Mode | AL | N | INT | 0 | Z | [9 empty] | x==1 |  |  | Z | [13 empty] | NOT |  |  | VMC BIL ETAT DU FRONTAUX ET REDONDANCE | VMC Supervision (Z) | BIL | 12 |  |  |  |  | 12301 | 0 | 16416 | 24 | 0 |  |  | UINT |  | variabile che se pari a 1 indica modalità manuale, se 2 modalità automatica, precond per be master/slave
ZJX9103 | BIL Keep_alive | CR | N | INT | 0 | Z | [26 empty] | NOT | 2000 |  |  |  | BIL | 12 |  |  |  |  | 12311 | 0 | 16416 | 44 | 0 |  |  | UINT |  | variabile che indica se il PLC è freezato o sta funzionando
ZZZ9100EC1 | BIL VMC Front-End etat du module EK1100_EC1 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13900 | 0 | 16416 | 3222 | 0 | EK1100_EC1 |  | UINT
ZZZ9100EC2 | BIL VMC Front-End etat du module EK1100_EC2 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13901 | 0 | 16416 | 3224 | 0 | EK1100_EC2 |  | UINT
ZZZ9110EC0 | BIL VMC Front-End etat du module EK1110 [0] | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 0 ET DU FRONTAL MASTER | VMC Supervision (Z) | BIL | [5 empty] | 13902 | 0 | 16416 | 3226 | 0 | EK1110 [0] |  | UINT
ZZZ9110EC1 | BIL VMC Front-End etat du module EK1110 [1] | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13903 | 0 | 16416 | 3228 | 0 | EK1110 [1] |  | UINT
ZZZ9110EC2 | BIL VMC Front-End etat du module EK1110 [2] | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13904 | 0 | 16416 | 3230 | 0 | EK1110 [2] |  | UINT
ZZZ9134M2 | BIL VMC API Front-End etat du module EL1134_M002 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13905 | 0 | 16416 | 3232 | 0 | EL1134_M002 |  | UINT
ZZZ9134M3 | BIL VMC API Front-End etat du module EL1134_M003 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13906 | 0 | 16416 | 3234 | 0 | EL1134_M003 |  | UINT
ZZZ9134M4 | BIL VMC API Front-End etat du module EL1134_M004 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13907 | 0 | 16416 | 3236 | 0 | EL1134_M004 |  | UINT
ZZZ9134M5 | BIL VMC API Front-End etat du module EL1134_M005 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13908 | 0 | 16416 | 3238 | 0 | EL1134_M005 |  | UINT
ZZZ9134M6 | BIL VMC API Front-End etat du module EL1134_M006 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13909 | 0 | 16416 | 3240 | 0 | EL1134_M006 |  | UINT
ZZZ9134M7 | BIL VMC API Front-End etat du module EL1134_M007 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13910 | 0 | 16416 | 3242 | 0 | EL1134_M007 |  | UINT
ZZZ9134M8 | BIL VMC API Front-End etat du module EL1134_M008 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13911 | 0 | 16416 | 3244 | 0 | EL1134_M008 |  | UINT
ZZZ9134M9 | BIL VMC API Front-End etat du module EL1134_M009 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13912 | 0 | 16416 | 3246 | 0 | EL1134_M009 |  | UINT
ZZZ9134M10 | BIL VMC API Front-End etat du module EL1134_M010 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13913 | 0 | 16416 | 3248 | 0 | EL1134_M010 |  | UINT
ZZZ9134M11 | BIL VMC API Front-End etat du module EL1134_M011 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13914 | 0 | 16416 | 3250 | 0 | EL1134_M011 |  | UINT
ZZZ9134M13 | BIL VMC API Front-End etat du module EL1134_M013 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13915 | 0 | 16416 | 3252 | 0 | EL1134_M013 |  | UINT
ZZZ9134M14 | BIL VMC API Front-End etat du module EL1134_M014 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13916 | 0 | 16416 | 3254 | 0 | EL1134_M014 |  | UINT
ZZZ9134M15 | BIL VMC API Front-End etat du module EL1134_M015 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13917 | 0 | 16416 | 3256 | 0 | EL1134_M015 |  | UINT
ZZZ9134M16 | BIL VMC API Front-End etat du module EL1134_M016 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13918 | 0 | 16416 | 3258 | 0 | EL1134_M016 |  | UINT
ZZZ9134M17 | BIL VMC API Front-End etat du module EL1134_M017 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13919 | 0 | 16416 | 3260 | 0 | EL1134_M017 |  | UINT
ZZZ9134M18 | BIL VMC API Front-End etat du module EL1134_M018 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13920 | 0 | 16416 | 3262 | 0 | EL1134_M018 |  | UINT
ZZZ9134M19 | BIL VMC API Front-End etat du module EL1134_M019 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13921 | 0 | 16416 | 3264 | 0 | EL1134_M019 |  | UINT
ZZZ9134M20 | BIL VMC API Front-End etat du module EL1134_M020 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13922 | 0 | 16416 | 3266 | 0 | EL1134_M020 |  | UINT
ZZZ9134M21 | BIL VMC API Front-End etat du module EL1134_M021 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13923 | 0 | 16416 | 3268 | 0 | EL1134_M021 |  | UINT
ZZZ9134M22 | BIL VMC API Front-End etat du module EL1134_M022 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13924 | 0 | 16416 | 3270 | 0 | EL1134_M022 |  | UINT
ZZZ9134M24 | BIL VMC API Front-End etat du module EL1134_M024 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13925 | 0 | 16416 | 3272 | 0 | EL1134_M024 |  | UINT
ZZZ9134M25 | BIL VMC API Front-End etat du module EL1134_M025 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13926 | 0 | 16416 | 3274 | 0 | EL1134_M025 |  | UINT
ZZZ9134M26 | BIL VMC API Front-End etat du module EL1134_M026 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13927 | 0 | 16416 | 3276 | 0 | EL1134_M026 |  | UINT
ZZZ9134M27 | BIL VMC API Front-End etat du module EL1134_M027 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13928 | 0 | 16416 | 3278 | 0 | EL1134_M027 |  | UINT
ZZZ9134M28 | BIL VMC API Front-End etat du module EL1134_M028 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13929 | 0 | 16416 | 3280 | 0 | EL1134_M028 |  | UINT
ZZZ9134M29 | BIL VMC API Front-End etat du module EL1134_M029 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13930 | 0 | 16416 | 3282 | 0 | EL1134_M029 |  | UINT
ZZZ9134M30 | BIL VMC API Front-End etat du module EL1134_M030 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13931 | 0 | 16416 | 3284 | 0 | EL1134_M030 |  | UINT
ZZZ9134M31 | BIL VMC API Front-End etat du module EL1134_M031 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13932 | 0 | 16416 | 3286 | 0 | EL1134_M031 |  | UINT
ZZZ9134M32 | BIL VMC API Front-End etat du module EL1134_M032 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13933 | 0 | 16416 | 3288 | 0 | EL1134_M032 |  | UINT
ZZZ9134M33 | BIL VMC API Front-End etat du module EL1134_M033 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13934 | 0 | 16416 | 3290 | 0 | EL1134_M033 |  | UINT
ZZZ9134M35 | BIL VMC API Front-End etat du module EL1134_M035 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13935 | 0 | 16416 | 3292 | 0 | EL1134_M035 |  | UINT
ZZZ9134M36 | BIL VMC API Front-End etat du module EL1134_M036 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13936 | 0 | 16416 | 3294 | 0 | EL1134_M036 |  | UINT
ZZZ9134M37 | BIL VMC API Front-End etat du module EL1134_M037 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13937 | 0 | 16416 | 3296 | 0 | EL1134_M037 |  | UINT
ZZZ9134M38 | BIL VMC API Front-End etat du module EL1134_M038 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13938 | 0 | 16416 | 3298 | 0 | EL1134_M038 |  | UINT
ZZZ9134M39 | BIL VMC API Front-End etat du module EL1134_M039 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13939 | 0 | 16416 | 3300 | 0 | EL1134_M039 |  | UINT
ZZZ9134M40 | BIL VMC API Front-End etat du module EL1134_M040 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13940 | 0 | 16416 | 3302 | 0 | EL1134_M040 |  | UINT
ZZZ9134M41 | BIL VMC API Front-End etat du module EL1134_M041 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13941 | 0 | 16416 | 3304 | 0 | EL1134_M041 |  | UINT
ZZZ9134M42 | BIL VMC API Front-End etat du module EL1134_M042 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13942 | 0 | 16416 | 3306 | 0 | EL1134_M042 |  | UINT
ZZZ9134M43 | BIL VMC API Front-End etat du module EL1134_M043 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13943 | 0 | 16416 | 3308 | 0 | EL1134_M043 |  | UINT
ZZZ9134M44 | BIL VMC API Front-End etat du module EL1134_M044 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL | [5 empty] | 13944 | 0 | 16416 | 3310 | 0 | EL1134_M044 |  | UINT
ZZZ9621M23 | BIL VMC API Front-End etat du module EL6021_M024 - ZVQ4001/4002 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13945 | 0 | 16416 | 3312 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
ZZZ9621M24 | BIL VMC API Front-End etat du module EL6021_M024 - ZVQ4003/4004/4005 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13946 | 0 | 16416 | 3314 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
ZZZ9621M25 | BIL VMC API Front-End etat du module EL6021 - Energie CATIII | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13947 | 0 | 16416 | 3316 | 0 | EL6021 - Energie CATIII |  | UINT
ZZZ9621M26 | BIL VMC API Front-End etat du module EL6021 - Energie CATI/II | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13948 | 0 | 16416 | 3318 | 0 | EL6021 - Energie CATI/II |  | UINT
ZZZ9621M27 | BIL VMC API Front-End etat du module EL6021 - SPARE01 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13949 | 0 | 16416 | 3320 | 0 | EL6021 - SPARE01 |  | UINT
ZZZ9621M28 | BIL VMC API Front-End etat du module EL6021 - SPARE02 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13950 | 0 | 16416 | 3322 | 0 | EL6021 - SPARE02 |  | UINT
ZZZ9621M29 | BIL VMC API Front-End etat du module EL6021 - SPARE03 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13951 | 0 | 16416 | 3324 | 0 | EL6021 - SPARE03 |  | UINT
ZZZ9621M30 | BIL VMC API Front-End etat du module EL6021 - SPARE04 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13952 | 0 | 16416 | 3326 | 0 | EL6021 - SPARE04 |  | UINT
ZZZ9621M31 | BIL VMC API Front-End etat du module EL6021 - SPARE05 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13953 | 0 | 16416 | 3328 | 0 | EL6021 - SPARE05 |  | UINT
ZZZ9941M10 | BIL VMC API Front-End etat du module EL9410_M010 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13954 | 0 | 16416 | 3330 | 0 | EL9410_M010 |  | UINT
ZZZ9941M12 | BIL VMC API Front-End etat du module EL9410_M012 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13955 | 0 | 16416 | 3332 | 0 | EL9410_M012 |  | UINT
ZZZ9941M17 | BIL VMC API Front-End etat du module EL9410_M017 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13956 | 0 | 16416 | 3334 | 0 | EL9410_M017 |  | UINT
ZZZ9314M11 | BIL VMC API Front-End etat du module ELM3148_M011 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13957 | 0 | 16416 | 3336 | 0 | ELM3148_M011 |  | UINT
ZZZ9314M18 | BIL VMC API Front-End etat du module ELM3148_M019 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13958 | 0 | 16416 | 3338 | 0 | ELM3148_M019 |  | UINT
ZZZ9289M13 | BIL VMC API Front-End etat du module EL2869_M013 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13959 | 0 | 16416 | 3340 | 0 | EL2869_M013 |  | UINT
ZZZ9289M14 | BIL VMC API Front-End etat du module EL2869_M014 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13960 | 0 | 16416 | 3342 | 0 | EL2869_M014 |  | UINT
ZZZ9289M15 | BIL VMC API Front-End etat du module EL2869_M015 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13961 | 0 | 16416 | 3344 | 0 | EL2869_M015 |  | UINT
ZZZ9289M16 | BIL VMC API Front-End etat du module EL2869_M016 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL | [5 empty] | 13962 | 0 | 16416 | 3346 | 0 | EL2869_M016 |  | UINT
ZZZ9670M40 | BIL VMC API Front-End etat du module EL6070_M40 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 0 ET DU FRONTAL MASTER | VMC Supervision (Z) | BIL | [5 empty] | 13963 | 0 | 16416 | 3348 | 0 | EL6070_M40 |  | UINT
ZZZ9189M41 | BIL VMC API Front-End etat du module EL1809_M41 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 0 ET DU FRONTAL MASTER | VMC Supervision (Z) | BIL | [5 empty] | 13964 | 0 | 16416 | 3350 | 0 | EL1809_M41 |  | UINT
ZZZ9289M42 | BIL VMC API Front-End etat du module EL2809_M42 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | NOT | 2000 |  | BIL ETAT DU MODULES DU CHAINE 0 ET DU FRONTAL MASTER | VMC Supervision (Z) | BIL | [5 empty] | 13965 | 0 | 16416 | 3352 | 0 | EL2809_M42 |  | UINT
ZJP9600DMA | VMC SUPERVISION FE MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZJP9001DMA; ZJP6103DMA | Y |  |  |  | VMC Supervision (Node) | VMC Supervision (Z) | BIL
ZJP9001DMA | BIL VMC FE PLC MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZZZDMA0; ZZDMA1 ; ZZZDMA2; ZJP9103; ZJS9103; ZJM9103; | Y |  |  |  | VMC Supervision BIL | VMC Supervision (Z) | BIL
ZZZ9DMA0 | BIL SYNTHESE ETAT DU MODULES DU CHAINE 0 ET DU FRONTAL MASTER | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZJP9103; ZZZ9670M40; ZZZ9189M41; ZZZ9289M42; ZZZ9110EC0 | Y |  |  |  | BIL ETAT DU MODULES DU CHAINE 0 ET DU FRONTAL MASTER | VMC Supervision (Z) | BIL
ZZZ9DMA1 | BIL SYNTHESE INFO ETAT DU MODULES DU CHAINE 1 - 1 SUR 2 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ9100EC1; ZZZ9134M2; ZZZ9134M3; ZZZ9134M4; ZZZ9134M5; ZZZ9134M6; ZZZ9134M7; ZZZ9134M8; ZZZ9134M9; ZZZ9134M10; ZZZ9134M11; ZZZ9134M13; ZZZ9134M14; ZZZ9134M15; ZZZ9134M16; ZZZ9134M17; ZZZ9134M18; ZZZ9134M19; ZZZ9134M20; ZZZ9134M21; ZZZ9134M22; ZZZ9134M23; ZZZ9134M24; ZZZ9134M25; ZZZ9134M26 | Y |  |  |  | BIL ETAT DU MODULES DU CHAINE 1 1 SUR 2 | VMC Supervision (Z) | BIL
ZZZ9DMA2 | BIL SYNTHESE INFO ETAT DU MODULES DU CHAINE 1 - 2 SUR 2 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ9134M27; ZZZ9134M28; ZZZ9134M29; ZZZ9134M30; ZZZ9134M31; ZZZ9134M32; ZZZ9134M33; ZZZ9134M35; ZZZ9134M36; ZZZ9134M37; ZZZ9134M38; ZZZ9134M39; ZZZ9134M40; ZZZ9134M41; ZZZ9134M42; ZZZ9134M43; ZZZ9134M44; ZZZ9110EC1; | Y |  |  |  | BIL ETAT DU MODULES DU CHAINE 1 2 SUR 2 | VMC Supervision (Z) | BIL
ZZZ9DMA3 | BIL SYNTHESE INFO ETAT DU MODULES DU CHAIN 2 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ9100EC2; ZZZ9621M23; ZZZ9621M24; ZZZ9621M25; ZZZ9621M26; ZZZ9621M27; ZZZ9621M28; ZZZ9621M29; ZZZ9621M30; ZZZ9621M31; ZZZ9941M32; ZZZ9941M33; ZZZ9314M34; ZZZ9314M35; ZZZ9289M36; ZZZ9289M37; ZZZ9289M38; ZZZ9289M39; ZZZ9110EC2 | Y |  |  |  | BIL ETAT DU MODULES DU CHAINE 2 | VMC Supervision (Z) | BIL
VZC9401D | BIL DF automate - ZVQ4001 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 901 | 0 | 14000 | 0 | 16416 | 3422 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 1 | 16416 | 3422 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VZC9401DC1 | BIL DF Com avec ZVQ4002 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 901 | 1 | 14000 | 2 | 16416 | 3422 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 3 | 16416 | 3422 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VZC9401DC2 | BIL: DF groupe redondé avec ZVQ4002 | AL | N | RES | 4 | A | [12 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 901 | 2 | 14000 | 4 | 16416 | 3422 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 5 | 16416 | 3422 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 3 | 14000 | 6 | 16416 | 3422 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 7 | 16416 | 3422 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 4 | 14000 | 8 | 16416 | 3423 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 9 | 16416 | 3423 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 5 | 14000 | 10 | 16416 | 3423 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 11 | 16416 | 3423 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 6 | 14000 | 12 | 16416 | 3423 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 13 | 16416 | 3423 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 7 | 14000 | 14 | 16416 | 3423 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14000 | 15 | 16416 | 3423 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 8 | 14001 | 0 | 16416 | 3424 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 1 | 16416 | 3424 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 9 | 14001 | 2 | 16416 | 3424 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 3 | 16416 | 3424 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| DF forcage commutateur | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 901 | 10 | 14001 | 4 | 16416 | 3424 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 5 | 16416 | 3424 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VAE94001D1 | BIL DF presence CAT 1 KUU4001 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 901 | 11 | 14001 | 6 | 16416 | 3424 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 7 | 16416 | 3424 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VAE94001D2 | BIL DF presence CAT 2 KUU4002 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 901 | 12 | 14001 | 8 | 16416 | 3425 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 9 | 16416 | 3425 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 13 | 14001 | 10 | 16416 | 3425 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 11 | 16416 | 3425 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 14 | 14001 | 12 | 16416 | 3425 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 13 | 16416 | 3425 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use | [36 empty] | BIL | 13 |  |  | 901 | 15 | 14001 | 14 | 16416 | 3425 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14001 | 15 | 16416 | 3425 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94011D2 | BIL DF KKM4011 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 0 | 14002 | 0 | 16416 | 3426 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 1 | 16416 | 3426 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94011DI1 | BIL DF Press. diff. VPB4011 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 1 | 14002 | 2 | 16416 | 3426 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 3 | 16416 | 3426 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94010DR1 | BIL DF Sonde T° PDR VTR4010 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 2 | 14002 | 4 | 16416 | 3426 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 5 | 16416 | 3426 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94011DR | BIL DF Sonde T° AS VTR4011 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 3 | 14002 | 6 | 16416 | 3426 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 7 | 16416 | 3426 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94012DO1 | BIL DF ouv SM AN VSA4012 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 4 | 14002 | 8 | 16416 | 3427 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 9 | 16416 | 3427 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94012DF1 | BIL DF fer SM AN VSB4012 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 5 | 14002 | 10 | 16416 | 3427 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 11 | 16416 | 3427 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VT94022D | BIL DF Sonde T° Repr. VTR4022 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 902 | 6 | 14002 | 12 | 16416 | 3427 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 13 | 16416 | 3427 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VAR94012DT | BIL DF Sonde T° AN VTR4012 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC | BIL | 13 |  |  | 902 | 7 | 14002 | 14 | 16416 | 3427 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14002 | 15 | 16416 | 3427 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VH94022D | BIL DF Sonde HR Repr. VHR4022 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 902 | 8 | 14003 | 0 | 16416 | 3428 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 1 | 16416 | 3428 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94010DR2 | BIL DF Sonde T° PDR VTR4010 défaut matériel | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 9 | 14003 | 2 | 16416 | 3428 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 3 | 16416 | 3428 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94011D1 | BIL DF KQF4011 VCT4010 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 902 | 10 | 14003 | 4 | 16416 | 3428 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 5 | 16416 | 3428 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94021D1 | BIL DF KQF4021 VCT4020 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 902 | 11 | 14003 | 6 | 16416 | 3428 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 7 | 16416 | 3428 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94021D2 | BIL DF KKM4021 VCT4020 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 902 | 12 | 14003 | 8 | 16416 | 3429 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 9 | 16416 | 3429 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94021DI1 | BIL DF Press. diff. VPB4021 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 902 | 13 | 14003 | 10 | 16416 | 3429 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 11 | 16416 | 3429 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCN94031D | BIL DF géné. Armoire VCT4030 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 902 | 14 | 14003 | 12 | 16416 | 3429 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 13 | 16416 | 3429 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 902 | 15 | 14003 | 14 | 16416 | 3429 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14003 | 15 | 16416 | 3429 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VTR94010T | BIL VTR4010 sonde T° pdr VCT4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 903 | 0 | 14004 | 0 | 16416 | 3430 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94011T | BIL VTR4011 sonde T° AP VCT4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 904 | 0 | 14005 | 0 | 16416 | 3432 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94012T | BIL VTR4012 sonde T° AN VCT4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 905 | 0 | 14006 | 0 | 16416 | 3434 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94031T | BIL VTR4031 sonde T° amb VCT4030/40/100 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 906 | 0 | 14007 | 0 | 16416 | 3436 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| KKM4011 re KM Vent. VCT4010 | MA | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 907 | 0 | 14008 | 0 | 16416 | 3438 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| KQF4011 Protection Vent. VCT4010 | MA | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 908 | 0 | 14009 | 0 | 16416 | 3440 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VHR94031H | BIL VHR4031 sonde HR% amb VCT4030/40/100 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 909 | 0 | 14010 | 0 | 16416 | 3442 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94022T | BIL VTR4022 sonde T° repris VCT4020 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 910 | 0 | 14011 | 0 | 16416 | 3444 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94022H | BIL VHR4022 sonde HR% repris VCT4020 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 911 | 0 | 14012 | 0 | 16416 | 3446 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL KUU4002 prés. U CAT2 VCT4010 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 912 | 0 | 14013 | 0 | 16416 | 3448 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 913 | 0 | 14014 | 0 | 16416 | 3450 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| VDF4100 DF géné. Armoire VCT4100 |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 914 | 0 | 14015 | 0 | 16416 | 3452 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VCT94011M1 | BIL VPB4011 Pressostat diff. VCT4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 915 | 0 | 14016 | 0 | 16416 | 3454 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Il VMC tratta la misura come booleana prendendo il primo bit della word
| BIL VDF4031 DF géné. Armoire VCT4030 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 916 | 0 | 14017 | 0 | 16416 | 3456 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL KUU4001 prés. U CAT1 VCT4010 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 917 | 0 | 14018 | 0 | 16416 | 3458 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL KAQ4001 BP Acquittement ZVQ4001 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 918 | 0 | 14019 | 0 | 16416 | 3460 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL Cmde VFN4020 VCT4020 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 0 | 14020 | 0 | 16416 | 3462 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 1 | 16416 | 3462 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Pos. KQF4021 VCT4020 | AL | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 919 | 1 | 14020 | 2 | 16416 | 3462 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 3 | 16416 | 3462 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94021M1 | BIL Press. diff. VPB4021 | CR | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 919 | 2 | 14020 | 4 | 16416 | 3462 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 5 | 16416 | 3462 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 3 | 14020 | 6 | 16416 | 3462 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 7 | 16416 | 3462 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 4 | 14020 | 8 | 16416 | 3463 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 9 | 16416 | 3463 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94012O1 | BIL Cmde ouv SM AN VRP4012 | CR | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 919 | 5 | 14020 | 10 | 16416 | 3463 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 11 | 16416 | 3463 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94012F1 | BIL Cmde ouv SM AN VRP4012 | CR | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 919 | 6 | 14020 | 12 | 16416 | 3463 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94012DI1 | BIL Damper Registre Discordance VRP4012 | CR | N | CAL | 4 | C | [22 empty] | AND |  | VRP94012O1 ; VRP94012F1 |  | POL |  |  | HVAC902 | HVAC BIL | BIL | 13
VRP94012AE1 | BIL DamperRegistre Aucun Etat VRP4012 | CR | N | CAL | 4 | C | [22 empty] | NOR |  | VRP94012O1 ; VRP94012F1 |  | POL |  |  | HVAC902 | HVAC BIL | BIL | 13
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 13 | 16416 | 3463 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 7 | 14020 | 14 | 16416 | 3463 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14020 | 15 | 16416 | 3463 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 8 | 14021 | 0 | 16416 | 3464 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 1 | 16416 | 3464 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 9 | 14021 | 2 | 16416 | 3464 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 3 | 16416 | 3464 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 10 | 14021 | 4 | 16416 | 3464 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 5 | 16416 | 3464 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 11 | 14021 | 6 | 16416 | 3464 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 7 | 16416 | 3464 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 12 | 14021 | 8 | 16416 | 3465 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 9 | 16416 | 3465 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 13 | 14021 | 10 | 16416 | 3465 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 11 | 16416 | 3465 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 14 | 14021 | 12 | 16416 | 3465 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14021 | 13 | 16416 | 3465 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 919 | 15 | 14021 | 14 | 16416 | 3465 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | [5 empty] | 14021 | 15 | 16416 | 3465 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
CER94011T1 | BIL CWC4011 Vanne EC (% ouv) VCT4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 920 | 0 | 14022 | 0 | 16416 | 3466 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94021T1 | BIL CWC4021 Vanne EC (% ouv) VCT4020 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 921 | 0 | 14023 | 0 | 16416 | 3468 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
GER94021T1 | BIL GWC4021 Vanne EG (% ouv)VCT4020 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 922 | 0 | 14024 | 0 | 16416 | 3470 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
GER94011T1 | BIL GWC4011 Vanne EG VCT4010 (% ouv) | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 923 | 0 | 14025 | 0 | 16416 | 3472 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL VFN4011 Vent. cde marche VCT4010 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 924 | 0 | 14026 | 0 | 16416 | 3474 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL VFN4021 Vent. cde marche VCT4020 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 925 | 0 | 14027 | 0 | 16416 | 3476 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL VRP4012 SM AN cde ouv VCT4010 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 926 | 0 | 14028 | 0 | 16416 | 3478 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL VFN4031 cde marche Arm. VCT4030 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 927 | 0 | 14029 | 0 | 16416 | 3480 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL VFN4100 cde marche Arm. VCT4100 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 928 | 0 | 14030 | 0 | 16416 | 3482 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VCN94100D | BIL DF géné. Armoire VCT4100 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 929 | 0 | 14031 | 0 | 16416 | 3484 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 1 | 16416 | 3484 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VT94031D | BIL DF Sonde T° Amb. VTR4031 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 929 | 1 | 14031 | 2 | 16416 | 3484 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 3 | 16416 | 3484 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VH94031D | BIL DF Sonde HR Amb. VHR4031 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 929 | 2 | 14031 | 4 | 16416 | 3484 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 5 | 16416 | 3484 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 3 | 14031 | 6 | 16416 | 3484 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 7 | 16416 | 3484 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 4 | 14031 | 8 | 16416 | 3485 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 9 | 16416 | 3485 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 5 | 14031 | 10 | 16416 | 3485 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 11 | 16416 | 3485 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 6 | 14031 | 12 | 16416 | 3485 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 13 | 16416 | 3485 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 7 | 14031 | 14 | 16416 | 3485 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14031 | 15 | 16416 | 3485 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 8 | 14032 | 0 | 16416 | 3486 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 1 | 16416 | 3486 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 9 | 14032 | 2 | 16416 | 3486 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 3 | 16416 | 3486 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 10 | 14032 | 4 | 16416 | 3486 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 5 | 16416 | 3486 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 11 | 14032 | 6 | 16416 | 3486 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 7 | 16416 | 3486 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 12 | 14032 | 8 | 16416 | 3487 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 9 | 16416 | 3487 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 13 | 14032 | 10 | 16416 | 3487 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 11 | 16416 | 3487 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 14 | 14032 | 12 | 16416 | 3487 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14032 | 13 | 16416 | 3487 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 929 | 15 | 14032 | 14 | 16416 | 3487 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | [5 empty] | 14032 | 15 | 16416 | 3487 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Mot des sorties digitale |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 930 | 0 | 14033 | 0 | 16416 | 3488 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VTR94020 | BIL ZVQ4001 Consigne T° Repr. VTR4022 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 301 | 0 | 14034 | 0 | 16416 | 3490 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94020 | BIL ZVQ4001 Consigne HR Repr. VHR4022 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 302 | 0 | 14035 | 0 | 16416 | 3492 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94010T2 | BIL ZVQ4001 Consigne T° PDR VTR4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 303 | 0 | 14036 | 0 | 16416 | 3494 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94010T1 | BIL ZVQ4001 Consigne T° Soufflage VTR4010 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 304 | 0 | 14037 | 0 | 16416 | 3496 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VVU90001D1 | BIL ZVQ4001 Conf1 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 306 | 0 | 14038 | 0 | 16416 | 3498 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 1 | 16416 | 3498 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU90001D6 | BIL ZVQ4001 Conf2 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 306 | 1 | 14038 | 2 | 16416 | 3498 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 3 | 16416 | 3498 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Conf3 (reserve) | AL | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 306 | 2 | 14038 | 4 | 16416 | 3498 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 5 | 16416 | 3498 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 3 | 14038 | 6 | 16416 | 3498 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 7 | 16416 | 3498 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU90003D1 | BIL ZVQ4001 Acquit | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 306 | 4 | 14038 | 8 | 16416 | 3499 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 9 | 16416 | 3499 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU94010D | BIL Marche VCT4010 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 306 | 5 | 14038 | 10 | 16416 | 3499 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 11 | 16416 | 3499 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Validation csg VCT4010 | AL | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 306 | 6 | 14038 | 12 | 16416 | 3499 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 13 | 16416 | 3499 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU940340D1 | BIL ZVQ4001 Sélect. Prio.arm Hiross | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 7 | 14038 | 14 | 16416 | 3499 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14038 | 15 | 16416 | 3499 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU94030D | BIL Marche VCT4030 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 8 | 14039 | 0 | 16416 | 3500 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 1 | 16416 | 3500 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU94020D | BIL Marche VCT4020 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 306 | 9 | 14039 | 2 | 16416 | 3500 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 3 | 16416 | 3500 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU94100D | BIL Marche VCT4100 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 10 | 14039 | 4 | 16416 | 3500 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 5 | 16416 | 3500 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 11 | 14039 | 6 | 16416 | 3500 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 7 | 16416 | 3500 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 12 | 14039 | 8 | 16416 | 3501 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 9 | 16416 | 3501 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 13 | 14039 | 10 | 16416 | 3501 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 11 | 16416 | 3501 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 14 | 14039 | 12 | 16416 | 3501 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 13 | 16416 | 3501 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 15 | 14039 | 14 | 16416 | 3501 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14039 | 15 | 16416 | 3501 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VTR94020CM1 | BIL CMD - ZVQ4001 Consigne T° Repr. VTR4022 | CT | N | RES | 4 | C |  |  | °C |  | 15 | 30 | [20 empty] | POL |  |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 301 | 0 | 14050 | 0 | 16416 | 3522 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94020CM1 | BIL CMD - ZVQ4001 Consigne HR Repr. VHR4022 | CT | N | RES | 4 | C |  |  | % |  | 30 | 80 | [20 empty] | POL |  |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 302 | 0 | 14051 | 0 | 16416 | 3524 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94010CM2 | BIL CMD - ZVQ4001 Consigne T° PDR VTR4010 | CT | N | RES | 4 | C |  |  | °C |  | 7 | 25 | [20 empty] | POL |  |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 303 | 0 | 14052 | 0 | 16416 | 3526 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94010CM1 | BIL CMD - ZVQ4001 Consigne T° Soufflage VTR4010 | CT | N | RES | 4 | C |  |  | °C |  | 16 | 24 | [20 empty] | POL |  |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 304 | 0 | 14053 | 0 | 16416 | 3528 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VVU90001CM1 | BIL CMD - Conf1 - U8,CONF1 (1) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 306 | 0 | 14054 | 0 | 16416 | 3530 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VVU90001CM6 | BIL CMD - Conf2 - U8,CONF2 (2) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 306 | 1 | 14054 | 1 | 16416 | 3530 | 1 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL CMD - Conf3 (reserve) - U8,CONF3 (3) | CT | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 2 | 14054 | 2 | 16416 | 3530 | 2 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL CMD - Reserve | CT | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 306 | 3 | 14054 | NA | NA | NA | NA | EL6021 - ZVQ4001/4002 |  | UINT
VVU90003CM1 | BIL CMD - Acquit - U8,ACQUITTEMENT (8) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 306 | 4 | 14054 | 3 | 16416 | 3530 | 3 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL CMD - Acquit - Reserved for PLC | CT | [40 empty] | NA | 14054 | 4 | 16416 | 3530 | 4 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94010CM | BIL CMD - Marche VCT4010 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 306 | 5 | 14054 | 5 | 16416 | 3530 | 5 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94010CA | BIL CMD - Arret VCT4010 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC902 | HVAC BIL | BIL | 13 |  |  | 306 | 5 | 14054 | 6 | 16416 | 3530 | 6 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL CMD - Validation csg VCT4010 | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 306 | 6 | 14054 | 7 | 16416 | 3530 | 7 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94030CO | BIL CMD - Sélect. Prio.arm Hiross VCT 4030- VCT 4030/40 - U8,VCT4030 (1) / U8,VCT4040(2) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 7 | 14054 | 8 | 16416 | 3531 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94030CF | BIL CMD - Sélect. Prio.arm Hiross VCT 4030- VCT 4030/40 - U8,VCT4030 (1) / U8,VCT4040(2) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 7 | 14054 | 9 | 16416 | 3531 | 1 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94030CM | BIL CMD - Marche VCT4030 - U8,MARCHE (4) / U8,ARRET(8) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 8 | 14054 | 10 | 16416 | 3531 | 2 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94030CA | BIL CMD - Arret VCT4030 - U8,MARCHE (4) / U8,ARRET(8) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 8 | 14054 | 11 | 16416 | 3531 | 3 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94020CM | BIL CMD - Marche VCT4020 - U8,MARCHE (16) / U8,ARRET(32) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 306 | 9 | 14054 | 12 | 16416 | 3531 | 4 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94020CA | BIL CMD - Arret VCT4020 - U8,MARCHE (16) / U8,ARRET(32) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 306 | 9 | 14054 | 13 | 16416 | 3531 | 5 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94100CM | BIL CMD - Marche VCT4100 - U8,MARCHE (64) / U8,ARRET(128) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 10 | 14054 | 14 | 16416 | 3531 | 6 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94100CA | BIL CMD - Arret VCT4100 - U8,MARCHE (64) / U8,ARRET(128) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 306 | 10 | 14054 | 15 | 16416 | 3531 | 7 | EL6021 - ZVQ4001/4002 |  | UINT
VZC9402D | BIL DF automate - ZVQ4002 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 941 | 0 | 14100 | 0 | 16416 | 3622 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 1 | 16416 | 3622 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VZC9402DC1 | BIL DF Com avec ZVQ4001 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 941 | 1 | 14100 | 2 | 16416 | 3622 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 3 | 16416 | 3622 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VZC9402DC2 | BIL DF groupe redondé avec ZVQ4001 | AL | N | RES | 4 | A | [12 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 941 | 2 | 14100 | 4 | 16416 | 3622 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 5 | 16416 | 3622 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 3 | 14100 | 6 | 16416 | 3622 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 7 | 16416 | 3622 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 4 | 14100 | 8 | 16416 | 3623 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 9 | 16416 | 3623 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 5 | 14100 | 10 | 16416 | 3623 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 11 | 16416 | 3623 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 6 | 14100 | 12 | 16416 | 3623 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 13 | 16416 | 3623 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 7 | 14100 | 14 | 16416 | 3623 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14100 | 15 | 16416 | 3623 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 8 | 14101 | 0 | 16416 | 3624 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 1 | 16416 | 3624 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 9 | 14101 | 2 | 16416 | 3624 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 3 | 16416 | 3624 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL DF forcage commutateur |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 10 | 14101 | 4 | 16416 | 3624 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 5 | 16416 | 3624 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VAE94002D1 | BIL DF presence CAT 1 KUU4005 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 941 | 11 | 14101 | 6 | 16416 | 3624 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 7 | 16416 | 3624 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VAE94002D2 | BIL DF presence CAT 2 KUU4006 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 941 | 12 | 14101 | 8 | 16416 | 3625 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 9 | 16416 | 3625 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 13 | 14101 | 10 | 16416 | 3625 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 11 | 16416 | 3625 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 14 | 14101 | 12 | 16416 | 3625 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 13 | 16416 | 3625 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 941 | 15 | 14101 | 14 | 16416 | 3625 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14101 | 15 | 16416 | 3625 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94051D2 | BIL DF KKM4051 VCT4050 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 0 | 14102 | 0 | 16416 | 3626 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 1 | 16416 | 3626 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94051DI | BIL DF Press. diff. VPB4051 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 1 | 14102 | 2 | 16416 | 3626 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 3 | 16416 | 3626 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 942 | 2 | 14102 | 4 | 16416 | 3626 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 5 | 16416 | 3626 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VT94052D | BIL DF VTR4052 Sonde T° Amb. VCT4050 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 942 | 3 | 14102 | 6 | 16416 | 3626 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 7 | 16416 | 3626 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VH94052D | BIL DF Sonde HR Amb. VHR4052 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 942 | 4 | 14102 | 8 | 16416 | 3627 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 9 | 16416 | 3627 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94050DR1 | BIL DF T° PDR VTR4050 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 5 | 14102 | 10 | 16416 | 3627 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 11 | 16416 | 3627 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94051DR | BIL DF Sonde T° AS VTR4051 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 6 | 14102 | 12 | 16416 | 3627 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 13 | 16416 | 3627 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94051D1 | BIL DF KQF4051 VCT4050 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 7 | 14102 | 14 | 16416 | 3627 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14102 | 15 | 16416 | 3627 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94052DO | BIL DF ouv SM AN VSA4052 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 8 | 14103 | 0 | 16416 | 3628 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 1 | 16416 | 3628 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94052DF | BIL DF fer SM AN VSB4052 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 9 | 14103 | 2 | 16416 | 3628 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 3 | 16416 | 3628 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCN94041D | BIL DF géné. armoire VCT4040 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 942 | 10 | 14103 | 4 | 16416 | 3628 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 5 | 16416 | 3628 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VFN94050DR2 | BIL DF Sonde T° PDR VTR4050 défaut matériel | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 942 | 11 | 14103 | 6 | 16416 | 3628 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 7 | 16416 | 3628 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VT94024D | BIL DF Sonde T° Repr. VTR4024 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 942 | 12 | 14103 | 8 | 16416 | 3629 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 9 | 16416 | 3629 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VH94024D | BIL DF Sonde HR Repr. VHR4024 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 942 | 13 | 14103 | 10 | 16416 | 3629 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 11 | 16416 | 3629 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 942 | 14 | 14103 | 12 | 16416 | 3629 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 13 | 16416 | 3629 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 942 | 15 | 14103 | 14 | 16416 | 3629 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14103 | 15 | 16416 | 3629 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VTR94050T | BIL VTR4050 sonde T° pdr VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 943 | 0 | 14104 | 0 | 16416 | 3630 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94051T | BIL VTR4051 sonde T° AP VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 944 | 0 | 14105 | 0 | 16416 | 3632 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94052T1 | BIL VTR4052 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 945 | 0 | 14106 | 0 | 16416 | 3634 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94052H1 | BIL VHR4052 sonde HR% amb. VCT4050 | MA | N | RES | 4 | C |  |  | % | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 946 | 0 | 14107 | 0 | 16416 | 3636 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94053T | BIL VTR4053 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 947 | 0 | 14108 | 0 | 16416 | 3638 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94054T | BIL VTR4054 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 948 | 0 | 14109 | 0 | 16416 | 3640 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94055T | BIL VTR4055 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 949 | 0 | 14110 | 0 | 16416 | 3642 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94056T | BIL VTR4056 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 950 | 0 | 14111 | 0 | 16416 | 3644 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94057T | BIL VTR4057 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 951 | 0 | 14112 | 0 | 16416 | 3646 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94058T | BIL VTR4058 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 952 | 0 | 14113 | 0 | 16416 | 3648 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94059T | BIL VTR4059 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 953 | 0 | 14114 | 0 | 16416 | 3650 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94075T | BIL VTR4075 sonde T° amb. VCT4050 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 954 | 0 | 14115 | 0 | 16416 | 3652 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94024T | BIL VTR4024 sonde T° repris VCT4020 | MA | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 955 | 0 | 14116 | 0 | 16416 | 3654 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94024H | BIL VHR4024 sonde HR% repris VCT4020 | MA | N | RES | 4 | C |  |  | % | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC903 | HVAC BIL | BIL | 13 |  |  | 956 | 0 | 14117 | 0 | 16416 | 3656 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL KSA4050 n.ctc ouv porte VCT4020 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 957 | 0 | 14118 | 0 | 16416 | 3658 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL KUU4005 prés. U CAT1 VCT4050 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 958 | 0 | 14119 | 0 | 16416 | 3660 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL Cmde VFN4051 VCT4050 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 0 | 14120 | 0 | 16416 | 3662 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 1 | 16416 | 3662 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Pos. KQF4051 VCT4050 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 1 | 14120 | 2 | 16416 | 3662 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 3 | 16416 | 3662 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94052O | BIL Cmde ouv SM AN VRP4052 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 959 | 2 | 14120 | 4 | 16416 | 3662 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 5 | 16416 | 3662 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94052F | BIL Cmde fer SM AN VRP4052 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 959 | 3 | 14120 | 6 | 16416 | 3662 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 7 | 16416 | 3662 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VRP94052DI | BIL Discordance VRP4052 | CR | N | CAL | 4 | C | [22 empty] | AND |  | VRP94052O ; VRP94052F |  |  |  |  | HVAC904 | HVAC BIL | BIL | 13
VRP94052AE | BIL Aucun Etat VRP4052 | CR | N | CAL | 4 | C | [22 empty] | NOR |  | VRP94052O ; VRP94052F |  |  |  |  | HVAC904 | HVAC BIL | BIL | 13
VCT94051M | BIL Press. diff. VPB4051 | CR | N | RES | 4 | [27 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 959 | 4 | 14120 | 8 | 16416 | 3663 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 9 | 16416 | 3663 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Prés. CAT2 KUU4006 |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 5 | 14120 | 10 | 16416 | 3663 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 11 | 16416 | 3663 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Voy. porte ouv. KHL4050 |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 6 | 14120 | 12 | 16416 | 3663 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 13 | 16416 | 3663 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Df Géné. Armoire VCT4040 |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 7 | 14120 | 14 | 16416 | 3663 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14120 | 15 | 16416 | 3663 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 8 | 14121 | 0 | 16416 | 3664 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 1 | 16416 | 3664 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 9 | 14121 | 2 | 16416 | 3664 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 3 | 16416 | 3664 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 10 | 14121 | 4 | 16416 | 3664 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 5 | 16416 | 3664 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 11 | 14121 | 6 | 16416 | 3664 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 7 | 16416 | 3664 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 12 | 14121 | 8 | 16416 | 3665 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 9 | 16416 | 3665 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 13 | 14121 | 10 | 16416 | 3665 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 11 | 16416 | 3665 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 14 | 14121 | 12 | 16416 | 3665 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 13 | 16416 | 3665 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 959 | 15 | 14121 | 14 | 16416 | 3665 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14121 | 15 | 16416 | 3665 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
GER94051T | BIL GWC4051 Vanne EG (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 960 | 0 | 14122 | 0 | 16416 | 3666 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94051T | BIL CWC4051 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 961 | 0 | 14123 | 0 | 16416 | 3668 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94053T | BIL CWC4053 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 962 | 0 | 14124 | 0 | 16416 | 3670 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94054T | BIL CWC4054 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 963 | 0 | 14125 | 0 | 16416 | 3672 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94055T | BIL CWC4055 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 964 | 0 | 14126 | 0 | 16416 | 3674 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94056T | BIL CWC4056 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 965 | 0 | 14127 | 0 | 16416 | 3676 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94057T | BIL CWC4057 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 966 | 0 | 14128 | 0 | 16416 | 3678 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94058T | BIL CWC4058 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 967 | 0 | 14129 | 0 | 16416 | 3680 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94059T | BIL CWC4059 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 968 | 0 | 14130 | 0 | 16416 | 3682 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
CER94075T | BIL CWC4075 Vanne EC (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 969 | 0 | 14131 | 0 | 16416 | 3684 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
GER94052T | BIL GWC4052 Vanne EG (% ouv) VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 970 | 0 | 14132 | 0 | 16416 | 3686 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 971 | 0 | 14133 | 0 | 16416 | 3688 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL VFN4051 Vent. cde marche VCT4050 | MA | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 972 | 0 | 14134 | 0 | 16416 | 3690 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL VRP4052 SM AN cde ouv VCT4050 | MA | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 973 | 0 | 14135 | 0 | 16416 | 3692 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL VFN4041 cde marche Arm. VCT4040 | MA | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 974 | 0 | 14136 | 0 | 16416 | 3694 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
| BIL KLH4050 Voyant défaut porte ouve | MA | N | RES | 4 | [27 empty] | POL |  |  |  |  | BIL | 13 |  |  | 975 | 0 | 14137 | 0 | 16416 | 3696 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VCT94053DR | BIL DF Sonde T° Amb. VTR4053 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 0 | 14138 | 0 | 16416 | 3698 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 1 | 16416 | 3698 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94054DR | BIL DF Sonde T° Amb. VTR4054 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 1 | 14138 | 2 | 16416 | 3698 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 3 | 16416 | 3698 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94055DR | BIL DF Sonde T° Amb. VTR4055 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 2 | 14138 | 4 | 16416 | 3698 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 5 | 16416 | 3698 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94056DR | BIL DF Sonde T° Amb. VTR4056 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 3 | 14138 | 6 | 16416 | 3698 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 7 | 16416 | 3698 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94057DR | BIL DF Sonde T° Amb. VTR4057 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 4 | 14138 | 8 | 16416 | 3699 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 9 | 16416 | 3699 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94058DR | BIL DF Sonde T° Amb. VTR4058 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 5 | 14138 | 10 | 16416 | 3699 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 11 | 16416 | 3699 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94059DR | BIL DF Sonde T° Amb. VTR4059 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 6 | 14138 | 12 | 16416 | 3699 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 13 | 16416 | 3699 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VCT94075DR | BIL DF Sonde T° Amb. VTR4075 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 976 | 7 | 14138 | 14 | 16416 | 3699 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14138 | 15 | 16416 | 3699 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 8 | 14139 | 0 | 16416 | 3700 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 1 | 16416 | 3700 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 9 | 14139 | 2 | 16416 | 3700 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 3 | 16416 | 3700 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 10 | 14139 | 4 | 16416 | 3700 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 5 | 16416 | 3700 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 11 | 14139 | 6 | 16416 | 3700 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 7 | 16416 | 3700 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 12 | 14139 | 8 | 16416 | 3701 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 9 | 16416 | 3701 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 13 | 14139 | 10 | 16416 | 3701 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 11 | 16416 | 3701 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 14 | 14139 | 12 | 16416 | 3701 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 13 | 16416 | 3701 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 976 | 15 | 14139 | 14 | 16416 | 3701 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14139 | 15 | 16416 | 3701 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VTR94050T1 | BIL ZVQ4002 Consigne T° Amb. Conf.1 VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 331 | 0 | 14140 | 0 | 16416 | 3702 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94050H1 | BIL ZVQ4002 Consigne HR Amb. Conf.1 VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 332 | 0 | 14141 | 0 | 16416 | 3704 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94050T3 | BIL ZVQ4002 Consigne T° PDR VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 333 | 0 | 14142 | 0 | 16416 | 3706 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94050T2 | BIL ZVQ4002 Consigne T° Amb. Conf.2 VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 334 | 0 | 14143 | 0 | 16416 | 3708 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94050H2 | BIL ZVQ4002 Consigne HR Amb. Conf.2 VCT4050 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 335 | 0 | 14144 | 0 | 16416 | 3710 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL ZVQ4002 Consigne T° AS VCT4050 | MA | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 336 | 0 | 14145 | 0 | 16416 | 3712 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VVU90001D2 | BIL ZVQ4002 Conf1 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 337 | 0 | 14146 | 0 | 16416 | 3714 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 1 | 16416 | 3714 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU90001D7 | BIL ZVQ4002 Conf2 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 337 | 1 | 14146 | 2 | 16416 | 3714 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 3 | 16416 | 3714 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Conf3 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 2 | 14146 | 4 | 16416 | 3714 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 5 | 16416 | 3714 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 3 | 14146 | 6 | 16416 | 3714 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 7 | 16416 | 3714 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU90003D2 | BIL ZVQ4002 Acquit | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 337 | 4 | 14146 | 8 | 16416 | 3715 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 9 | 16416 | 3715 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU94050D | BIL Marche VCT4050 | CR | N | RES | 4 | [27 empty] | POL | 2000 |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 337 | 5 | 14146 | 10 | 16416 | 3715 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 11 | 16416 | 3715 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| BIL Validation csg VCT4050 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 6 | 14146 | 12 | 16416 | 3715 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 13 | 16416 | 3715 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU940430D1 | BIL Sélect. Prio.arm Hiross | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 337 | 7 | 14146 | 14 | 16416 | 3715 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14146 | 15 | 16416 | 3715 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VVU94040D | BIL Marche VCT4040 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 337 | 8 | 14147 | 0 | 16416 | 3716 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 1 | 16416 | 3716 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 9 | 14147 | 2 | 16416 | 3716 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 3 | 16416 | 3716 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 10 | 14147 | 4 | 16416 | 3716 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 5 | 16416 | 3716 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 11 | 14147 | 6 | 16416 | 3716 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 7 | 16416 | 3716 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 12 | 14147 | 8 | 16416 | 3717 | 0 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 9 | 16416 | 3717 | 1 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 13 | 14147 | 10 | 16416 | 3717 | 2 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 11 | 16416 | 3717 | 3 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 14 | 14147 | 12 | 16416 | 3717 | 4 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 13 | 16416 | 3717 | 5 | EL6021 - ZVQ4001/4002 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 15 | 14147 | 14 | 16416 | 3717 | 6 | EL6021 - ZVQ4001/4002 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14147 | 15 | 16416 | 3717 | 7 | EL6021 - ZVQ4001/4002 |  | BITVAL
VTR94050CM1 | BIL CMD - ZVQ4002 Consigne T° Amb. Conf.1 VCT4050 | CT | N | RES | 4 | C |  |  | °C |  | 0 | 50 | [20 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 331 | 0 | 14160 | 0 | 16416 | 3742 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94050CM1 | BIL CMD - ZVQ4002 Consigne HR Amb. Conf.1 VCT4050 | CT | N | RES | 4 | C |  |  | % |  | 0 | 100 | [20 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 332 | 0 | 14161 | 0 | 16416 | 3744 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94050CM3 | BIL CMD - ZVQ4002 Consigne T° PDR VCT4050 | CT | N | RES | 4 | C |  |  | °C |  | 16 | 24 | [20 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 333 | 0 | 14162 | 0 | 16416 | 3746 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VTR94050CM2 | BIL CMD - ZVQ4002 Consigne T° Amb. Conf.2 VCT4050 | CT | N | RES | 4 | C |  |  | °C |  | 0 | 50 | [20 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 334 | 0 | 14163 | 0 | 16416 | 3748 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VHR94050CM2 | BIL CMD - ZVQ4002 Consigne HR Amb. Conf.2 VCT4050 | CT | N | RES | 4 | C |  |  | % |  | 0 | 100 | [20 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 335 | 0 | 14164 | 0 | 16416 | 3750 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL CMD - ZVQ4002 ConsigneT° AS VCT4050 | CT | N | RES | 4 | C |  |  | °C |  | 10 | 30 | [25 empty] | BIL | 13 |  |  | 336 | 0 | 14165 | 0 | 16416 | 3752 | 0 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VVU90001CM2 | BIL CMD - Conf1 - U8,CONF1 (1) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 337 | 0 | 14166 | 0 | 16416 | 3754 | 0 | EL6021 - ZVQ4001/4002 |  | UINT | 1
VVU90001CM7 | BIL CMD - Conf2 - U8,CONF2 (2) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 337 | 1 | 14166 | 1 | 16416 | 3754 | 1 | EL6021 - ZVQ4001/4002 |  | UINT | 2
| BIL CMD - Conf3 (reserve) - U8,CONF3 (3) | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 337 | 2 | 14166 | 2 | 16416 | 3754 | 2 | EL6021 - ZVQ4001/4002 |  | UINT | 4 | Non preso in carico dal VMC
| BIL CMD - Reserve | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 337 | 3 | 14166 | NA | NA | NA | NA | EL6021 - ZVQ4001/4002 |  | UINT
VVU90003CM2 | BIL CMD - Acquit - U8,ACQUITTEMENT (16) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 337 | 4 | 14166 | 3 | 16416 | 3754 | 3 | EL6021 - ZVQ4001/4002 |  | UINT | 8
| BIL CMD - Acquit - Reserved for PLC | CT | [40 empty] | NA | 14166 | 4 | 16416 | 3754 | 4 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94050CM | BIL CMD - Marche VCT4050 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 337 | 5 | 14166 | 5 | 16416 | 3754 | 5 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94050CA | BIL CMD - Arret VCT4050 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC904 | HVAC BIL | BIL | 13 |  |  | 337 | 5 | 14166 | 6 | 16416 | 3754 | 6 | EL6021 - ZVQ4001/4002 |  | UINT
| BIL CMD - Validation csg VCT4050 | CT | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 337 | 6 | 14166 | 7 | 16416 | 3754 | 7 | EL6021 - ZVQ4001/4002 |  | UINT |  | Non preso in carico dal VMC
VVU94040CO | BIL CMD - Sélect. Prio.arm Hiross VCT 4030/40 - U8,VCT4030 (1) / U8,VCT4040(2) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 337 | 7 | 14166 | 8 | 16416 | 3755 | 0 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94040CF | BIL CMD - Sélect. Prio.arm Hiross VCT 4030/40 - U8,VCT4030 (1) / U8,VCT4040(2) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 337 | 7 | 14166 | 9 | 16416 | 3755 | 1 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94040CM | BIL CMD - Marche VCT4040 - U8,MARCHE (4) / U8,ARRET(8) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 337 | 8 | 14166 | 10 | 16416 | 3755 | 2 | EL6021 - ZVQ4001/4002 |  | UINT
VVU94040CA | BIL CMD - Arret VCT4040 - U8,MARCHE (4) / U8,ARRET(8) | CT | N | RES | 4 | C | [26 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 337 | 8 | 14166 | 11 | 16416 | 3755 | 3 | EL6021 - ZVQ4001/4002 |  | UINT
VZC9403D | BIL DF automate - ZVQ4003 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 981 | 0 | 14200 | 0 | 16416 | 3822 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 1 | 16416 | 3822 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 1 | 14200 | 2 | 16416 | 3822 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 3 | 16416 | 3822 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 2 | 14200 | 4 | 16416 | 3822 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 5 | 16416 | 3822 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 3 | 14200 | 6 | 16416 | 3822 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 7 | 16416 | 3822 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 4 | 14200 | 8 | 16416 | 3823 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 9 | 16416 | 3823 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 5 | 14200 | 10 | 16416 | 3823 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 11 | 16416 | 3823 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 6 | 14200 | 12 | 16416 | 3823 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 13 | 16416 | 3823 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 7 | 14200 | 14 | 16416 | 3823 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14200 | 15 | 16416 | 3823 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 8 | 14201 | 0 | 16416 | 3824 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 1 | 16416 | 3824 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 9 | 14201 | 2 | 16416 | 3824 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 3 | 16416 | 3824 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL DF forcage commutateur | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 10 | 14201 | 4 | 16416 | 3824 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 5 | 16416 | 3824 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VAE94003D1 | BIL DF Prés. CAT2 KUU4011 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 981 | 11 | 14201 | 6 | 16416 | 3824 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 7 | 16416 | 3824 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 12 | 14201 | 8 | 16416 | 3825 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 9 | 16416 | 3825 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 13 | 14201 | 10 | 16416 | 3825 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 11 | 16416 | 3825 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 14 | 14201 | 12 | 16416 | 3825 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 13 | 16416 | 3825 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 981 | 15 | 14201 | 14 | 16416 | 3825 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14201 | 15 | 16416 | 3825 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94071D2 | BIL DF KKM4071 VCT4070 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 0 | 14202 | 0 | 16416 | 3826 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 1 | 16416 | 3826 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94071DI1 | BIL DF Press. diff. VPB4071 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 1 | 14202 | 2 | 16416 | 3826 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 3 | 16416 | 3826 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94070DR1 | BIL DF T° PDR VTR4070 | AL | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 2 | 14202 | 4 | 16416 | 3826 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 5 | 16416 | 3826 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94071DT | BIL DF Sonde T° AS VTR4071 | AL | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 3 | 14202 | 6 | 16416 | 3826 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 7 | 16416 | 3826 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94072DO1 | BIL DF ouv SM AN VSA4072 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 4 | 14202 | 8 | 16416 | 3827 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 9 | 16416 | 3827 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94072DF1 | BIL DF fer SM AN VSB4072 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 5 | 14202 | 10 | 16416 | 3827 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 11 | 16416 | 3827 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VT94082D | BIL DF Sonde T° Repr. VTR4082 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 982 | 6 | 14202 | 12 | 16416 | 3827 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 13 | 16416 | 3827 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VAR94072DT | BIL DF Sonde T° AN VTR4072 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 7 | 14202 | 14 | 16416 | 3827 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14202 | 15 | 16416 | 3827 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VH94082D | BIL DF Sonde HR Repr. VHR4082 | AL | N | RES | 4 | [27 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 982 | 8 | 14203 | 0 | 16416 | 3828 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 1 | 16416 | 3828 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94071D1 | BIL DF KQF4071 VFN4071 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 9 | 14203 | 2 | 16416 | 3828 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 3 | 16416 | 3828 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94081D1 | BIL DF KQF4081 VFN4081 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 982 | 10 | 14203 | 4 | 16416 | 3828 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 5 | 16416 | 3828 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 982 | 11 | 14203 | 6 | 16416 | 3828 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 7 | 16416 | 3828 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94081D2 | BIL DF KKM4081 VTC4080 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 982 | 12 | 14203 | 8 | 16416 | 3829 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 9 | 16416 | 3829 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94081DI1 | BIL DF Press. diff. VPB4081 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 982 | 13 | 14203 | 10 | 16416 | 3829 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 11 | 16416 | 3829 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94070DR2 | BIL DF Sonde T° PDR VTR4070 défaut matériel | AL | N | RES | 4 | C |  |  | °C | [9 empty] | C | [13 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 982 | 14 | 14203 | 12 | 16416 | 3829 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 13 | 16416 | 3829 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 982 | 15 | 14203 | 14 | 16416 | 3829 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14203 | 15 | 16416 | 3829 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94070T | BIL VTR4070 Sonde T° pdr VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 983 | 0 | 14204 | 0 | 16416 | 3830 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94071T | BIL VTR4071 Sonde T° puls VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 984 | 0 | 14205 | 0 | 16416 | 3832 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94072T | BIL VTR4072 Sonde T° AN VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 985 | 0 | 14206 | 0 | 16416 | 3834 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL KKL4112 BP Clim interne L.Repli | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 986 | 0 | 14207 | 0 | 16416 | 3836 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL KKM4071 re KM Vent VCT4070 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 987 | 0 | 14208 | 0 | 16416 | 3838 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL KQF4071 Protection Vent. VCT4070 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 988 | 0 | 14209 | 0 | 16416 | 3840 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VRP94072F1 | BIL VSB4072 SM AN Ferm VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 989 | 0 | 14210 | 0 | 16416 | 3842 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Il VMC tratta la misura come booleana prendendo il primo bit della word
VRP94072O1 | BIL VSA4072 SM AN fdc ouv VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 990 | 0 | 14211 | 0 | 16416 | 3844 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Il VMC tratta la misura come booleana prendendo il primo bit della word
VRP94072DI1 | BIL Discordance VSB 4072 VSA4072 | CR | N | CAL | 4 | C | [22 empty] | AND |  | VRP94072O1 ; VRP94072F1 |  |  |  |  | HVAC908 | HVAC BIL | BIL | 13
VRP94072AE1 | BIL Aucun Etat VSB 4072 VSA4072 | CR | N | CAL | 4 | C | [22 empty] | NOR |  | VRP94072O1 ; VRP94072F1 |  |  |  |  | HVAC908 | HVAC BIL | BIL | 13
| BIL KKM4081 re KM Vent VCT4080 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 991 | 0 | 14212 | 0 | 16416 | 3846 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL KQF4081 Protection Extra. VCT4080 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 992 | 0 | 14213 | 0 | 16416 | 3848 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VCT94081M1 | BIL VPB4081 Pressostat diff. VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 993 | 0 | 14214 | 0 | 16416 | 3850 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Il VMC tratta la misura come booleana prendendo il primo bit della word
| BIL KUU4011 prés. U CAT2 VCT4080 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 994 | 0 | 14215 | 0 | 16416 | 3852 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VCT94071M1 | BIL VPB4071 Pressostat diff. VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 995 | 0 | 14216 | 0 | 16416 | 3854 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Il VMC tratta la misura come booleana prendendo il primo bit della word
VTR94082T | BIL VTR4082 Sonde T° repris VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 996 | 0 | 14217 | 0 | 16416 | 3856 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94082H | BIL VHR4082 Sonde HR% repris VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 997 | 0 | 14218 | 0 | 16416 | 3858 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL KAQ4002 BP acquittement ZVQ4003 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 998 | 0 | 14219 | 0 | 16416 | 3860 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
CER94071T1 | BIL CWC4071 vanne EC (%ouv) VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 1000 | 0 | 14220 | 0 | 16416 | 3862 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94081T1 | BIL CWC4081 vanne EC (%ouv) VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 1001 | 0 | 14221 | 0 | 16416 | 3864 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
GER94081T1 | BIL GWC4081 vanne EG (%ouv) VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 1002 | 0 | 14222 | 0 | 16416 | 3866 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
GER94071T1 | BIL GWC4071 vanne EG (%ouv) VCT4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 1003 | 0 | 14223 | 0 | 16416 | 3868 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL VFN4071 Vent. Cde marche VCT4070 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1004 | 0 | 14224 | 0 | 16416 | 3870 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL VFN4081 Vent. Cde marche VCT4080 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1005 | 0 | 14225 | 0 | 16416 | 3872 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL VRP4072 SM Air neuf VCT4070 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1006 | 0 | 14226 | 0 | 16416 | 3874 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VTR94080 | BIL ZVQ4003 Consigne T° Repr. VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 361 | 0 | 14227 | 0 | 16416 | 3876 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94080 | BIL ZVQ4003 Consigne HR Repr. VCT4080 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 362 | 0 | 14228 | 0 | 16416 | 3878 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94070T2 | BIL ZVQ4003 Consigne T° PDR VTR4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | C | BIL | 13 |  |  | 363 | 0 | 14229 | 0 | 16416 | 3880 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001D3 | BIL ZVQ4003 Conf1 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 364 | 0 | 14230 | 0 | 16416 | 3882 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 1 | 16416 | 3882 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90001D8 | BIL ZVQ4003 Conf2 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 364 | 1 | 14230 | 2 | 16416 | 3882 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 3 | 16416 | 3882 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Conf3 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 2 | 14230 | 4 | 16416 | 3882 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 5 | 16416 | 3882 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 3 | 14230 | 6 | 16416 | 3882 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 7 | 16416 | 3882 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90003D3 | BIL ZVQ4003 Acquit | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 364 | 4 | 14230 | 8 | 16416 | 3883 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 9 | 16416 | 3883 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU94070D | BIL Marche VCT4070 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 364 | 5 | 14230 | 10 | 16416 | 3883 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 11 | 16416 | 3883 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Validation csg VCT4070 | CR | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 6 | 14230 | 12 | 16416 | 3883 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 13 | 16416 | 3883 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU94080D | BIL Marche VCT4080 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 364 | 7 | 14230 | 14 | 16416 | 3883 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14230 | 15 | 16416 | 3883 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90002D | BIL ZVQ4003 Passage clim interne | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  |  |  | BIL | 13 |  |  | 364 | 8 | 14231 | 0 | 16416 | 3884 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 1 | 16416 | 3884 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 9 | 14231 | 2 | 16416 | 3884 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 3 | 16416 | 3884 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 10 | 14231 | 4 | 16416 | 3884 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 5 | 16416 | 3884 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 11 | 14231 | 6 | 16416 | 3884 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 7 | 16416 | 3884 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 12 | 14231 | 8 | 16416 | 3885 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 9 | 16416 | 3885 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 13 | 14231 | 10 | 16416 | 3885 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 11 | 16416 | 3885 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 14 | 14231 | 12 | 16416 | 3885 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 13 | 16416 | 3885 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 364 | 15 | 14231 | 14 | 16416 | 3885 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14231 | 15 | 16416 | 3885 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94070T1 | BIL ZVQ4003 T° Soufflage VTR4070 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC907 | HVAC BIL | BIL | 13 |  |  | 365 | 0 | 14232 | 0 | 16416 | 3886 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94080CM1 | BIL CMD - ZVQ4003 T° Repr. VCT4080 | CT | N | RES | 4 | C |  |  | °C |  | 0 | 50 | [20 empty] | POL |  |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 361 | 0 | 14233 | 0 | 16416 | 3888 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94080CM1 | BIL CMD - ZVQ4003 HR Repr. VCT4080 | CT | N | RES | 4 | C |  |  | % |  | 0 | 100 | [20 empty] | POL |  |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 362 | 0 | 14234 | 0 | 16416 | 3890 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94070CM2 | BIL CMD - ZVQ4003 T° PDR VTR4070 | CT | N | RES | 4 | C |  |  | °C |  | 7 | 25 | [20 empty] | POL |  |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 363 | 0 | 14235 | 0 | 16416 | 3892 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94070CM1 | BIL CMD - ZVQ4003 T° Soufflage VTR4070 | CT | N | RES | 4 | C |  |  | °C |  | 16 | 24 | [20 empty] | POL |  |  | HVAC908 | HVAC BIL | BIL | 13 |  |  | 365 | 0 | 14236 | 0 | 16416 | 3894 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001CM3 | BIL CMD - ZVQ4003 Conf1 - U8,CONF1 (1) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 0 | 14237 | 0 | 16416 | 3896 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001CM8 | BIL CMD - ZVQ4003 Conf2 - U8,CONF2 (2) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 1 | 14237 | 1 | 16416 | 3896 | 1 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - ZVQ4003 Conf3 - U8,CONF3 (3) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 2 | 14237 | 2 | 16416 | 3896 | 2 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL CMD - Reserve | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 364 | 3 | 14237 | NA | NA | NA | NA | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VVU90003CM3 | BIL CMD - Acquit - U8,ACQUITTEMENT (16) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 4 | 14237 | 3 | 16416 | 3896 | 3 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - Acquit - Reserved for PLC | [41 empty] | NA | 14237 | 4 | 16416 | 3896 | 4 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94070CM | BIL CMD - Marche VCT4070 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 5 | 14237 | 5 | 16416 | 3896 | 5 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94070CA | BIL CMD - Arret VCT4070 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 5 | 14237 | 6 | 16416 | 3896 | 6 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - Validation csg VCT4070 | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 364 | 6 | 14237 | 7 | 16416 | 3896 | 7 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VVU94080CM | BIL CMD - Marche VCT4080 - U8,VCT4030 (1) / U8,VCT4040(2) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC08 | HVAC BIL | BIL | 13 |  |  | 364 | 7 | 14237 | 8 | 16416 | 3897 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94080CA | BIL CMD - Arret VCT4080 - U8,VCT4030 (1) / U8,VCT4040(2) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC08 | HVAC BIL | BIL | 13 |  |  | 364 | 7 | 14237 | 9 | 16416 | 3897 | 1 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU940002CM1 | BIL CMD - ZVQ4003 Passage clim interne mode ope - MODE OPE(4) / MODE ECO(8) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 8 | 14237 | 10 | 16416 | 3897 | 2 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU940002CA1 | BIL CMD - ZVQ4003 Passage clim interne mode eco - MODE OPE(4) / MODE ECO(8) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 364 | 8 | 14237 | 11 | 16416 | 3897 | 3 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VZC9404D | BIL DF automate - ZVQ4004 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 1021 | 0 | 14250 | 0 | 16416 | 3922 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 1 | 16416 | 3922 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 1 | 14250 | 2 | 16416 | 3922 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 3 | 16416 | 3922 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 2 | 14250 | 4 | 16416 | 3922 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 5 | 16416 | 3922 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 3 | 14250 | 6 | 16416 | 3922 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 7 | 16416 | 3922 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 4 | 14250 | 8 | 16416 | 3923 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 9 | 16416 | 3923 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 5 | 14250 | 10 | 16416 | 3923 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 11 | 16416 | 3923 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 6 | 14250 | 12 | 16416 | 3923 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 13 | 16416 | 3923 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 7 | 14250 | 14 | 16416 | 3923 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14250 | 15 | 16416 | 3923 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 8 | 14251 | 0 | 16416 | 3924 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 1 | 16416 | 3924 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 9 | 14251 | 2 | 16416 | 3924 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 3 | 16416 | 3924 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL DF forcage commutateur | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 10 | 14251 | 4 | 16416 | 3924 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 5 | 16416 | 3924 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VAE94004D1 | BIL DF Prés. CAT1 KUU4007 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 1021 | 11 | 14251 | 6 | 16416 | 3924 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 7 | 16416 | 3924 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 12 | 14251 | 8 | 16416 | 3925 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 9 | 16416 | 3925 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 13 | 14251 | 10 | 16416 | 3925 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 11 | 16416 | 3925 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 14 | 14251 | 12 | 16416 | 3925 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 13 | 16416 | 3925 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1021 | 15 | 14251 | 14 | 16416 | 3925 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14251 | 15 | 16416 | 3925 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94061D2 | BIL DF KKM4061 VCT4060 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 0 | 14252 | 0 | 16416 | 3926 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 1 | 16416 | 3926 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94061DI | BIL DF Press. diff. VPB4061 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 1 | 14252 | 2 | 16416 | 3926 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 3 | 16416 | 3926 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1022 | 2 | 14252 | 4 | 16416 | 3926 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 5 | 16416 | 3926 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VT94062D | BIL DF Sonde T° Amb. VTR4062 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1022 | 3 | 14252 | 6 | 16416 | 3926 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 7 | 16416 | 3926 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VH94062D | BIL DF Sonde HR Amb. VHR4062 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1022 | 4 | 14252 | 8 | 16416 | 3927 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 9 | 16416 | 3927 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94060DR1 | BIL DF T° PDR VTR4060 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 5 | 14252 | 10 | 16416 | 3927 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 11 | 16416 | 3927 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94061DR | BIL DF Sonde T° AS VTR4061 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 6 | 14252 | 12 | 16416 | 3927 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 13 | 16416 | 3927 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94060DR2 | BIL DF Sonde T° PDR VTR4060 défaut matériel | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 7 | 14252 | 14 | 16416 | 3927 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14252 | 15 | 16416 | 3927 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94062DO | BIL DF ouv SM AN VSA4062 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 8 | 14253 | 0 | 16416 | 3928 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 1 | 16416 | 3928 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94062DF | BIL DF ferm SM AN VSB4062 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 9 | 14253 | 2 | 16416 | 3928 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 3 | 16416 | 3928 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1022 | 10 | 14253 | 4 | 16416 | 3928 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 5 | 16416 | 3928 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1022 | 11 | 14253 | 6 | 16416 | 3928 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 7 | 16416 | 3928 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VT94094D | BIL DF Sonde T° Repr. VTR4094 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1022 | 12 | 14253 | 8 | 16416 | 3929 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 9 | 16416 | 3929 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VH94094D | BIL DF Sonde HR Repr. VHR4094 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1022 | 13 | 14253 | 10 | 16416 | 3929 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 11 | 16416 | 3929 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94061D1 | BIL DF KQF4061 VCT4060 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1022 | 14 | 14253 | 12 | 16416 | 3929 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14253 | 13 | 16416 | 3929 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1022 | 15 | 14253 | 14 | 16416 | 3929 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [31 empty] | POL |  |  |  |  | BIL | 13 |  |  |  |  | 14253 | 15 | 16416 | 3929 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94060T | BIL VTR4060 sonde T° pdr VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1023 | 0 | 14254 | 0 | 16416 | 3930 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94061T | BIL VTR4061 sonde T° AP VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1024 | 0 | 14255 | 0 | 16416 | 3932 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94062T1 | BIL VTR4062 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1025 | 0 | 14256 | 0 | 16416 | 3934 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94062H1 | BIL VHR4062 sonde HR% amb. VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1026 | 0 | 14257 | 0 | 16416 | 3936 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94063T | BIL VTR4063 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1027 | 0 | 14258 | 0 | 16416 | 3938 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94064T | BIL VTR4064 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1028 | 0 | 14259 | 0 | 16416 | 3940 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94065T | BIL VTR4065 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1029 | 0 | 14260 | 0 | 16416 | 3942 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94066T | BIL VTR4066 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1030 | 0 | 14261 | 0 | 16416 | 3944 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94067T | BIL VTR4067 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1031 | 0 | 14262 | 0 | 16416 | 3946 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94068T | BIL VTR4068 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1032 | 0 | 14263 | 0 | 16416 | 3948 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94069T | BIL VTR4069 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1033 | 0 | 14264 | 0 | 16416 | 3950 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94076T | BIL VTR4076 sonde T° amb. VCT4060 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1034 | 0 | 14265 | 0 | 16416 | 3952 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94094T | BIL VTR4094 sonde T° repris VCT4090 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1035 | 0 | 14266 | 0 | 16416 | 3954 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94094H | BIL VHR4094 sonde HR% repris VCT4090 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1036 | 0 | 14267 | 0 | 16416 | 3956 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL KSA4050 n.ctc ouv porte VCT4060 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1037 | 0 | 14268 | 0 | 16416 | 3958 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL KUU4006 prés. U CAT1 VCT4060 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1038 | 0 | 14269 | 0 | 16416 | 3960 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL Cmde VFN4061 VCT4060 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 0 | 14270 | 0 | 16416 | 3962 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 1 | 16416 | 3962 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Pos. KQF4061 VCT4060 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 1 | 14270 | 2 | 16416 | 3962 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 3 | 16416 | 3962 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94062O | BIL Cmde ouv SM AN VRP4062 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC | BIL | 13 |  |  | 1039 | 2 | 14270 | 4 | 16416 | 3962 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 5 | 16416 | 3962 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94062F | BIL Cmde fer SM AN VRP4062 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC | BIL | 13 |  |  | 1039 | 3 | 14270 | 6 | 16416 | 3962 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 7 | 16416 | 3962 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VRP94062AE | BIL Aucun Etat VRP4062 | CR | N | CAL | 4 | C | [22 empty] | NOR |  | VRP94062O ; VRP94062F |  |  |  |  | HVAC905 | HVAC BIL | BIL | 13
VRP94062DI | BIL Discordance VRP4062 | CR | N | CAL | 4 | C | [22 empty] | AND |  | VRP94062O ; VRP94062F |  |  |  |  | HVAC905 | HVAC BIL | BIL | 13
VCT94061M | BIL Press. diff. VPB4061 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1039 | 4 | 14270 | 8 | 16416 | 3963 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 9 | 16416 | 3963 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 5 | 14270 | 10 | 16416 | 3963 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 11 | 16416 | 3963 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Voy. porte ouv. KHL4060 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 6 | 14270 | 12 | 16416 | 3963 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 13 | 16416 | 3963 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 7 | 14270 | 14 | 16416 | 3963 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14270 | 15 | 16416 | 3963 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 8 | 14271 | 0 | 16416 | 3964 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 1 | 16416 | 3964 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 9 | 14271 | 2 | 16416 | 3964 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 3 | 16416 | 3964 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 10 | 14271 | 4 | 16416 | 3964 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 5 | 16416 | 3964 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 11 | 14271 | 6 | 16416 | 3964 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 7 | 16416 | 3964 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 12 | 14271 | 8 | 16416 | 3965 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 9 | 16416 | 3965 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 13 | 14271 | 10 | 16416 | 3965 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 11 | 16416 | 3965 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 14 | 14271 | 12 | 16416 | 3965 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 13 | 16416 | 3965 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1039 | 15 | 14271 | 14 | 16416 | 3965 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14271 | 15 | 16416 | 3965 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
GER94061T | BIL GWC4061 Vanne EG (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1040 | 0 | 14272 | 0 | 16416 | 3966 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94061T | BIL CWC4061 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1041 | 0 | 14273 | 0 | 16416 | 3968 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94063T | BIL CWC4063 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1042 | 0 | 14274 | 0 | 16416 | 3970 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94064T | BIL CWC4064 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1043 | 0 | 14275 | 0 | 16416 | 3972 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94065T | BIL CWC4065 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1044 | 0 | 14276 | 0 | 16416 | 3974 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94066T | BIL CWC4066 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1045 | 0 | 14277 | 0 | 16416 | 3976 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94067T | BIL CWC4067 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1046 | 0 | 14278 | 0 | 16416 | 3978 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94068T | BIL CWC4068 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1047 | 0 | 14279 | 0 | 16416 | 3980 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94069T | BIL CWC4069 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1048 | 0 | 14280 | 0 | 16416 | 3982 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
CER94076T | BIL CWC4076 Vanne EC (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1049 | 0 | 14281 | 0 | 16416 | 3984 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
GER94062T | BIL GWC4062 Vanne EG (% ouv) VCT4060 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1050 | 0 | 14282 | 0 | 16416 | 3986 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| Reserve |  | N | RES | 4 | [30 empty] | HVAC905 | HVAC BIL | BIL | 13 |  |  | 1051 | 0 | 14283 | 0 | 16416 | 3988 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL VFN4061 Ventilateur VCT4060 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1052 | 0 | 14284 | 0 | 16416 | 3990 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL VRP4062 SM AN cde ouv VCT4060 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1053 | 0 | 14285 | 0 | 16416 | 3992 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL KHL4060 Vy Df porte ouv VCT4060 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1054 | 0 | 14286 | 0 | 16416 | 3994 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VCT94063DR | BIL DF Sonde T° Amb. VTR4063 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 0 | 14287 | 0 | 16416 | 3996 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 1 | 16416 | 3996 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94064DR | BIL DF Sonde T° Amb. VTR4064 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 1 | 14287 | 2 | 16416 | 3996 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 3 | 16416 | 3996 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94065DR | BIL DF Sonde T° Amb. VTR4065 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 2 | 14287 | 4 | 16416 | 3996 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 5 | 16416 | 3996 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94066DR | BIL DF Sonde T° Amb. VTR4066 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 3 | 14287 | 6 | 16416 | 3996 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 7 | 16416 | 3996 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94067DR | BIL DF Sonde T° Amb. VTR4067 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 4 | 14287 | 8 | 16416 | 3997 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 9 | 16416 | 3997 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94068DR | BIL DF Sonde T° Amb. VTR4068 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 5 | 14287 | 10 | 16416 | 3997 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 11 | 16416 | 3997 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94069DR | BIL DF Sonde T° Amb. VTR4069 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 6 | 14287 | 12 | 16416 | 3997 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 13 | 16416 | 3997 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VCT94076DR | BIL DF Sonde T° Amb. VTR4076 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC906 | HVAC BIL | BIL | 13 |  |  | 1055 | 7 | 14287 | 14 | 16416 | 3997 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14287 | 15 | 16416 | 3997 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 8 | 14288 | 0 | 16416 | 3998 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 1 | 16416 | 3998 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 9 | 14288 | 2 | 16416 | 3998 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 3 | 16416 | 3998 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 10 | 14288 | 4 | 16416 | 3998 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 5 | 16416 | 3998 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 11 | 14288 | 6 | 16416 | 3998 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 7 | 16416 | 3998 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 12 | 14288 | 8 | 16416 | 3999 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 9 | 16416 | 3999 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 13 | 14288 | 10 | 16416 | 3999 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 11 | 16416 | 3999 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 14 | 14288 | 12 | 16416 | 3999 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 13 | 16416 | 3999 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1055 | 15 | 14288 | 14 | 16416 | 3999 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14288 | 15 | 16416 | 3999 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94060T1 | BIL ZVQ4004 Consigne T° Amb. Conf1 VCT4060 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 391 | 0 | 14289 | 0 | 16416 | 4000 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94060H1 | BIL ZVQ4004 Consigne HR Amb. Conf1 VCT4060 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 392 | 0 | 14290 | 0 | 16416 | 4002 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94060T3 | BIL ZVQ4004 Consigne T° PDR VTR4060 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 393 | 0 | 14291 | 0 | 16416 | 4004 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94060T2 | BIL ZVQ4004 Consigne T° Amb. Conf2 VCT4060 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 394 | 0 | 14292 | 0 | 16416 | 4006 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94060H2 | BIL ZVQ4004 Consigne HR Amb. Conf2 VCT4060 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 395 | 0 | 14293 | 0 | 16416 | 4008 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL ZVQ4004 T° Puls. VCT4060 | MA | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 396 | 0 | 14294 | 0 | 16416 | 4010 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico da VMC
VVU90001D4 | BIL ZVQ4004 Conf1 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 397 | 0 | 14295 | 0 | 16416 | 4012 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 1 | 16416 | 4012 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90001D9 | BIL ZVQ4004 Conf2 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 397 | 1 | 14295 | 2 | 16416 | 4012 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 3 | 16416 | 4012 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Conf3 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 2 | 14295 | 4 | 16416 | 4012 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 5 | 16416 | 4012 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 3 | 14295 | 6 | 16416 | 4012 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 7 | 16416 | 4012 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90003D4 | BIL ZVQ4004 Acquit | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 397 | 4 | 14295 | 8 | 16416 | 4013 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 9 | 16416 | 4013 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU94060D | BIL Marche VCT4060 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 397 | 5 | 14295 | 10 | 16416 | 4013 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 11 | 16416 | 4013 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Validation csg VCT4060 | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 6 | 14295 | 12 | 16416 | 4013 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 13 | 16416 | 4013 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 7 | 14295 | 14 | 16416 | 4013 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14295 | 15 | 16416 | 4013 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 8 | 14296 | 0 | 16416 | 4014 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 1 | 16416 | 4014 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 9 | 14296 | 2 | 16416 | 4014 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 3 | 16416 | 4014 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 10 | 14296 | 4 | 16416 | 4014 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 5 | 16416 | 4014 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 11 | 14296 | 6 | 16416 | 4014 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 7 | 16416 | 4014 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 12 | 14296 | 8 | 16416 | 4015 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 9 | 16416 | 4015 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 13 | 14296 | 10 | 16416 | 4015 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 11 | 16416 | 4015 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 14 | 14296 | 12 | 16416 | 4015 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 13 | 16416 | 4015 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 397 | 15 | 14296 | 14 | 16416 | 4015 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14296 | 15 | 16416 | 4015 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94060CM1 | BIL CMD - ZVQ4004 T° Amb. Conf1 VCT4060 | CT | N | RES | 4 | C |  |  | °C |  | 0 | 50 | [20 empty] | POL |  |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 391 | 0 | 14297 | 0 | 16416 | 4016 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94060CM1 | BIL CMD - ZVQ4004 HR Amb. Conf1 VCT4060 | CT | N | RES | 4 | C |  |  | % |  | 0 | 100 | [20 empty] | POL |  |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 392 | 0 | 14298 | 0 | 16416 | 4018 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94060CM3 | BIL CMD - ZVQ4004 T° PDR VTR4060 | CT | N | RES | 4 | C |  |  | °C |  | 16 | 24 | [20 empty] | POL |  |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 393 | 0 | 14299 | 0 | 16416 | 4020 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94060CM2 | BIL CMD - ZVQ4004 T° Amb. Conf2 VCT4060 | CT | N | RES | 4 | C |  |  | °C |  | 0 | 50 | [20 empty] | POL |  |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 394 | 0 | 14300 | 0 | 16416 | 4022 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94060CM2 | BIL CMD - ZVQ4004 HR Amb. Conf2 VCT4060 | CT | N | RES | 4 | C |  |  | % |  | 0 | 100 | [20 empty] | POL |  |  | HVAC905 | HVAC BIL | BIL | 13 |  |  | 395 | 0 | 14301 | 0 | 16416 | 4024 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - ZVQ4004 T° Puls. VCT4060 | CT | N | RES | 4 | C |  |  | °C |  | 10 | 30 | [25 empty] | BIL | 13 |  |  | 396 | 0 | 14302 | 0 | 16416 | 4026 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in acrico dal VMC
VVU90001CM4 | BIL CMD - ZVQ4004 Conf1 -U8,CONF1 (1) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 397 | 0 | 14303 | 0 | 16416 | 4028 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001CM9 | BIL CMD - ZVQ4004 Conf2 - U8,CONF2 (2) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 397 | 1 | 14303 | 1 | 16416 | 4028 | 1 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - ZVQ4003 Conf3 - U8,CONF3 (3) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 397 | 2 | 14303 | 2 | 16416 | 4028 | 2 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL CMD - Reserve | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 397 | 3 | 14303 | NA | NA | NA | NA | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90003CM4 | BIL CMD - Acquit - U8,ACQUITTEMENT (16) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 397 | 4 | 14303 | 3 | 16416 | 4028 | 3 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - Acquit - Reserved for PLC | [41 empty] | NA | 14303 | 4 | 16416 | 4028 | 4 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94060CM | BIL CMD - Marche VCT4060 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC05 | HVAC BIL | BIL | 13 |  |  | 397 | 5 | 14303 | 5 | 16416 | 4028 | 5 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94060CA | BIL CMD - Arret VCT4060 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC05 | HVAC BIL | BIL | 13 |  |  | 397 | 5 | 14303 | 6 | 16416 | 4028 | 6 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - Validation csg VCT4060 | CT | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 397 | 6 | 14303 | 7 | 16416 | 4028 | 7 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VZC9405D | BIL DF automate - ZVQ4005 | AL | N | RES | 4 | A |  | K | [10 empty] | A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 1061 | 0 | 14350 | 0 | 16416 | 4122 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 1 | 16416 | 4122 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 1 | 14350 | 2 | 16416 | 4122 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 3 | 16416 | 4122 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 2 | 14350 | 4 | 16416 | 4122 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 5 | 16416 | 4122 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 3 | 14350 | 6 | 16416 | 4122 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 7 | 16416 | 4122 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 4 | 14350 | 8 | 16416 | 4123 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 9 | 16416 | 4123 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 5 | 14350 | 10 | 16416 | 4123 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 11 | 16416 | 4123 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 6 | 14350 | 12 | 16416 | 4123 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 13 | 16416 | 4123 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 7 | 14350 | 14 | 16416 | 4123 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14350 | 15 | 16416 | 4123 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 8 | 14351 | 0 | 16416 | 4124 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 1 | 16416 | 4124 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 9 | 14351 | 2 | 16416 | 4124 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 3 | 16416 | 4124 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL DF forcage commutateurs | AL | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 10 | 14351 | 4 | 16416 | 4124 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL |  | Non preso in carico dal VMC
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 5 | 16416 | 4124 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VAE94005D1 | BIL DF Prés. CAT2 KUU4008 | AL | N | RES | 4 | C;A |  | K | [10 empty] | C;A | [13 empty] | POL | 2000 |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL | 13 |  |  | 1061 | 11 | 14351 | 6 | 16416 | 4124 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 7 | 16416 | 4124 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 12 | 14351 | 8 | 16416 | 4125 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 9 | 16416 | 4125 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 13 | 14351 | 10 | 16416 | 4125 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 11 | 16416 | 4125 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 14 | 14351 | 12 | 16416 | 4125 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 13 | 16416 | 4125 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1061 | 15 | 14351 | 14 | 16416 | 4125 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14351 | 15 | 16416 | 4125 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94091D1 | BIL DF KKM4091 VCT4090 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1062 | 0 | 14352 | 0 | 16416 | 4126 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 1 | 16416 | 4126 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94091DI1 | BIL DF Press. diff VPB4091 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1062 | 1 | 14352 | 2 | 16416 | 4126 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 3 | 16416 | 4126 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 2 | 14352 | 4 | 16416 | 4126 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 5 | 16416 | 4126 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VT94092D | BIL DF Sonde T° Repr. VTR4092 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1062 | 3 | 14352 | 6 | 16416 | 4126 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 7 | 16416 | 4126 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VH94092D | BIL DF Sonde HR Repr. VHR4092 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1062 | 4 | 14352 | 8 | 16416 | 4127 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 9 | 16416 | 4127 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 5 | 14352 | 10 | 16416 | 4127 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 11 | 16416 | 4127 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 6 | 14352 | 12 | 16416 | 4127 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 13 | 16416 | 4127 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 7 | 14352 | 14 | 16416 | 4127 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14352 | 15 | 16416 | 4127 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 8 | 14353 | 0 | 16416 | 4128 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 1 | 16416 | 4128 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 9 | 14353 | 2 | 16416 | 4128 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 3 | 16416 | 4128 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 10 | 14353 | 4 | 16416 | 4128 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 5 | 16416 | 4128 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 11 | 14353 | 6 | 16416 | 4128 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 7 | 16416 | 4128 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VT94084D | BIL DF Sonde T° Repr. VTR4084 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 1062 | 12 | 14353 | 8 | 16416 | 4129 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 9 | 16416 | 4129 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VH94084D | BIL DF Sonde HR Repr. VHR4084 | AL | N | RES | 4 | C | [12 empty] | C | [13 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 1062 | 13 | 14353 | 10 | 16416 | 4129 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 11 | 16416 | 4129 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VFN94091D2 | BIL DF KQF4091 VCT4090 | AL | N | RES | 4 | C |  | K | [10 empty] | C | [13 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1062 | 14 | 14353 | 12 | 16416 | 4129 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 13 | 16416 | 4129 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1062 | 15 | 14353 | 14 | 16416 | 4129 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14353 | 15 | 16416 | 4129 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94092T | BIL VTR4092 Sonde T° repris VCT4090 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1063 | 0 | 14354 | 0 | 16416 | 4130 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94084T | BIL VTR4084 Sonde T° repris VCT4080 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 1064 | 0 | 14355 | 0 | 16416 | 4132 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94092H | BIL VHR4092 Sonde HR% repris VCT4090 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1065 | 0 | 14356 | 0 | 16416 | 4134 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94084H | BIL VHR4084 Sonde HR% repris VCT4080 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC909 | HVAC BIL | BIL | 13 |  |  | 1066 | 0 | 14357 | 0 | 16416 | 4136 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL KKM4091 re KM Vent. VCT4090 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1067 | 0 | 14358 | 0 | 16416 | 4138 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL KQF4091 Protection Vent. VCT4090 | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1068 | 0 | 14359 | 0 | 16416 | 4140 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VCT94091M1 | BIL VPB4091 Pressostat diff. VCT4090 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1069 | 0 | 14360 | 0 | 16416 | 4142 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Il VMC tratta la misura come booleana prendendo il primo bit della word
| BIL Mot des entrées digitale | MA | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1070 | 0 | 14361 | 0 | 16416 | 4144 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
CER94091T1 | BIL CWC4091 vanne EC(% ouv) VCT4090 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1071 | 0 | 14362 | 0 | 16416 | 4146 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
GER94091T1 | BIL GWC4091 vanne EG(% ouv) VCT4090 | MA | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 1072 | 0 | 14363 | 0 | 16416 | 4148 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1073 | 0 | 14364 | 0 | 16416 | 4150 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 1074 | 0 | 14365 | 0 | 16416 | 4152 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL VFN4091 Vent. puls VCT4090 | MA | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 1075 | 0 | 14366 | 0 | 16416 | 4154 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VTR94090 | BIL ZVQ4005 Consigne T° Amb. VTR4090 | MA | N | RES | 4 | C |  |  | °C | [23 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 421 | 0 | 14367 | 0 | 16416 | 4156 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94090 | BIL ZVQ4005 Consigne HR Amb. VCT4090 | MA | N | RES | 4 | C |  |  | % | [23 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 422 | 0 | 14368 | 0 | 16416 | 4158 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001D5 | BIL Conf1 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 423 | 0 | 14369 | 0 | 16416 | 4160 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 1 | 16416 | 4160 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90001D10 | BIL Conf2 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 423 | 1 | 14369 | 2 | 16416 | 4160 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 3 | 16416 | 4160 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Conf3 | CR | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 2 | 14369 | 4 | 16416 | 4160 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 5 | 16416 | 4160 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Reserve |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 3 | 14369 | 6 | 16416 | 4160 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 7 | 16416 | 4160 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU90003D5 | BIL Acquit | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC901 | HVAC BIL | BIL | 13 |  |  | 423 | 4 | 14369 | 8 | 16416 | 4161 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 9 | 16416 | 4161 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VVU94090D | BIL Marche VCT4090 | CR | N | RES | 4 | C | [26 empty] | POL | 2000 |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 423 | 5 | 14369 | 10 | 16416 | 4161 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 11 | 16416 | 4161 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| BIL Validation csg VCT4090 | AL | N | RES | 4 | C | [31 empty] | BIL | 13 |  |  | 423 | 6 | 14369 | 12 | 16416 | 4161 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 13 | 16416 | 4161 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 7 | 14369 | 14 | 16416 | 4161 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14369 | 15 | 16416 | 4161 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 8 | 14370 | 0 | 16416 | 4162 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 1 | 16416 | 4162 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 9 | 14370 | 2 | 16416 | 4162 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 3 | 16416 | 4162 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 10 | 14370 | 4 | 16416 | 4162 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 5 | 16416 | 4162 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 11 | 14370 | 6 | 16416 | 4162 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 7 | 16416 | 4162 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 12 | 14370 | 8 | 16416 | 4163 | 0 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 9 | 16416 | 4163 | 1 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 13 | 14370 | 10 | 16416 | 4163 | 2 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 11 | 16416 | 4163 | 3 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 14 | 14370 | 12 | 16416 | 4163 | 4 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 13 | 16416 | 4163 | 5 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| Not use |  | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 15 | 14370 | 14 | 16416 | 4163 | 6 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
| VALIDITY | [36 empty] | BIL | 13 |  |  |  |  | 14370 | 15 | 16416 | 4163 | 7 | EL6021 - ZVQ4003/4004/4005 |  | BITVAL
VTR94090CM1 | BIL ZVQ4005 Consigne T° Amb. VTR4090 | CT | N | RES | 4 | C |  |  | °C |  | 0 | 50 | [20 empty] | POL |  |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 421 | 0 | 14371 | 0 | 16416 | 4164 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VHR94090CM1 | BIL ZVQ4005 Consigne HR Amb. VCT4090 | CT | N | RES | 4 | C |  |  | % |  | 0 | 100 | [20 empty] | POL |  |  | HVAC910 | HVAC BIL | BIL | 13 |  |  | 422 | 0 | 14372 | 0 | 16416 | 4166 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001CM5 | BIL CMD - ZVQ4005 Conf1 - U8,CONF1 (1) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 423 | 0 | 14373 | 0 | 16416 | 4168 | 0 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90001CM10 | BIL CMD - ZVQ4005 Conf2 - U8,CONF2 (2) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 423 | 1 | 14373 | 1 | 16416 | 4168 | 1 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - ZVQ4003 Conf3 - U8,CONF3 (3) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 423 | 2 | 14373 | 2 | 16416 | 4168 | 2 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
| BIL CMD - Reserve | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 423 | 3 | 14373 | NA | NA | NA | NA | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU90003CM5 | BIL CMD - ZVQ4005 Acquit - U8,ACQUITTEMENT (8) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC01 | HVAC BIL | BIL | 13 |  |  | 423 | 4 | 14373 | 3 | 16416 | 4168 | 3 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - Acquit - Reserved for PLC | [41 empty] | NA | 14373 | 4 | 16416 | 4168 | 4 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94090CM | BIL CMD - Marche VCT4090 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC10 | HVAC BIL | BIL | 13 |  |  | 423 | 5 | 14373 | 5 | 16416 | 4168 | 5 | EL6021 - ZVQ4003/4004/4005 |  | UINT
VVU94090CA | BIL CMD - Arret VCT4090 - U8,MARCHE (32) / U8,ARRET(64) | CT | N | RES | 4 | C | [29 empty] | BIL HVAC10 | HVAC BIL | BIL | 13 |  |  | 423 | 5 | 14373 | 6 | 16416 | 4168 | 6 | EL6021 - ZVQ4003/4004/4005 |  | UINT
| BIL CMD - Validation csg VCT4090 | CT | N | RES | 4 | [32 empty] | BIL | 13 |  |  | 423 | 6 | 14373 | 7 | 16416 | 4168 | 7 | EL6021 - ZVQ4003/4004/4005 |  | UINT |  | Non preso in carico dal VMC
VVU90001CMGC1 | BIL CMDE BIL CONFIGURATION - MODE Conf1 | CT |  |  |  | C | [12 empty] | C |  |  |  | VVU90001CM1; VVU90001CM2; VVU90001CM3; VVU90001CM4; VVU90001CM5 | [9 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 | [11 empty] | U8
VVU90001CMGC2 | BIL CMDE BIL CONFIGURATION - MODE Conf2 | CT |  |  |  | C | [12 empty] | C |  |  |  | VVU90001CM7; VVU90001CM8; VVU90001CM9; VVU90001CM6; VVU90001CM10 | [9 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 | [11 empty] | U8
VVU90003CMGC | BIL CMDE ACQUITTEMENT DEFAULT (ACTIVER RESET) | CT |  |  |  | C | [12 empty] | C |  |  |  | VVU90003CM1; VVU90003CM2; VVU90003CM3; VVU90003CM4; VVU90003CM5 | [9 empty] | POL |  |  | HVAC901 | HVAC BIL | BIL | 13 | [11 empty] | U8
VVU94030COGC | BIL CMDE Priority selection cabinet Hiross VCT4030 | CT |  |  |  | C | [12 empty] | C |  |  |  | VVU94030CO; VVU94040CF | [9 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 | [11 empty] | U8
VVU94040COGC | BIL CMDE Priority selection cabinet Hiross VCT4040 | CT |  |  |  | C | [12 empty] | C |  |  |  | VVU94030CF; VVU94040CO | [9 empty] | POL |  |  | HVAC907 | HVAC BIL | BIL | 13 | [11 empty] | U8
HVAC900DMA | BIL SYNTHESE DEFAUT HVAC900 ARCHITECTURE DU SYSTEME | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC9401D; VZC9401DC1; VZC9401DC2; VAE94001D1; VAE94001D2; VZC9402D; VZC9402DC1; VZC9402DC2; VAE94002D1; VAE94002D2; VZC9403D; VAE94003D1; VZC9404D; VAE94004D1; VZC9405D; VAE94005D1; | Y |  |  |  | HVAC900 ARCHITECTURE DU SYSTEME | HVAC BIL | BIL
HVAC902DMA | BIL SYNTHESE DEFAUT HVAC902 VCT4010 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VRP94012DO1; VRP94012DF1; VFN94010DR2; VFN94010DR1; VAR94012DT; VFN94011D1; VFN94011D2; VCT94011DI1; VCT94011DR | Y |  |  |  | HVAC902 | HVAC BIL | BIL
HVAC903DMA | BIL SYNTHESE DEFAUT HVAC903 VCT 4020 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VT94022D; VH94022D; VFN94021D1; VFN94021D2; VFN94021DI1;VT94024D; VH94024D | Y |  |  |  | HVAC903 | HVAC BIL | BIL
HVAC904DMA | BIL SYNTHESE DEFAUT HVAC904 VCT 4050 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VRP94052DO; VRP94052DF; VFN94050DR2; VFN94050DR1; VFN94051DR; VFN94051D2; VFN94051D1; VFN94051DI | Y |  |  |  | HVAC904 | HVAC BIL | BIL
HVAC905DMA | BIL SYNTHESE DEFAUT HVAC905 VCT 4060 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VFN94061D2; VFN94061D1; VFN94061DI; VCT94061DR; VFN94060DR2; VFN94060DR1;VRP94062DO; VRP94062DF | Y |  |  |  | HVAC905 | HVAC BIL | BIL
HVAC906DMA | BIL SYNTHESE DEFAUT HVAC906 HALL INTEGRATION | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VT94052D;VH94052D;VCT94053DR;VCT94054DR;VCT94055DR;VCT94056DR;VCT94057DR;VCT94058DR;VCT94059DR;VCT94075DR;VT94062D;VH94062D;VCT94063DR;VCT94064DR;VCT94065DR;VCT94066DR; VCT94067DR;VCT94068DR;VCT94069DR;VCT94076DR; | Y |  |  |  | HVAC906 | HVAC BIL | BIL
HVAC907DMA | BIL SYNTHESE DEFAUT HVAC907 LOCAL 103 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VCN94031D; VCN94100D; VT94031D; VH94031D; VCN94041D | Y |  |  |  | HVAC907 | HVAC BIL | BIL
HVAC908DMA | BIL SYNTHESE DEFAUT HVAC908 VCT4070 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VFN94071D2; VCT94071DI1; VFN94070DR1; VCT94071DT; VRP94072DO1; VRP94072DF1; VAR94072DT; VFN94071D1; VFN94070DR2; | Y |  |  |  | HVAC908 | HVAC BIL | BIL
HVAC909DMA | BIL SYNTHESE DEFAUT HVAC909 VCT4080 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VT94082D; VH94082D; VFN94081D1; VFN94081D2; VFN94081DI1; VT94084D; VH94084D; | Y |  |  |  | HVAC909 | HVAC BIL | BIL
HVAC910DMA | BIL SYNTHESE DEFAUT HVAC910 VCT4090 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VFN94091D1; VFN94091DI1; VT94092D; VH94092D; VFN94091D2; VT94094D; VH94094D; | Y |  |  |  | HVAC910 | HVAC BIL | BIL
VZC9001DMA | BIL HVAC SYNTHESE DEFAUT | AL | N | CAL | 0 | Z | [24 empty] | HVAC900DMA; HVAC902DMA; HVAC903DMA; HVAC904DMA; HVAC905DMA; HVAC906DMA; HVAC907DMA; HVAC908DMA; HVAC909DMA; HVAC910DMA; | Y |  |  |  | HVAC BIL (node) | HVAC BIL | BIL
VZC6900DMA | HVAC (C) SYNTHESE DEFAUT | AL | N | CAL | 0 | Z | [24 empty] | VZC9001DMA; VZC6001DMA | Y |  |  |  | HVAC (C) | HVAC (C) (node) | BIL
JSY9001 | BIL ALARME INCORRECT DATA CAR | AL | N | TCP | 4 | F | [12 empty] | F | [13 empty] | MTCP |  |  | MG93 BIL CAR | Moyer Generaux interfaces externes (MG) | BIL | [12 empty] | BITVAL
SDC9001 | BIL SYNTHESE DEFAUT COMMUNICATION FAILURE CAR | CR | N | TCP | 4 | F | [12 empty] | F | [13 empty] | MTCP |  |  | MG93 BIL CAR | Moyer Generaux interfaces externes (MG) | BIL | [12 empty] | BITVAL
MG93DMA | BIL SYNTHESE ALARME MG93 BIL CAR | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | JSY9001 | Y |  |  |  | MG93 BIL CAR | Moyer Generaux interfaces externes (MG) | BIL
MG9700DMA | SYNTHESE DEFAUT MOYENS GENERAUX INTERFACES EXTERNES | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | MG72DMA; MG93DMA | Y |  |  |  | Moyer Generaux interfaces externes (Node) | Moyer Generaux interfaces externes (MG) | BIL
SZI94001D | BIL Niveau +8.700 Defaut SDJ4001 001 Dock integration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94001W | BIL Niveau +8.700 Alarme Feu SDJ4001 001 Dock integration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94004D | BIL Niveau +8.700 Defaut SDJ4004 005 Local transfo. | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94004W | BIL Niveau +8.700 Alarme Feu SDJ4004 005 Local transfo. | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94003D | BIL Niveau +8.700 Defaut SDJ4003 002 Climatisation 1 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94003W | BIL Niveau +8.700 Alarme Feu SDJ4003 002 Climatisation 1 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94037D | BIL Niveau +8.700 Defaut SDJ4037 002 Climatisation 1 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94037W | BIL Niveau +8.700 Alarme Feu SDJ4037 002 Climatisation 1 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94002D | BIL Niveau +8.700 Defaut SDJ4002 002 Climatisation 1 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94002W | BIL Niveau +8.700 Alarme Feu SDJ4002 002 Climatisation 1 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94032D | BIL Niveau +12.700 Defaut SDJ4032 102 Local Energie | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94032W | BIL Niveau +12.700 Alarme Feu SDJ4032 102 Local Energie | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94013D | BIL Niveau +12.700 Defaut SDJ4013 102 Local Energie | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94013W | BIL Niveau +12.700 Alarme Feu SDJ4013 102 Local Energie | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94014D | BIL Niveau +12.700 Defaut SDJ4013 102b Local Batteries | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94014W | BIL Niveau +12.700 Alarme Feu SDJ4013 102b Local Batteries | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94031D | BIL Niveau +12.700 Defaut SDJ4031 104 Local sting | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94031W | BIL Niveau +12.700 Alarme Feu SDJ4031 104 Local sting | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94015D | BIL Niveau +12.700 Defaut SDJ4015 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94015W | BIL Niveau +12.700 Alarme Feu SDJ4015 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94016D | BIL Niveau +12.700 Defaut SDJ4016 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94016W | BIL Niveau +12.700 Alarme Feu SDJ4016 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94017D | BIL Niveau +12.700 Defaut SDJ4017 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94017W | BIL Niveau +12.700 Alarme Feu SDJ4017 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94018D | BIL Niveau +12.700 Defaut SDJ4018 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94018W | BIL Niveau +12.700 Alarme Feu SDJ4018 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94019D | BIL Niveau +12.700 Defaut SDJ4019 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94019W | BIL Niveau +12.700 Alarme Feu SDJ4019 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94020D | BIL Niveau +12.700 Defaut SDJ4020 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94020W | BIL Niveau +12.700 Alarme Feu SDJ4020 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94021D | BIL Niveau +12.700 Defaut SDJ4021 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94021W | BIL Niveau +12.700 Alarme Feu SDJ4021 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94022D | BIL Niveau +12.700 Defaut SDJ4022 103 Local RMO | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94022W | BIL Niveau +12.700 Alarme Feu SDJ4022 103 Local RMO | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI90 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94069D | BIL Niveau +15.700 Defaut SDJ4069 Local 202A | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94069W | BIL Niveau +15.700 Alarme Feu SDJ4069 Local 202A | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94043D | BIL Niveau +15.700 Defaut SDJ4043 Local 202 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94043W | BIL Niveau +15.700 Alarme Feu SDJ4043 Local 202 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94044D | BIL Niveau +15.700 Defaut SDJ4044 Local 202 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94044W | BIL Niveau +15.700 Alarme Feu SDJ4044 Local 202 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94045D | BIL Niveau +20.000 Defaut SDJ4045 Local 302 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94045W | BIL Niveau +20.000 Alarme Feu SDJ4045 Local 302 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94046D | BIL Niveau +20.000 Defaut SDJ4046 Local 302 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94046W | BIL Niveau +20.000 Alarme Feu SDJ4046 Local 302 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94047D | BIL Niveau +42.900 Defaut SDJ4047 Local 502 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94047W | BIL Niveau +42.900 Alarme Feu SDJ4047 Local 502 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94048D | BIL Niveau +42.900 Defaut SDJ4048 Local 502 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94048W | BIL Niveau +42.900 Alarme Feu SDJ4048 Local 502 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94049D | BIL Niveau +46.300 Defaut SDJ4049 Local 602 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94049W | BIL Niveau +46.300 Alarme Feu SDJ4049 Local 602 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94050D | BIL Niveau +46.300 Defaut SDJ4050 Local 602 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94050W | BIL Niveau +46.300 Alarme Feu SDJ4050 Local 602 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94051D | BIL Niveau +50.200 Defaut SDJ4051 Local 702 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94051W | BIL Niveau +50.200 Alarme Feu SDJ4051 Local 702 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94052D | BIL Niveau +50.200 Defaut SDJ4050 Local 702 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94052W | BIL Niveau +50.200 Alarme Feu SDJ4050 Local 702 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94041D | BIL Niveau +51.950 Defaut SDJ4041 Local 702 Mach. Ascenseur | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94041W | BIL Niveau +51.950 Alarme Feu SDJ4041 Local 702 Mach. Ascenseur | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94039D | BIL Niveau +42.900 Defaut SDJ4039 Dock integration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94039W | BIL Niveau +42.900 Alarme Feu SDJ4039 Dock integration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94042D | BIL Niveau +42.900 Defaut SDJ4042 Dock integration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94042W | BIL Niveau +42.900 Alarme Feu SDJ4042 Dock integration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94034D | BIL Niveau +15.200 Defaut SDJ4034 Dock integration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94034W | BIL Niveau +15.200 Alarme Feu SDJ4034 Dock integration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94035D | BIL Niveau +15.200 Defaut SDJ4035 Dock integration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94035W | BIL Niveau +15.200 Alarme Feu SDJ4035 Dock integration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI91 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94012D | BIL Niveau +8.700 Defaut SDJ4012 008 Calibration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94012W | BIL Niveau +8.700 Alarme Feu SDJ4012 008 Calibration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94010D | BIL Niveau +8.700 Defaut SDJ4010 008 Calibration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94010W | BIL Niveau +8.700 Alarme Feu SDJ4010 008 Calibration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94011D | BIL Niveau +8.700 Defaut SDJ4011 008 Calibration | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94011W | BIL Niveau +8.700 Alarme Feu SDJ4011 008 Calibration | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94006D | BIL Niveau +8.700 Defaut SDJ4006 010 Climatisation 2 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94006W | BIL Niveau +8.700 Alarme Feu SDJ4006 010 Climatisation 2 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94005D | BIL Niveau +8.700 Defaut SDJ4005 010 Climatisation 2 | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94005W | BIL Niveau +8.700 Alarme Feu SDJ4005 010 Climatisation 2 | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94008D | BIL Niveau +8.700 Defaut SDJ4008 009 Labo Interv. | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94008W | BIL Niveau +8.700 Alarme Feu SDJ4008 009 Labo Interv. | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94009D | BIL Niveau +8.700 Defaut SDJ4009 009 Labo Interv. | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94009W | BIL Niveau +8.700 Alarme Feu SDJ4009 009 Labo Interv. | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94007D | BIL Niveau +8.700 Defaut SDJ4007 009 Labo Interv. | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94007W | BIL Niveau +8.700 Alarme Feu SDJ4007 009 Labo Interv. | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94061D | BIL Niveau +27.920 - +36.820 Defaut SDJ4061 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94061W | BIL Niveau +27.920 - +36.820 Alarme Feu SDJ4061 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94062D | BIL Niveau +27.920 - +36.820 Defaut SDJ4062 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94062W | BIL Niveau +27.920 - +36.820 Alarme Feu SDJ4062 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94060D | BIL Niveau +27.920 - +33.320 Defaut SDJ4060 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94060W | BIL Niveau +27.920 - +33.320 Alarme Feu SDJ4060 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94059D | BIL Niveau +27.920 - +33.320 Defaut SDJ4059 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94059W | BIL Niveau +27.920 - +33.320 Alarme Feu SDJ4059 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94055D | BIL Niveau +25.120 - +27.920 Defaut SDJ4055 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94055W | BIL Niveau +25.120 - +27.920 Alarme Feu SDJ4055 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94056D | BIL Niveau +25.120 - +27.920 Defaut SDJ4056 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94056W | BIL Niveau +25.120 - +27.920 Alarme Feu SDJ4056 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94057D | BIL Niveau +25.120 - +27.920 Defaut SDJ4057 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94057W | BIL Niveau +25.120 - +27.920 Alarme Feu SDJ4057 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94057D | BIL Niveau +25.120 - +27.920 Defaut SDJ4058 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI94057W | BIL Niveau +25.120 - +27.920 Alarme Feu SDJ4058 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI92 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9405D | BIL Niveau +12.700 Defaut Declancheurs manuels SBG4005 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9405W | BIL Niveau +12.700 Alarme Feu Declancheurs manuels SBG4005 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9406D | BIL Niveau +15.700 Defaut Declancheurs manuels SBG4006 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9406W | BIL Niveau +15.700 Alarme Feu Declancheurs manuels SBG4006 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9407D | BIL Niveau +20.000 Defaut Declancheurs manuels SBG4007 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9407W | BIL Niveau +20.000 Alarme Feu Declancheurs manuels SBG4007 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9408D | BIL Niveau +37.200 Defaut Declancheurs manuels SBG4008 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9408W | BIL Niveau +37.200 Alarme Feu Declancheurs manuels SBG4008 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9404D | BIL Niveau +8.700 Defaut Declancheurs manuels SBG4004 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9404W | BIL Niveau +8.700 Alarme Feu Declancheurs manuels SBG4004 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9409D | BIL Niveau +42.300 Defaut Declancheurs manuels SBG4009 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9409W | BIL Niveau +42.300 Alarme Feu Declancheurs manuels SBG4009 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9411D | BIL Niveau +46.300 Defaut Declancheurs manuels SBG4011 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9411W | BIL Niveau +46.300 Alarme Feu Declancheurs manuels SBG4011 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9461D | BIL Niveau +50.200 Defaut Declancheurs manuels SBG4601 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9461W | BIL Niveau +50.200 Alarme Feu Declancheurs manuels SBG4601 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9413D | BIL Niveau +20.000 Defaut Declancheurs manuels SBG4013 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9413W | BIL Niveau +20.000 Alarme Feu Declancheurs manuels SBG4013 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9410D | BIL Niveau +42.200 Defaut Declancheurs manuels SBG4010 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9410W | BIL Niveau +42.200 Alarme Feu Declancheurs manuels SBG4010 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9412D | BIL Niveau +46.300 Defaut Declancheurs manuels SBG4012 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9412W | BIL Niveau +46.300 Alarme Feu Declancheurs manuels SBG4012 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9403D | BIL Niveau +8.700 Defaut Declancheurs manuels SBG4003 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9403W | BIL Niveau +8.700 Alarme Feu Declancheurs manuels SBG4003 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9402D | BIL Niveau +8.700 Defaut Declancheurs manuels SBG4002 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9402W | BIL Niveau +8.700 Alarme Feu Declancheurs manuels SBG4002 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9401D | BIL Niveau +8.700 Defaut Declancheurs manuels SBG4001 BIL Building | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9401W | BIL Niveau +8.700 Alarme Feu Declancheurs manuels SBG4001 BIL Building | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9417D | BIL Niveau +36.820 Defaut Declancheurs manuels SBG4017 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9417W | BIL Niveau +36.820 Alarme Feu Declancheurs manuels SBG4017 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9418D | BIL Niveau +33.320 Defaut Declancheurs manuels SBG4018 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9418W | BIL Niveau +33.320 Alarme Feu Declancheurs manuels SBG4018 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9419D | BIL Niveau +27.920 Defaut Declancheurs manuels SBG4019 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9419W | BIL Niveau +27.920 Alarme Feu Declancheurs manuels SBG4019 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9420D | BIL Niveau +25.120 Defaut Declancheurs manuels SBG4020 BIL Cage | CR | N | TCP | 4 | S | [26 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
SZI9420W | BIL Niveau +25.120 Alarme Feu Declancheurs manuels SBG4020 BIL Cage | AL | N | TCP | 4 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI93 (DETIN BIL Group) | Detection Interfaces Externes (DI) | BIL | 13 | [11 empty] | BITVAL
EFR9001 | BIL UPS CATIIIA - Input frequency | MA | N | RES | 4 | E |  |  | Hz | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30004 | 0 | 14500 | 0 | 16416 | 4422 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001I1 | BIL UPS CATIIIA - Input current phase A | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30005 | 0 | 14501 | 0 | 16416 | 4424 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001I2 | BIL UPS CATIIIA - Input current phase B | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30006 | 0 | 14502 | 0 | 16416 | 4426 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001I3 | BIL UPS CATIIIA - Input current phase C | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30007 | 0 | 14503 | 0 | 16416 | 4428 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EFR9002 | BIL UPS CATIIIA - Output frequency | MA | N | RES | 4 | E |  |  | Hz | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30014 | 0 | 14504 | 0 | 16416 | 4430 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9002I1 | BIL UPS CATIIIA - Output current phase A | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30015 | 0 | 14505 | 0 | 16416 | 4432 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9002I2 | BIL UPS CATIIIA - Output current phase B | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30016 | 0 | 14506 | 0 | 16416 | 4434 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9002I3 | BIL UPS CATIIIA - Output current phase C | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30017 | 0 | 14507 | 0 | 16416 | 4436 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9002P1 | BIL UPS CATIIIA - Output kW phase A | MA | N | RES | 4 | E |  |  | kW | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30018 | 0 | 14508 | 0 | 16416 | 4438 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9002P2 | BIL UPS CATIIIA - Output kW phase B | MA | N | RES | 4 | E |  |  | kW | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30019 | 0 | 14509 | 0 | 16416 | 4440 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9002P3 | BIL UPS CATIIIA - Output kW phase C | MA | N | RES | 4 | E |  |  | kW | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30020 | 0 | 14510 | 0 | 16416 | 4442 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9002L1 | BIL UPS CATIIIA - Load percent phase A | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30021 | 0 | 14511 | 0 | 16416 | 4444 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9002L2 | BIL UPS CATIIIA - Load percent phase B | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30022 | 0 | 14512 | 0 | 16416 | 4446 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9002L3 | BIL UPS CATIIIA - Load percent phase C | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30023 | 0 | 14513 | 0 | 16416 | 4448 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9002CF1 | BIL UPS CATIIIA - Output A phase load peak ratio | MA | N | RES | 4 | E |  |  |  | 0.01 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30024 | 0 | 14514 | 0 | 16416 | 4450 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9002CF2 | BIL UPS CATIIIA - Output B phase load peak ratio | MA | N | RES | 4 | E |  |  |  | 0.01 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30025 | 0 | 14515 | 0 | 16416 | 4452 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9002CF3 | BIL UPS CATIIIA - Output C phase load peak ratio | MA | N | RES | 4 | E |  |  |  | 0.01 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30026 | 0 | 14516 | 0 | 16416 | 4454 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR9001UBP | BIL UPS CATIIIA - Battery voltage positive | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30031 | 0 | 14517 | 0 | 16416 | 4456 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR9001UBM | BIL UPS CATIIIA - Battery voltage negative | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30032 | 0 | 14518 | 0 | 16416 | 4458 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001DP | BIL UPS CATIIIA - Positive battery discharge current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30033 | 0 | 14519 | 0 | 16416 | 4460 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001DM | BIL UPS CATIIIA - Negative battery discharge current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30034 | 0 | 14520 | 0 | 16416 | 4462 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001CP | BIL UPS CATIIIA - Positive battery charging current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30035 | 0 | 14521 | 0 | 16416 | 4464 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9001CM | BIL UPS CATIIIA - Negative battery charging current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30036 | 0 | 14522 | 0 | 16416 | 4466 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9001 | BIL UPS CATIIIA - Battery capacity | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30037 | 0 | 14523 | 0 | 16416 | 4468 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EDR9001 | BIL UPS CATIIIA - Battery backup time | MA | N | RES | 4 | E |  |  | Min | 1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30038 | 0 | 14524 | 0 | 16416 | 4470 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ETR9001 | BIL UPS CATIIIA - Battery temperature | MA | N | RES | 4 | E |  |  | °C | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30039 | 0 | 14525 | 0 | 16416 | 4472 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ETR9002 | BIL UPS CATIIIA - Ambient temperature | MA | N | RES | 4 | E |  |  | °C | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30040 | 0 | 14526 | 0 | 16416 | 4474 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9002S1 | BIL UPS CATIIIA - Output kVA phase A | MA | N | RES | 4 | E |  |  | kVA | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30047 | 0 | 14527 | 0 | 16416 | 4476 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9002S2 | BIL UPS CATIIIA - Output kVA phase B | MA | N | RES | 4 | E |  |  | kVA | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30048 | 0 | 14528 | 0 | 16416 | 4478 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9002S3 | BIL UPS CATIIIA - Output kVA phase C | MA | N | RES | 4 | E |  |  | kVA | 0.1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30049 | 0 | 14529 | 0 | 16416 | 4480 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900112 | BIL UPS CATIIIA - Input AB line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91_1 |  | BIL | 16 |  |  | 30050 | 0 | 14530 | 0 | 16416 | 4482 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900123 | BIL UPS CATIIIA - Input BC line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91_1 |  | BIL | 16 |  |  | 30051 | 0 | 14531 | 0 | 16416 | 4484 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900131 | BIL UPS CATIIIA - Input CA line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91_1 |  | BIL | 16 |  |  | 30052 | 0 | 14532 | 0 | 16416 | 4486 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900212 | BIL UPS CATIIIA - Output AB line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91_1 |  | BIL | 16 |  |  | 30056 | 0 | 14533 | 0 | 16416 | 4488 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900223 | BIL UPS CATIIIA - Output BC line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91_1 |  | BIL | 16 |  |  | 30057 | 0 | 14534 | 0 | 16416 | 4490 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900231 | BIL UPS CATIIIA - Output CA line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E91_1 |  | BIL | 16 |  |  | 30058 | 0 | 14535 | 0 | 16416 | 4492 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUL9001D | BIL UPS CATIIIA - BIL UPS system status | MA | N | RES | 4 | E |  |  |  | 1 | [23 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 30071 | 0 | 14536 | 0 | 16416 | 4494 | 0 | EL6021 - UPS/TGBT CATIII |  | U16 | 0x0000 - Initialize 0x0001 - Standby operation 0x0002 - Output is off 0x0003 - Bypass operation 0x0004 - Normal operation 0x0005 - Battery operation 0x0006 - Battery self-test 0x0008 - ECO Mode 0x0009 - EPO activated 0x000A - Maintenance bypass op. 0x000D - Hybrid operation 0x000E - Self-aging mode 0x0014 - REC is OFF 0x0015 - Input 0x0016 - On battery 0x001E - Inverter standby 0x001F - Inverter Output 0x0020 - Inverter self-aging 0x0028 - ECU is Off 0x0029 - ECU Standby 0x002A - ECU active
EUL9002D1 | BIL Output dry contact - OFF | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 0 | 14537 | 0 | 16416 | 4496 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 1 | 16416 | 4496 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D2 | BIL Output dry contact - Common Alarm | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 1 | 14537 | 2 | 16416 | 4496 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 3 | 16416 | 4496 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D3 | BIL Output dry contact - Normal Operation | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 2 | 14537 | 4 | 16416 | 4496 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 5 | 16416 | 4496 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D4 | BIL Output dry contact - Battery Operation | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 3 | 14537 | 6 | 16416 | 4496 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 7 | 16416 | 4496 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D5 | BIL Output dry contact - Static Bypass | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 4 | 14537 | 8 | 16416 | 4497 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 9 | 16416 | 4497 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D6 | BIL Output dry contact - Output Overloaded | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 5 | 14537 | 10 | 16416 | 4497 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 11 | 16416 | 4497 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D7 | BIL Output dry contact - Fan Inoperable | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 6 | 14537 | 12 | 16416 | 4497 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 13 | 16416 | 4497 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D8 | BIL Output dry contact - Battery Fault | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 7 | 14537 | 14 | 16416 | 4497 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14537 | 15 | 16416 | 4497 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D9 | BIL Output dry contact - Battery Disconnected | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 8 | 14538 | 0 | 16416 | 4498 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 1 | 16416 | 4498 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D10 | BIL Output dry contact - Battery Voltage Low | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 9 | 14538 | 2 | 16416 | 4498 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 3 | 16416 | 4498 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D11 | BIL Output dry contact - Input Out Of Tolerance | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 10 | 14538 | 4 | 16416 | 4498 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 5 | 16416 | 4498 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D12 | BIL Output dry contact - Bypass Out Of Tolerance | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 11 | 14538 | 6 | 16416 | 4498 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 7 | 16416 | 4498 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D13 | BIL Output dry contact - EPO Activated | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 12 | 14538 | 8 | 16416 | 4499 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 9 | 16416 | 4499 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9002D14 | BIL Output dry contact - Maintenance Mode | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40201 | 13 | 14538 | 10 | 16416 | 4499 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 11 | 16416 | 4499 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Output dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40201 | 14 | 14538 | 12 | 16416 | 4499 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 13 | 16416 | 4499 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Output dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40201 | 15 | 14538 | 14 | 16416 | 4499 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14538 | 15 | 16416 | 4499 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D1 | BIL Input dry contact - OFF | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 0 | 14539 | 0 | 16416 | 4500 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 1 | 16416 | 4500 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D2 | BIL Input dry contact - UPS ON | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 1 | 14539 | 2 | 16416 | 4500 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 3 | 16416 | 4500 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D3 | BIL Input dry contact - UPS OFF | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 2 | 14539 | 4 | 16416 | 4500 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 5 | 16416 | 4500 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D4 | BIL Input dry contact - Battery Fault | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 3 | 14539 | 6 | 16416 | 4500 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 7 | 16416 | 4500 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D5 | BIL Input dry contact - Genset enable | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 4 | 14539 | 8 | 16416 | 4501 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 9 | 16416 | 4501 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D6 | BIL Input dry contact - Custom Alarm 3 | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 5 | 14539 | 10 | 16416 | 4501 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 11 | 16416 | 4501 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D7 | BIL Input dry contact - Custom Alarm 4 | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 6 | 14539 | 12 | 16416 | 4501 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 13 | 16416 | 4501 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D8 | BIL Input dry contact - Disable ECO | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 7 | 14539 | 14 | 16416 | 4501 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14539 | 15 | 16416 | 4501 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9001D9 | BIL Input dry contact - Force INV off | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E91 |  | BIL | 16 |  |  | 40221 | 8 | 14540 | 0 | 16416 | 4502 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 1 | 16416 | 4502 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 9 | 14540 | 2 | 16416 | 4502 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 3 | 16416 | 4502 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 10 | 14540 | 4 | 16416 | 4502 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 5 | 16416 | 4502 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 11 | 14540 | 6 | 16416 | 4502 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 7 | 16416 | 4502 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 12 | 14540 | 8 | 16416 | 4503 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 9 | 16416 | 4503 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 13 | 14540 | 10 | 16416 | 4503 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 11 | 16416 | 4503 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 14 | 14540 | 12 | 16416 | 4503 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 13 | 16416 | 4503 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 15 | 14540 | 14 | 16416 | 4503 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14540 | 15 | 16416 | 4503 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL UPS CATIIIA - UOB Output Switch | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10002 | 0 | 14541 | 0 | 16416 | 4504 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14541 | 1 | 16416 | 4504 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14541 | 2 | 16416 | 4504 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 3 | 16416 | 4504 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14541 | 4 | 16416 | 4504 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 5 | 16416 | 4504 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14541 | 6 | 16416 | 4504 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 7 | 16416 | 4504 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14541 | 8 | 16416 | 4505 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 9 | 16416 | 4505 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14541 | 10 | 16416 | 4505 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 11 | 16416 | 4505 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14541 | 12 | 16416 | 4505 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 13 | 16416 | 4505 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14541 | 14 | 16416 | 4505 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14541 | 15 | 16416 | 4505 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Manu-Bypass Switch | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10003 | 0 | 14542 | 0 | 16416 | 4506 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14542 | 1 | 16416 | 4506 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14542 | 2 | 16416 | 4506 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 3 | 16416 | 4506 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14542 | 4 | 16416 | 4506 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 5 | 16416 | 4506 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14542 | 6 | 16416 | 4506 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 7 | 16416 | 4506 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14542 | 8 | 16416 | 4507 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 9 | 16416 | 4507 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14542 | 10 | 16416 | 4507 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 11 | 16416 | 4507 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14542 | 12 | 16416 | 4507 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 13 | 16416 | 4507 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14542 | 14 | 16416 | 4507 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14542 | 15 | 16416 | 4507 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Load over INV capacity | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10026 | 0 | 14543 | 0 | 16416 | 4508 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14543 | 1 | 16416 | 4508 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14543 | 2 | 16416 | 4508 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 3 | 16416 | 4508 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14543 | 4 | 16416 | 4508 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 5 | 16416 | 4508 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14543 | 6 | 16416 | 4508 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 7 | 16416 | 4508 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14543 | 8 | 16416 | 4509 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 9 | 16416 | 4509 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14543 | 10 | 16416 | 4509 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 11 | 16416 | 4509 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14543 | 12 | 16416 | 4509 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 13 | 16416 | 4509 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14543 | 14 | 16416 | 4509 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14543 | 15 | 16416 | 4509 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Inverter EPO | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10033 | 0 | 14544 | 0 | 16416 | 4510 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14544 | 1 | 16416 | 4510 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14544 | 2 | 16416 | 4510 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 3 | 16416 | 4510 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14544 | 4 | 16416 | 4510 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 5 | 16416 | 4510 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14544 | 6 | 16416 | 4510 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 7 | 16416 | 4510 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14544 | 8 | 16416 | 4511 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 9 | 16416 | 4511 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14544 | 10 | 16416 | 4511 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 11 | 16416 | 4511 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14544 | 12 | 16416 | 4511 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 13 | 16416 | 4511 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14544 | 14 | 16416 | 4511 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14544 | 15 | 16416 | 4511 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Inverter fault | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10066 | 0 | 14545 | 0 | 16416 | 4512 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14545 | 1 | 16416 | 4512 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14545 | 2 | 16416 | 4512 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 3 | 16416 | 4512 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14545 | 4 | 16416 | 4512 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 5 | 16416 | 4512 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14545 | 6 | 16416 | 4512 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 7 | 16416 | 4512 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14545 | 8 | 16416 | 4513 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 9 | 16416 | 4513 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14545 | 10 | 16416 | 4513 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 11 | 16416 | 4513 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14545 | 12 | 16416 | 4513 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 13 | 16416 | 4513 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14545 | 14 | 16416 | 4513 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14545 | 15 | 16416 | 4513 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Fan fault | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10068 | 0 | 14546 | 0 | 16416 | 4514 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14546 | 1 | 16416 | 4514 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14546 | 2 | 16416 | 4514 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 3 | 16416 | 4514 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14546 | 4 | 16416 | 4514 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 5 | 16416 | 4514 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14546 | 6 | 16416 | 4514 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 7 | 16416 | 4514 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14546 | 8 | 16416 | 4515 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 9 | 16416 | 4515 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14546 | 10 | 16416 | 4515 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 11 | 16416 | 4515 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14546 | 12 | 16416 | 4515 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 13 | 16416 | 4515 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14546 | 14 | 16416 | 4515 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14546 | 15 | 16416 | 4515 | 7 | EL6021 - UPS/TGBT CATIII
| UPS CATIIIA - Charger fault | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10076 | 0 | 14547 | 0 | 16416 | 4516 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14547 | 1 | 16416 | 4516 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14547 | 2 | 16416 | 4516 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 3 | 16416 | 4516 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14547 | 4 | 16416 | 4516 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 5 | 16416 | 4516 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14547 | 6 | 16416 | 4516 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 7 | 16416 | 4516 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14547 | 8 | 16416 | 4517 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 9 | 16416 | 4517 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14547 | 10 | 16416 | 4517 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 11 | 16416 | 4517 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14547 | 12 | 16416 | 4517 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 13 | 16416 | 4517 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14547 | 14 | 16416 | 4517 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14547 | 15 | 16416 | 4517 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Batt. polarity reversed | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10083 | 0 | 14548 | 0 | 16416 | 4518 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14548 | 1 | 16416 | 4518 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14548 | 2 | 16416 | 4518 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 3 | 16416 | 4518 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14548 | 4 | 16416 | 4518 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 5 | 16416 | 4518 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14548 | 6 | 16416 | 4518 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 7 | 16416 | 4518 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14548 | 8 | 16416 | 4519 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 9 | 16416 | 4519 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14548 | 10 | 16416 | 4519 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 11 | 16416 | 4519 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14548 | 12 | 16416 | 4519 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 13 | 16416 | 4519 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14548 | 14 | 16416 | 4519 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14548 | 15 | 16416 | 4519 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - No battery connected | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10084 | 0 | 14549 | 0 | 16416 | 4520 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14549 | 1 | 16416 | 4520 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14549 | 2 | 16416 | 4520 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 3 | 16416 | 4520 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14549 | 4 | 16416 | 4520 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 5 | 16416 | 4520 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14549 | 6 | 16416 | 4520 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 7 | 16416 | 4520 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14549 | 8 | 16416 | 4521 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 9 | 16416 | 4521 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14549 | 10 | 16416 | 4521 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 11 | 16416 | 4521 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14549 | 12 | 16416 | 4521 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 13 | 16416 | 4521 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14549 | 14 | 16416 | 4521 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14549 | 15 | 16416 | 4521 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - Bypass overload | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10147 | 0 | 14550 | 0 | 16416 | 4522 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14550 | 1 | 16416 | 4522 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14550 | 2 | 16416 | 4522 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 3 | 16416 | 4522 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14550 | 4 | 16416 | 4522 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 5 | 16416 | 4522 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14550 | 6 | 16416 | 4522 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 7 | 16416 | 4522 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14550 | 8 | 16416 | 4523 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 9 | 16416 | 4523 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14550 | 10 | 16416 | 4523 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 11 | 16416 | 4523 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14550 | 12 | 16416 | 4523 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 13 | 16416 | 4523 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14550 | 14 | 16416 | 4523 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14550 | 15 | 16416 | 4523 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - BIL UPS Important Alarm | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10204 | 0 | 14551 | 0 | 16416 | 4524 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14551 | 1 | 16416 | 4524 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14551 | 2 | 16416 | 4524 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 3 | 16416 | 4524 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14551 | 4 | 16416 | 4524 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 5 | 16416 | 4524 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14551 | 6 | 16416 | 4524 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 7 | 16416 | 4524 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14551 | 8 | 16416 | 4525 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 9 | 16416 | 4525 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14551 | 10 | 16416 | 4525 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 11 | 16416 | 4525 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14551 | 12 | 16416 | 4525 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 13 | 16416 | 4525 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14551 | 14 | 16416 | 4525 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14551 | 15 | 16416 | 4525 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIA - BIL UPS over temperature | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10207 | 0 | 14552 | 0 | 16416 | 4526 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14552 | 1 | 16416 | 4526 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14552 | 2 | 16416 | 4526 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 3 | 16416 | 4526 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14552 | 4 | 16416 | 4526 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 5 | 16416 | 4526 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14552 | 6 | 16416 | 4526 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 7 | 16416 | 4526 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14552 | 8 | 16416 | 4527 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 9 | 16416 | 4527 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14552 | 10 | 16416 | 4527 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 11 | 16416 | 4527 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14552 | 12 | 16416 | 4527 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 13 | 16416 | 4527 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14552 | 14 | 16416 | 4527 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14552 | 15 | 16416 | 4527 | 7 | EL6021 - UPS/TGBT CATIII
EFR9003 | BIL UPS CATIIIB - Input frequency | MA | N | RES | 4 | E |  |  | Hz | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30004 | 0 | 14600 | 0 | 16416 | 4622 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003I1 | BIL UPS CATIIIB - Input current phase A | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30005 | 0 | 14601 | 0 | 16416 | 4624 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003I2 | BIL UPS CATIIIB - Input current phase B | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30006 | 0 | 14602 | 0 | 16416 | 4626 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003I3 | BIL UPS CATIIIB - Input current phase C | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30007 | 0 | 14603 | 0 | 16416 | 4628 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EFR9004 | BIL UPS CATIIIB - Output frequency | MA | N | RES | 4 | E |  |  | Hz | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30014 | 0 | 14604 | 0 | 16416 | 4630 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9004I1 | BIL UPS CATIIIB - Output current phase A | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30015 | 0 | 14605 | 0 | 16416 | 4632 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9004I2 | BIL UPS CATIIIB - Output current phase B | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30016 | 0 | 14606 | 0 | 16416 | 4634 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9004I3 | BIL UPS CATIIIB - Output current phase C | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30017 | 0 | 14607 | 0 | 16416 | 4636 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9004P1 | BIL UPS CATIIIB - Output kW phase A | MA | N | RES | 4 | E |  |  | kW | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30018 | 0 | 14608 | 0 | 16416 | 4638 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9004P2 | BIL UPS CATIIIB - Output kW phase B | MA | N | RES | 4 | E |  |  | kW | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30019 | 0 | 14609 | 0 | 16416 | 4640 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9004P3 | BIL UPS CATIIIB - Output kW phase C | MA | N | RES | 4 | E |  |  | kW | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30020 | 0 | 14610 | 0 | 16416 | 4642 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9004L1 | BIL UPS CATIIIB - Load percent phase A | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30021 | 0 | 14611 | 0 | 16416 | 4644 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9004L2 | BIL UPS CATIIIB - Load percent phase B | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30022 | 0 | 14612 | 0 | 16416 | 4646 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9004L3 | BIL UPS CATIIIB - Load percent phase C | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30023 | 0 | 14613 | 0 | 16416 | 4648 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9004CF1 | BIL UPS CATIIIB - Output A phase load peak ratio | MA | N | RES | 4 | E |  |  |  | 0.01 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30024 | 0 | 14614 | 0 | 16416 | 4650 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9004CF2 | BIL UPS CATIIIB - Output B phase load peak ratio | MA | N | RES | 4 | E |  |  |  | 0.01 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30025 | 0 | 14615 | 0 | 16416 | 4652 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9004CF3 | BIL UPS CATIIIB - Output C phase load peak ratio | MA | N | RES | 4 | E |  |  |  | 0.01 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30026 | 0 | 14616 | 0 | 16416 | 4654 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR9003UBP | BIL UPS CATIIIB - Battery voltage positive | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30031 | 0 | 14617 | 0 | 16416 | 4656 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR9003UBM | BIL UPS CATIIIB - Battery voltage negative | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30032 | 0 | 14618 | 0 | 16416 | 4658 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003DP | BIL UPS CATIIIB - Positive battery discharge current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30033 | 0 | 14619 | 0 | 16416 | 4660 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003DM | BIL UPS CATIIIB - Negative battery discharge current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30034 | 0 | 14620 | 0 | 16416 | 4662 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003CP | BIL UPS CATIIIB - Positive battery charging current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30035 | 0 | 14621 | 0 | 16416 | 4664 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EIR9003CM | BIL UPS CATIIIB - Negative battery charging current | MA | N | RES | 4 | E |  |  | A | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30036 | 0 | 14622 | 0 | 16416 | 4666 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ENR9003 | BIL UPS CATIIIB - Battery capacity | MA | N | RES | 4 | E |  |  | % | 1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30037 | 0 | 14623 | 0 | 16416 | 4668 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EDR9003 | BIL UPS CATIIIB - Battery backup time | MA | N | RES | 4 | E |  |  | Min | 1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30038 | 0 | 14624 | 0 | 16416 | 4670 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ETR9003 | BIL UPS CATIIIB - Battery temperature | MA | N | RES | 4 | E |  |  | °C | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30039 | 0 | 14625 | 0 | 16416 | 4672 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
ETR9004 | BIL UPS CATIIIB - Ambient temperature | MA | N | RES | 4 | E |  |  | °C | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30040 | 0 | 14626 | 0 | 16416 | 4674 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9004S1 | BIL UPS CATIIIB - Output kVA phase A | MA | N | RES | 4 | E |  |  | kVA | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30047 | 0 | 14627 | 0 | 16416 | 4676 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9004S2 | BIL UPS CATIIIB - Output kVA phase B | MA | N | RES | 4 | E |  |  | kVA | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30048 | 0 | 14628 | 0 | 16416 | 4678 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EWR9004S3 | BIL UPS CATIIIB - Output kVA phase C | MA | N | RES | 4 | E |  |  | kVA | 0.1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30049 | 0 | 14629 | 0 | 16416 | 4680 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900312 | BIL UPS CATIIIB - Input AB line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92_1 |  | BIL | 16 |  |  | 30050 | 0 | 14630 | 0 | 16416 | 4682 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900323 | BIL UPS CATIIIB - Input BC line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92_1 |  | BIL | 16 |  |  | 30051 | 0 | 14631 | 0 | 16416 | 4684 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900331 | BIL UPS CATIIIB - Input CA line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92_1 |  | BIL | 16 |  |  | 30052 | 0 | 14632 | 0 | 16416 | 4686 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900412 | BIL UPS CATIIIB - Output AB line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92_1 |  | BIL | 16 |  |  | 30056 | 0 | 14633 | 0 | 16416 | 4688 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900423 | BIL UPS CATIIIB - Output BC line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92_1 |  | BIL | 16 |  |  | 30057 | 0 | 14634 | 0 | 16416 | 4690 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUR900431 | BIL UPS CATIIIB - Output CA line voltage | MA | N | RES | 4 | E |  |  | V | 0.1 | [23 empty] | 2000 |  | E92_1 |  | BIL | 16 |  |  | 30058 | 0 | 14635 | 0 | 16416 | 4692 | 0 | EL6021 - UPS/TGBT CATIII |  | U16
EUL9003D | BIL UPS CATIIIB - BIL UPS system status | MA | N | RES | 4 | E |  |  |  | 1 | [23 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 30071 | 0 | 14636 | 0 | 16416 | 4694 | 0 | EL6021 - UPS/TGBT CATIII |  | U16 | 0x0000 - Initialize 0x0001 - Standby operation 0x0002 - Output is off 0x0003 - Bypass operation 0x0004 - Normal operation 0x0005 - Battery operation 0x0006 - Battery self-test 0x0008 - ECO Mode 0x0009 - EPO activated 0x000A - Maintenance bypass op. 0x000D - Hybrid operation 0x000E - Self-aging mode 0x0014 - REC is OFF 0x0015 - Input 0x0016 - On battery 0x001E - Inverter standby 0x001F - Inverter Output 0x0020 - Inverter self-aging 0x0028 - ECU is Off 0x0029 - ECU Standby 0x002A - ECU active
EUL9004D1 | BIL Output dry contact - OFF | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 0 | 14637 | 0 | 16416 | 4696 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 1 | 16416 | 4696 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D2 | BIL Output dry contact - Common Alarm | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 1 | 14637 | 2 | 16416 | 4696 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 3 | 16416 | 4696 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D3 | BIL Output dry contact - Normal Operation | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 2 | 14637 | 4 | 16416 | 4696 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 5 | 16416 | 4696 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D4 | BIL Output dry contact - Battery Operation | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 3 | 14637 | 6 | 16416 | 4696 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 7 | 16416 | 4696 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D5 | BIL Output dry contact - Static Bypass | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 4 | 14637 | 8 | 16416 | 4697 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 9 | 16416 | 4697 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D6 | BIL Output dry contact - Output Overloaded | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 5 | 14637 | 10 | 16416 | 4697 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 11 | 16416 | 4697 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D7 | BIL Output dry contact - Fan Inoperable | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 6 | 14637 | 12 | 16416 | 4697 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 13 | 16416 | 4697 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D8 | BIL Output dry contact - Battery Fault | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 7 | 14637 | 14 | 16416 | 4697 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14637 | 15 | 16416 | 4697 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D9 | BIL Output dry contact - Battery Disconnected | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 8 | 14638 | 0 | 16416 | 4698 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 1 | 16416 | 4698 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D10 | BIL Output dry contact - Battery Voltage Low | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 9 | 14638 | 2 | 16416 | 4698 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 3 | 16416 | 4698 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D11 | BIL Output dry contact - Input Out Of Tolerance | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 10 | 14638 | 4 | 16416 | 4698 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 5 | 16416 | 4698 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D12 | BIL Output dry contact - Bypass Out Of Tolerance | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 11 | 14638 | 6 | 16416 | 4698 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 7 | 16416 | 4698 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D13 | BIL Output dry contact - EPO Activated | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 12 | 14638 | 8 | 16416 | 4699 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 9 | 16416 | 4699 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9004D14 | BIL Output dry contact - Maintenance Mode | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40201 | 13 | 14638 | 10 | 16416 | 4699 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 11 | 16416 | 4699 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Output dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40201 | 14 | 14638 | 12 | 16416 | 4699 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 13 | 16416 | 4699 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Output dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40201 | 15 | 14638 | 14 | 16416 | 4699 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14638 | 15 | 16416 | 4699 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D1 | BIL Input dry contact - OFF | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 0 | 14639 | 0 | 16416 | 4700 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 1 | 16416 | 4700 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D2 | BIL Input dry contact - UPS ON | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 1 | 14639 | 2 | 16416 | 4700 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 3 | 16416 | 4700 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D3 | BIL Input dry contact - UPS OFF | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 2 | 14639 | 4 | 16416 | 4700 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 5 | 16416 | 4700 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D4 | BIL Input dry contact - Battery Fault | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 3 | 14639 | 6 | 16416 | 4700 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 7 | 16416 | 4700 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D5 | BIL Input dry contact - Genset enable | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 4 | 14639 | 8 | 16416 | 4701 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 9 | 16416 | 4701 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D6 | BIL Input dry contact - Custom Alarm 3 | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 5 | 14639 | 10 | 16416 | 4701 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 11 | 16416 | 4701 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D7 | BIL Input dry contact - Custom Alarm 4 | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 6 | 14639 | 12 | 16416 | 4701 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 13 | 16416 | 4701 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D8 | BIL Input dry contact - Disable ECO | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 7 | 14639 | 14 | 16416 | 4701 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14639 | 15 | 16416 | 4701 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
EUL9003D9 | BIL Input dry contact - Force INV off | CR | N | RES | 4 | E | [27 empty] | 2000 |  | E92 |  | BIL | 16 |  |  | 40221 | 8 | 14640 | 0 | 16416 | 4702 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 1 | 16416 | 4702 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 9 | 14640 | 2 | 16416 | 4702 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 3 | 16416 | 4702 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 10 | 14640 | 4 | 16416 | 4702 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 5 | 16416 | 4702 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 11 | 14640 | 6 | 16416 | 4702 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 7 | 16416 | 4702 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 12 | 14640 | 8 | 16416 | 4703 | 0 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 9 | 16416 | 4703 | 1 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 13 | 14640 | 10 | 16416 | 4703 | 2 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 11 | 16416 | 4703 | 3 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 14 | 14640 | 12 | 16416 | 4703 | 4 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 13 | 16416 | 4703 | 5 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL Input dry contact - Not Used |  | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 40221 | 15 | 14640 | 14 | 16416 | 4703 | 6 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14640 | 15 | 16416 | 4703 | 7 | EL6021 - UPS/TGBT CATIII |  | BITVAL
| BIL UPS CATIIIB - UOB Output Switch | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10002 | 0 | 14641 | 0 | 16416 | 4704 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14641 | 1 | 16416 | 4704 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14641 | 2 | 16416 | 4704 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 3 | 16416 | 4704 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14641 | 4 | 16416 | 4704 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 5 | 16416 | 4704 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14641 | 6 | 16416 | 4704 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 7 | 16416 | 4704 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14641 | 8 | 16416 | 4705 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 9 | 16416 | 4705 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14641 | 10 | 16416 | 4705 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 11 | 16416 | 4705 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14641 | 12 | 16416 | 4705 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 13 | 16416 | 4705 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14641 | 14 | 16416 | 4705 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14641 | 15 | 16416 | 4705 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Manu-Bypass Switch | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10003 | 0 | 14642 | 0 | 16416 | 4706 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14642 | 1 | 16416 | 4706 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14642 | 2 | 16416 | 4706 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 3 | 16416 | 4706 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14642 | 4 | 16416 | 4706 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 5 | 16416 | 4706 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14642 | 6 | 16416 | 4706 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 7 | 16416 | 4706 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14642 | 8 | 16416 | 4707 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 9 | 16416 | 4707 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14642 | 10 | 16416 | 4707 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 11 | 16416 | 4707 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14642 | 12 | 16416 | 4707 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 13 | 16416 | 4707 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14642 | 14 | 16416 | 4707 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14642 | 15 | 16416 | 4707 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Load over INV capacity | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10026 | 0 | 14643 | 0 | 16416 | 4708 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14643 | 1 | 16416 | 4708 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14643 | 2 | 16416 | 4708 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 3 | 16416 | 4708 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14643 | 4 | 16416 | 4708 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 5 | 16416 | 4708 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14643 | 6 | 16416 | 4708 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 7 | 16416 | 4708 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14643 | 8 | 16416 | 4709 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 9 | 16416 | 4709 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14643 | 10 | 16416 | 4709 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 11 | 16416 | 4709 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14643 | 12 | 16416 | 4709 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 13 | 16416 | 4709 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14643 | 14 | 16416 | 4709 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14643 | 15 | 16416 | 4709 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Inverter EPO | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10033 | 0 | 14644 | 0 | 16416 | 4710 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14644 | 1 | 16416 | 4710 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14644 | 2 | 16416 | 4710 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 3 | 16416 | 4710 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14644 | 4 | 16416 | 4710 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 5 | 16416 | 4710 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14644 | 6 | 16416 | 4710 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 7 | 16416 | 4710 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14644 | 8 | 16416 | 4711 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 9 | 16416 | 4711 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14644 | 10 | 16416 | 4711 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 11 | 16416 | 4711 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14644 | 12 | 16416 | 4711 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 13 | 16416 | 4711 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14644 | 14 | 16416 | 4711 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14644 | 15 | 16416 | 4711 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Inverter fault | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10066 | 0 | 14645 | 0 | 16416 | 4712 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14645 | 1 | 16416 | 4712 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14645 | 2 | 16416 | 4712 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 3 | 16416 | 4712 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14645 | 4 | 16416 | 4712 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 5 | 16416 | 4712 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14645 | 6 | 16416 | 4712 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 7 | 16416 | 4712 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14645 | 8 | 16416 | 4713 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 9 | 16416 | 4713 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14645 | 10 | 16416 | 4713 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 11 | 16416 | 4713 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14645 | 12 | 16416 | 4713 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 13 | 16416 | 4713 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14645 | 14 | 16416 | 4713 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14645 | 15 | 16416 | 4713 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Fan fault | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10068 | 0 | 14646 | 0 | 16416 | 4714 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14646 | 1 | 16416 | 4714 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14646 | 2 | 16416 | 4714 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 3 | 16416 | 4714 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14646 | 4 | 16416 | 4714 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 5 | 16416 | 4714 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14646 | 6 | 16416 | 4714 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 7 | 16416 | 4714 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14646 | 8 | 16416 | 4715 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 9 | 16416 | 4715 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14646 | 10 | 16416 | 4715 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 11 | 16416 | 4715 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14646 | 12 | 16416 | 4715 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 13 | 16416 | 4715 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14646 | 14 | 16416 | 4715 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14646 | 15 | 16416 | 4715 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Charger fault | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10076 | 0 | 14647 | 0 | 16416 | 4716 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14647 | 1 | 16416 | 4716 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14647 | 2 | 16416 | 4716 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 3 | 16416 | 4716 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14647 | 4 | 16416 | 4716 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 5 | 16416 | 4716 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14647 | 6 | 16416 | 4716 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 7 | 16416 | 4716 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14647 | 8 | 16416 | 4717 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 9 | 16416 | 4717 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14647 | 10 | 16416 | 4717 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 11 | 16416 | 4717 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14647 | 12 | 16416 | 4717 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 13 | 16416 | 4717 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14647 | 14 | 16416 | 4717 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14647 | 15 | 16416 | 4717 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Batt. polarity reversed | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10083 | 0 | 14648 | 0 | 16416 | 4718 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14648 | 1 | 16416 | 4718 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14648 | 2 | 16416 | 4718 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 3 | 16416 | 4718 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14648 | 4 | 16416 | 4718 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 5 | 16416 | 4718 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14648 | 6 | 16416 | 4718 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 7 | 16416 | 4718 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14648 | 8 | 16416 | 4719 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 9 | 16416 | 4719 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14648 | 10 | 16416 | 4719 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 11 | 16416 | 4719 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14648 | 12 | 16416 | 4719 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 13 | 16416 | 4719 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14648 | 14 | 16416 | 4719 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14648 | 15 | 16416 | 4719 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - No battery connected | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10084 | 0 | 14649 | 0 | 16416 | 4720 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14649 | 1 | 16416 | 4720 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14649 | 2 | 16416 | 4720 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 3 | 16416 | 4720 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14649 | 4 | 16416 | 4720 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 5 | 16416 | 4720 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14649 | 6 | 16416 | 4720 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 7 | 16416 | 4720 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14649 | 8 | 16416 | 4721 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 9 | 16416 | 4721 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14649 | 10 | 16416 | 4721 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 11 | 16416 | 4721 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14649 | 12 | 16416 | 4721 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 13 | 16416 | 4721 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14649 | 14 | 16416 | 4721 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14649 | 15 | 16416 | 4721 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - Bypass overload | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10147 | 0 | 14650 | 0 | 16416 | 4722 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14650 | 1 | 16416 | 4722 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14650 | 2 | 16416 | 4722 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 3 | 16416 | 4722 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14650 | 4 | 16416 | 4722 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 5 | 16416 | 4722 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14650 | 6 | 16416 | 4722 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 7 | 16416 | 4722 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14650 | 8 | 16416 | 4723 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 9 | 16416 | 4723 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14650 | 10 | 16416 | 4723 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 11 | 16416 | 4723 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14650 | 12 | 16416 | 4723 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 13 | 16416 | 4723 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14650 | 14 | 16416 | 4723 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14650 | 15 | 16416 | 4723 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - BIL UPS Important Alarm | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10204 | 0 | 14651 | 0 | 16416 | 4724 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14651 | 1 | 16416 | 4724 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14651 | 2 | 16416 | 4724 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 3 | 16416 | 4724 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14651 | 4 | 16416 | 4724 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 5 | 16416 | 4724 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14651 | 6 | 16416 | 4724 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 7 | 16416 | 4724 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14651 | 8 | 16416 | 4725 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 9 | 16416 | 4725 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14651 | 10 | 16416 | 4725 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 11 | 16416 | 4725 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14651 | 12 | 16416 | 4725 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 13 | 16416 | 4725 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14651 | 14 | 16416 | 4725 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14651 | 15 | 16416 | 4725 | 7 | EL6021 - UPS/TGBT CATIII
| BIL UPS CATIIIB - BIL UPS over temperature | CR | N | RES | 4 | E | [31 empty] | BIL | 16 |  |  | 10207 | 0 | 14652 | 0 | 16416 | 4726 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [36 empty] | BIL | 16 |  |  |  |  | 14652 | 1 | 16416 | 4726 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 1 | 14652 | 2 | 16416 | 4726 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 3 | 16416 | 4726 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 2 | 14652 | 4 | 16416 | 4726 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 5 | 16416 | 4726 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 3 | 14652 | 6 | 16416 | 4726 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 7 | 16416 | 4726 | 7 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 4 | 14652 | 8 | 16416 | 4727 | 0 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 9 | 16416 | 4727 | 1 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 5 | 14652 | 10 | 16416 | 4727 | 2 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 11 | 16416 | 4727 | 3 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 6 | 14652 | 12 | 16416 | 4727 | 4 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 13 | 16416 | 4727 | 5 | EL6021 - UPS/TGBT CATIII
| N/A | [41 empty] | 7 | 14652 | 14 | 16416 | 4727 | 6 | EL6021 - UPS/TGBT CATIII
| VALIDITY | [42 empty] | 14652 | 15 | 16416 | 4727 | 7 | EL6021 - UPS/TGBT CATIII
???? | Courant Phase 1 CAT2 TGBT | MA | N | RES | 4 | E |  |  | A | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32028 | 0 | 14700 | 0 | 16416 | 4822 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Courant Phase 2 CAT2 TGBT | MA | N | RES | 4 | E |  |  | A | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32030 | 0 | 14702 | 0 | 16416 | 4826 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Courant Phase3 CAT2 TGBT | MA | N | RES | 4 | E |  |  | A | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32032 | 0 | 14704 | 0 | 16416 | 4830 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Tension Composée Phase 1 et 2 CAT2 TGBT | MA | N | RES | 4 | E |  |  | V | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32056 | 0 | 14706 | 0 | 16416 | 4834 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Tension Composée Phase 2 et 3 CAT2 TGBT | MA | N | RES | 4 | E |  |  | V | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32058 | 0 | 14708 | 0 | 16416 | 4838 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Tension Composée Phase 3 et 1 CAT2 TGBT | MA | N | RES | 4 | E |  |  | V | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32060 | 0 | 14710 | 0 | 16416 | 4842 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Fréquence QF4000 TGBT CAT2 | MA | N | RES | 4 | E |  |  | Hz |  | 40Hz | 70Hz | [21 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32068 | 0 | 14712 | 0 | 16416 | 4846 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Puissance Active Totale CAT2 TGBT | MA | N | RES | 4 | E |  |  | W | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32078 | 0 | 14714 | 0 | 16416 | 4850 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Puissance Réactive Totale CAT2 TGBT | MA | N | RES | 4 | E |  |  | Var | [24 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32080 | 0 | 14716 | 0 | 16416 | 4854 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Cosinus Phi Phase 1 CAT2 TGBT | MA | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 32212 | 0 | 14718 | 0 | 16416 | 4858 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Surveillance Tension CAT2 TGBT - Undervoltage | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 12500 | 5 | 14720 | 10 | 16416 | 4863 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | Surveillance Tension JDB CAT2 TGBT - Overvoltage | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 19 | 3 | 12500 | 6 | 14720 | 12 | 16416 | 4863 | 4 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | Courant Phase 1 CAT1 TGBT | MA | N | RES | 4 | E |  |  | A | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32028 | 0 | 14730 | 0 | 16416 | 4882 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Courant Phase 2 CAT1 TGBT | MA | N | RES | 4 | E |  |  | A | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32030 | 0 | 14732 | 0 | 16416 | 4886 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Courant Phase3 CAT1 TGBT | MA | N | RES | 4 | E |  |  | A | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32032 | 0 | 14734 | 0 | 16416 | 4890 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Tension Composée Phase 1 et 2 CAT1 TGBT | MA | N | RES | 4 | E |  |  | V | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32056 | 0 | 14736 | 0 | 16416 | 4894 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Tension Composée Phase 2 et 3 CAT1 TGBT | MA | N | RES | 4 | E |  |  | V | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32058 | 0 | 14738 | 0 | 16416 | 4898 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Tension Composée Phase 3 et 1 CAT1 TGBT | MA | N | RES | 4 | E |  |  | V | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32060 | 0 | 14740 | 0 | 16416 | 4902 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Fréquence QF4000 TGBT CAT1 | MA | N | RES | 4 | E |  |  | Hz |  | 40Hz | 70Hz | [21 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32068 | 0 | 14742 | 0 | 16416 | 4906 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Puissance Active Totale CAT1 TGBT | MA | N | RES | 4 | E |  |  | W | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32078 | 0 | 14744 | 0 | 16416 | 4910 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Puissance Réactive Totale CAT1 TGBT | MA | N | RES | 4 | E |  |  | Var | [24 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32080 | 0 | 14746 | 0 | 16416 | 4914 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Cosinus Phi Phase 1 CAT1 TGBT | MA | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 32212 | 0 | 14748 | 0 | 16416 | 4918 | 0 | EL6021 - TGBT CATI/II |  | I32
???? | Surveillance Tension CAT1 TGBT - Undervoltage | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 12500 | 5 | 14750 | 10 | 16416 | 4923 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | Surveillance Tension JDB CAT1 TGBT - Overvoltage | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 20 | 3 | 12500 | 6 | 14750 | 12 | 16416 | 4923 | 4 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4002 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14281 | 0 | 14760 | 0 | 16416 | 4942 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4002 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14281 | 1 | 14760 | 2 | 16416 | 4942 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4003 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14321 | 0 | 14761 | 0 | 16416 | 4944 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4003 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14321 | 1 | 14761 | 2 | 16416 | 4944 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4004 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14361 | 0 | 14762 | 0 | 16416 | 4946 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4004 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14361 | 1 | 14762 | 2 | 16416 | 4946 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4012 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14441 | 0 | 14763 | 0 | 16416 | 4948 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4012 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14441 | 1 | 14763 | 2 | 16416 | 4948 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4014 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14521 | 0 | 14764 | 0 | 16416 | 4950 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4014 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 15 | 3 | 14521 | 1 | 14764 | 2 | 16416 | 4950 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4005 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14201 | 0 | 14765 | 0 | 16416 | 4952 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4005 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14201 | 1 | 14765 | 2 | 16416 | 4952 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4006 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14241 | 0 | 14766 | 0 | 16416 | 4954 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4006 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14241 | 1 | 14766 | 2 | 16416 | 4954 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4007 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14281 | 0 | 14767 | 0 | 16416 | 4956 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4007 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14281 | 1 | 14767 | 2 | 16416 | 4956 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4008 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14321 | 0 | 14768 | 0 | 16416 | 4958 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4008 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14321 | 1 | 14768 | 2 | 16416 | 4958 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4009 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14361 | 0 | 14769 | 0 | 16416 | 4960 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4009 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14361 | 1 | 14769 | 2 | 16416 | 4960 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4010 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14401 | 0 | 14770 | 0 | 16416 | 4962 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4010 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14401 | 1 | 14770 | 2 | 16416 | 4962 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4011 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14441 | 0 | 14771 | 0 | 16416 | 4964 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4011 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14441 | 1 | 14771 | 2 | 16416 | 4964 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4013 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14481 | 0 | 14772 | 0 | 16416 | 4966 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4013 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14481 | 1 | 14772 | 2 | 16416 | 4966 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4015 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14521 | 0 | 14773 | 0 | 16416 | 4968 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4015 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 16 | 3 | 14521 | 1 | 14773 | 2 | 16416 | 4968 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4021 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 17 | 3 | 14481 | 0 | 14774 | 0 | 16416 | 4970 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4021 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 17 | 3 | 14481 | 1 | 14774 | 2 | 16416 | 4970 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4022 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 17 | 3 | 14521 | 0 | 14775 | 0 | 16416 | 4972 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4022 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 17 | 3 | 14521 | 1 | 14775 | 2 | 16416 | 4972 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4018 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 17 | 3 | 14561 | 0 | 14776 | 0 | 16416 | 4974 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4018 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 17 | 3 | 14561 | 1 | 14776 | 2 | 16416 | 4974 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4016 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14201 | 0 | 14777 | 0 | 16416 | 4976 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4016 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14201 | 1 | 14777 | 2 | 16416 | 4976 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4017 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14241 | 0 | 14778 | 0 | 16416 | 4978 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4017 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14241 | 1 | 14778 | 2 | 16416 | 4978 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4023 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14281 | 0 | 14779 | 0 | 16416 | 4980 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4023 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14281 | 1 | 14779 | 2 | 16416 | 4980 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4024 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14321 | 0 | 14780 | 0 | 16416 | 4982 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4024 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14321 | 1 | 14780 | 2 | 16416 | 4982 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4025 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14361 | 0 | 14781 | 0 | 16416 | 4984 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4025 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14361 | 1 | 14781 | 2 | 16416 | 4984 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4026 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14401 | 0 | 14782 | 0 | 16416 | 4986 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4026 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14401 | 1 | 14782 | 2 | 16416 | 4986 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4027 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14441 | 0 | 14783 | 0 | 16416 | 4988 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4027 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14441 | 1 | 14783 | 2 | 16416 | 4988 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4028 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14481 | 0 | 14784 | 0 | 16416 | 4990 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4028 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14481 | 1 | 14784 | 2 | 16416 | 4990 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4019 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14521 | 0 | 14785 | 0 | 16416 | 4992 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4019 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14521 | 1 | 14785 | 2 | 16416 | 4992 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4020 - OF | CR | N | RES | 4 | E | [27 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14561 | 0 | 14786 | 0 | 16416 | 4994 | 0 | EL6021 - TGBT CATI/II |  | BIT_VAL
???? | QF4020 - SD | AL | N | RES | 4 | E | [9 empty] | x == 1 | [17 empty] | 2000 |  |  |  | BIL | 15 | 18 | 3 | 14561 | 1 | 14786 | 2 | 16416 | 4994 | 2 | EL6021 - TGBT CATI/II |  | BIT_VAL
WCO6001M | MARCHE CAMERA CN1 ATT SHELTER NORD | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 7 | 12379 | 14 | 16416 | 181 | 6 | EL6021_M176 |  | BITVAL
WCO6002M | MARCHE CAMERA CN2 ATT SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 11 | 12380 | 6 | 16416 | 182 | 6 | EL6021_M176 |  | BITVAL
WCO6003M | MARCHE CAMERA CN3 POE SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 13 | 12380 | 10 | 16416 | 183 | 2 | EL6021_M176 |  | BITVAL
WCO6004M | MARCHE CAMERA CN4 ATT SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 15 | 12380 | 14 | 16416 | 183 | 6 | EL6021_M176 |  | BITVAL
WCO6005M | MARCHE CAMERA CN5 POE SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 101 | 1 | 12381 | 2 | 16416 | 184 | 2 | EL6021_M176 |  | BITVAL
SZI8020W | Pandora - FC2020 synthèse de défaut d’alimentation | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | PANDORA Etat Centrale DI | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1000 | 9 | 14292 | 2 | 16416 | 4006 | 2 | EL6021_M11 |  | BITVAL
SSY8020D | Pandora - FC2020 BUS Line Open | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | PANDORA Etat Centrale DI | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 6607 | 13 | 14294 | 10 | 16416 | 4011 | 2 | EL6021_M11 |  | BITVAL
SZI8001W | Pandora - Salle Meteo 0001 - ZDA01 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1500 | 15 | 14296 | 14 | 16416 | 4015 | 6 | EL6021_M11 |  | BITVAL
SZI8002W | Pandora - Accueil 0003 - ZDA02 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1501 | 15 | 14298 | 14 | 16416 | 4019 | 6 | EL6021_M11 |  | BITVAL
SZI8003W | Pandora - Salle Dir 0005 - ZDA03 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1502 | 15 | 14300 | 14 | 16416 | 4023 | 6 | EL6021_M11 |  | BITVAL
SZI8004W | Pandora - Salle D'Operation 0006 - ZDA04 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1503 | 15 | 14302 | 14 | 16416 | 4027 | 6 | EL6021_M11 |  | BITVAL
SZI8005W | Pandora - Salle Das Et Cdc 0007 - ZDA05 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1504 | 15 | 14304 | 14 | 16416 | 4031 | 6 | EL6021_M11 |  | BITVAL
SZI8006W | Pandora - Salle Autorites 0008 - ZDA06 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1505 | 15 | 14306 | 14 | 16416 | 4035 | 6 | EL6021_M11 |  | BITVAL
SZI8007W | Pandora - Loc Cfs Et Banc De Controle 0009 - ZDA07 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1506 | 15 | 14308 | 14 | 16416 | 4039 | 6 | EL6021_M11 |  | BITVAL
SZI8008W | Pandora - Loc Telecom/Cfs 0010 - ZDA08 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1507 | 15 | 14310 | 14 | 16416 | 4043 | 6 | EL6021_M11 |  | BITVAL
SZI8009W | Pandora - Loc Energie 0011 - ZDA09 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1508 | 15 | 14312 | 14 | 16416 | 4047 | 6 | EL6021_M11 |  | BITVAL
SZI8010W | Pandora - Loc Onduleur 0012 - ZDA10 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1509 | 15 | 14314 | 14 | 16416 | 4051 | 6 | EL6021_M11 |  | BITVAL
SZI8011W | Pandora - Loc Batterie 0013 - ZDA11 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1510 | 15 | 14316 | 14 | 16416 | 4055 | 6 | EL6021_M11 |  | BITVAL
SZI8012W | Pandora - Loc Onduleur 0014 - ZDA12 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1511 | 15 | 14318 | 14 | 16416 | 4059 | 6 | EL6021_M11 |  | BITVAL
SZI8013W | Pandora - Loc Batterie 0015 - ZDA13 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1512 | 15 | 14320 | 14 | 16416 | 4063 | 6 | EL6021_M11 |  | BITVAL
SZI8014W | Pandora - Salle De Conviviabilite 0019 - ZDA14 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1513 | 15 | 14322 | 14 | 16416 | 4067 | 6 | EL6021_M11 |  | BITVAL
SCE8001W | Pandora - Alerte Evacuation Ouvrage - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1514 | 15 | 14324 | 14 | 16416 | 4071 | 6 | EL6021_M11 |  | BITVAL
SZI8015W | Pandora - Salle De Crise 0020 -ZDA15 - Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1515 | 15 | 14326 | 14 | 16416 | 4075 | 6 | EL6021_M11 |  | BITVAL
SZI8001D | Pandora - Salle Meteo 0001 - ZDA01 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1500 | 7 | 14295 | 14 | 16416 | 4013 | 6 | EL6021_M11 |  | BITVAL
SZI8002D | Pandora - Accueil 0003 - ZDA02 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1501 | 7 | 14297 | 14 | 16416 | 4017 | 6 | EL6021_M11 |  | BITVAL
SZI8003D | Pandora - Salle Dir 0005 - ZDA03 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1502 | 7 | 14299 | 14 | 16416 | 4021 | 6 | EL6021_M11 |  | BITVAL
SZI8004D | Pandora - Salle D'Operation 0006 - ZDA04 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1503 | 7 | 14301 | 14 | 16416 | 4025 | 6 | EL6021_M11 |  | BITVAL
SZI8005D | Pandora - Salle Das Et Cdc 0007 - ZDA05 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1504 | 7 | 14303 | 14 | 16416 | 4029 | 6 | EL6021_M11 |  | BITVAL
SZI8006D | Pandora - Salle Autorites 0008 - ZDA06 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1505 | 7 | 14305 | 14 | 16416 | 4033 | 6 | EL6021_M11 |  | BITVAL
SZI8007D | Pandora - Loc Cfs Et Banc De Controle 0009 - ZDA07 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1506 | 7 | 14307 | 14 | 16416 | 4037 | 6 | EL6021_M11 |  | BITVAL
SZI8008D | Pandora - Loc Telecom/Cfs 0010 - ZDA08 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1507 | 7 | 14309 | 14 | 16416 | 4041 | 6 | EL6021_M11 |  | BITVAL
SZI8009D | Pandora - Loc Energie 0011 - ZDA09 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1508 | 7 | 14311 | 14 | 16416 | 4045 | 6 | EL6021_M11 |  | BITVAL
SZI8010D | Pandora - Loc Onduleur 0012 - ZDA10 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1509 | 7 | 14313 | 14 | 16416 | 4049 | 6 | EL6021_M11 |  | BITVAL
SZI8011D | Pandora - Loc Batterie 0013 - ZDA11 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1510 | 7 | 14315 | 14 | 16416 | 4053 | 6 | EL6021_M11 |  | BITVAL
SZI8012D | Pandora - Loc Onduleur 0014 - ZDA12 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1511 | 7 | 14317 | 14 | 16416 | 4057 | 6 | EL6021_M11 |  | BITVAL
SZI8013D | Pandora - Loc Batterie 0015 - ZDA13 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1512 | 7 | 14319 | 14 | 16416 | 4061 | 6 | EL6021_M11 |  | BITVAL
SZI8014D | Pandora - Salle De Conviviabilite 0019 - ZDA14 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1513 | 7 | 14321 | 14 | 16416 | 4065 | 6 | EL6021_M11 |  | BITVAL
SCE8001D | Pandora - Alerte Evacuation Ouvrage - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1514 | 7 | 14323 | 14 | 16416 | 4069 | 6 | EL6021_M11 |  | BITVAL
SZI8015D | Pandora - Salle De Crise 0020 -ZDA15 - Hors Service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI80 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1515 | 7 | 14325 | 14 | 16416 | 4073 | 6 | EL6021_M11 |  | BITVAL
SZI81019W | Pandora - 264.001.SDJ1019/Salle Meteo 01 - Z1 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2500 | 15 | 14328 | 14 | 16416 | 4079 | 6 | EL6021_M11 |  | BITVAL
SZI81019D1 | Pandora - 264.001.SDJ1019/Salle Meteo 01 - Z1 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2500 | 13 | 14328 | 10 | 16416 | 4079 | 2 | EL6021_M11 |  | BITVAL
SZI81019D2 | Pandora - 264.001.SDJ1019/Salle Meteo 01 - Z1 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2500 | 7 | 14327 | 14 | 16416 | 4077 | 6 | EL6021_M11 |  | BITVAL
SZI81015W | Pandora - 264.003.SDJ1015/Acceuil 03 - Z2 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2501 | 15 | 14330 | 14 | 16416 | 4083 | 6 | EL6021_M11 |  | BITVAL
SZI81015D1 | Pandora - 264.003.SDJ1015/Acceuil 03 - Z2 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2501 | 13 | 14330 | 10 | 16416 | 4083 | 2 | EL6021_M11 |  | BITVAL
SZI81015D2 | Pandora - 264.003.SDJ1015/Acceuil 03 - Z2 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2501 | 7 | 14329 | 14 | 16416 | 4081 | 6 | EL6021_M11 |  | BITVAL
SZI81016W | Pandora - 264.003.SDJ1016/Acceuil 03 - Z2 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2502 | 15 | 14332 | 14 | 16416 | 4087 | 6 | EL6021_M11 |  | BITVAL
SZI81016D1 | Pandora - 264.003.SDJ1016/Acceuil 03 - Z2 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2502 | 13 | 14332 | 10 | 16416 | 4087 | 2 | EL6021_M11 |  | BITVAL
SZI81016D2 | Pandora - 264.003.SDJ1016/Acceuil 03 - Z2 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2502 | 7 | 14331 | 14 | 16416 | 4085 | 6 | EL6021_M11 |  | BITVAL
SZI81021W | Pandora - 264.003.SDJ1021/Acceuil 03 - Z2 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2503 | 15 | 14334 | 14 | 16416 | 4091 | 6 | EL6021_M11 |  | BITVAL
SZI81021D1 | Pandora - 264.003.SDJ1021/Acceuil 03 - Z2 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2503 | 13 | 14334 | 10 | 16416 | 4091 | 2 | EL6021_M11 |  | BITVAL
SZI81021D2 | Pandora - 264.003.SDJ1021/Acceuil 03 - Z2 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2503 | 7 | 14333 | 14 | 16416 | 4089 | 6 | EL6021_M11 |  | BITVAL
SZI81022W | Pandora - 264.005.SDJ1022/Salle DIR 05 - Z3 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2504 | 15 | 14336 | 14 | 16416 | 4095 | 6 | EL6021_M11 |  | BITVAL
SZI81022D1 | Pandora - 264.005.SDJ1022/Salle DIR 05 - Z3 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2504 | 13 | 14336 | 10 | 16416 | 4095 | 2 | EL6021_M11 |  | BITVAL
SZI81022D2 | Pandora - 264.005.SDJ1022/Salle DIR 05 - Z3 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2504 | 7 | 14335 | 14 | 16416 | 4093 | 6 | EL6021_M11 |  | BITVAL
SZI81009W | Pandora - 264.006.SDJ1009/Salle Operation 06-Z4 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2505 | 15 | 14338 | 14 | 16416 | 4099 | 6 | EL6021_M11 |  | BITVAL
SZI81009D1 | Pandora - 264.006.SDJ1009/Salle Operation 06-Z4 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2505 | 13 | 14338 | 10 | 16416 | 4099 | 2 | EL6021_M11 |  | BITVAL
SZI81009D2 | Pandora - 264.006.SDJ1009/Salle Operation 06-Z4 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2505 | 7 | 14337 | 14 | 16416 | 4097 | 6 | EL6021_M11 |  | BITVAL
SZI81010W | Pandora - 264.006.SDJ1010/Salle Operation 06-Z4 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2506 | 15 | 14340 | 14 | 16416 | 4103 | 6 | EL6021_M11 |  | BITVAL
SZI81010D1 | Pandora - 264.006.SDJ1010/Salle Operation 06-Z4 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2506 | 13 | 14340 | 10 | 16416 | 4103 | 2 | EL6021_M11 |  | BITVAL
SZI81010D2 | Pandora - 264.006.SDJ1010/Salle Operation 06-Z4 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2506 | 7 | 14339 | 14 | 16416 | 4101 | 6 | EL6021_M11 |  | BITVAL
SZI81011W | Pandora - 264.006.SDJ1011/Salle Operation 06-Z4 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2507 | 15 | 14342 | 14 | 16416 | 4107 | 6 | EL6021_M11 |  | BITVAL
SZI81011D1 | Pandora - 264.006.SDJ1011/Salle Operation 06-Z4 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2507 | 13 | 14342 | 10 | 16416 | 4107 | 2 | EL6021_M11 |  | BITVAL
SZI81011D2 | Pandora - 264.006.SDJ1011/Salle Operation 06-Z4 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI81 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2507 | 7 | 14341 | 14 | 16416 | 4105 | 6 | EL6021_M11 |  | BITVAL
SZI81012W | Pandora - 264.006.SDJ1012/Salle Operation 06-Z4 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2508 | 15 | 14344 | 14 | 16416 | 4111 | 6 | EL6021_M11 |  | BITVAL
SZI81012D1 | Pandora - 264.006.SDJ1012/Salle Operation 06-Z4 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2508 | 13 | 14344 | 10 | 16416 | 4111 | 2 | EL6021_M11 |  | BITVAL
SZI81012D2 | Pandora - 264.006.SDJ1012/Salle Operation 06-Z4 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2508 | 7 | 14343 | 14 | 16416 | 4109 | 6 | EL6021_M11 |  | BITVAL
SZI81013W | Pandora - 264.006.SDJ1013/Salle Operation 06-Z4 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2509 | 15 | 14346 | 14 | 16416 | 4115 | 6 | EL6021_M11 |  | BITVAL
SZI81013D1 | Pandora - 264.006.SDJ1013/Salle Operation 06-Z4 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2509 | 13 | 14346 | 10 | 16416 | 4115 | 2 | EL6021_M11 |  | BITVAL
SZI81013D2 | Pandora - 264.006.SDJ1013/Salle Operation 06-Z4 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2509 | 7 | 14345 | 14 | 16416 | 4113 | 6 | EL6021_M11 |  | BITVAL
SZI81014W | Pandora - 264.006.SDJ1014/Salle Operation 06-Z4 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2510 | 15 | 14348 | 14 | 16416 | 4119 | 6 | EL6021_M11 |  | BITVAL
SZI81014D1 | Pandora - 264.006.SDJ1014/Salle Operation 06-Z4 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2510 | 13 | 14348 | 10 | 16416 | 4119 | 2 | EL6021_M11 |  | BITVAL
SZI81014D2 | Pandora - 264.006.SDJ1014/Salle Operation 06-Z4 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2510 | 7 | 14347 | 14 | 16416 | 4117 | 6 | EL6021_M11 |  | BITVAL
SZI81005W | Pandora - 264.007.SDJ1005/Salle DAS et CDC 07 - Z5 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2511 | 15 | 14350 | 14 | 16416 | 4123 | 6 | EL6021_M11 |  | BITVAL
SZI81005D1 | Pandora - 264.007.SDJ1005/Salle DAS et CDC 07 - Z5 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2511 | 13 | 14350 | 10 | 16416 | 4123 | 2 | EL6021_M11 |  | BITVAL
SZI81005D2 | Pandora - 264.007.SDJ1005/Salle DAS et CDC 07 - Z5 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2511 | 7 | 14349 | 14 | 16416 | 4121 | 6 | EL6021_M11 |  | BITVAL
SZI81007W | Pandora - 264.007.SDJ1007/Salle DAS et CDC 07 - Z5 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2512 | 15 | 14352 | 14 | 16416 | 4127 | 6 | EL6021_M11 |  | BITVAL
SZI81007D1 | Pandora - 264.007.SDJ1007/Salle DAS et CDC 07 - Z5 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2512 | 13 | 14352 | 10 | 16416 | 4127 | 2 | EL6021_M11 |  | BITVAL
SZI81007D2 | Pandora - 264.007.SDJ1007/Salle DAS et CDC 07 - Z5 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2512 | 7 | 14351 | 14 | 16416 | 4125 | 6 | EL6021_M11 |  | BITVAL
SZI81023W | Pandora - 264.008.SDJ1023/Salle Autorites 08 - Z6 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2513 | 15 | 14354 | 14 | 16416 | 4131 | 6 | EL6021_M11 |  | BITVAL
SZI81023D1 | Pandora - 264.008.SDJ1023/Salle Autorites 08 - Z6 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2513 | 13 | 14354 | 10 | 16416 | 4131 | 2 | EL6021_M11 |  | BITVAL
SZI81023D2 | Pandora - 264.008.SDJ1023/Salle Autorites 08 - Z6 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2513 | 7 | 14353 | 14 | 16416 | 4129 | 6 | EL6021_M11 |  | BITVAL
SZI81001W | Pandora - 264.009.SDJ1001/LOC CFS Banc de Controle 09 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2514 | 15 | 14356 | 14 | 16416 | 4135 | 6 | EL6021_M11 |  | BITVAL
SZI81001D1 | Pandora - 264.009.SDJ1001/LOC CFS Banc de Controle 09 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2514 | 13 | 14356 | 10 | 16416 | 4135 | 2 | EL6021_M11 |  | BITVAL
SZI81001D2 | Pandora - 264.009.SDJ1001/LOC CFS Banc de Controle 09 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2514 | 7 | 14355 | 14 | 16416 | 4133 | 6 | EL6021_M11 |  | BITVAL
SZI81004W | Pandora - 264.010.SDJ1004/LOC TELECOM/CFS 10 - Z8 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2515 | 15 | 14358 | 14 | 16416 | 4139 | 6 | EL6021_M11 |  | BITVAL
SZI81004D1 | Pandora - 264.010.SDJ1004/LOC TELECOM/CFS 10 - Z8 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2515 | 13 | 14358 | 10 | 16416 | 4139 | 2 | EL6021_M11 |  | BITVAL
SZI81004D2 | Pandora - 264.010.SDJ1004/LOC TELECOM/CFS 10 - Z8 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI82 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2515 | 7 | 14357 | 14 | 16416 | 4137 | 6 | EL6021_M11 |  | BITVAL
SZI81033W | Pandora - 264.011.SDJ1033/LOC Energie 12 - Z9 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2516 | 15 | 14360 | 14 | 16416 | 4143 | 6 | EL6021_M11 |  | BITVAL
SZI81033D1 | Pandora - 264.011.SDJ1033/LOC Energie 12 - Z9 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2516 | 13 | 14360 | 10 | 16416 | 4143 | 2 | EL6021_M11 |  | BITVAL
SZI81033D2 | Pandora - 264.011.SDJ1033/LOC Energie 12 - Z9 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2516 | 7 | 14359 | 14 | 16416 | 4141 | 6 | EL6021_M11 |  | BITVAL
SZI81031W | Pandora - 264.012.SDJ1031/LOC ONDULEUR 12 - Z10 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2517 | 15 | 14362 | 14 | 16416 | 4147 | 6 | EL6021_M11 |  | BITVAL
SZI81031D1 | Pandora - 264.012.SDJ1031/LOC ONDULEUR 12 - Z10 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2517 | 13 | 14362 | 10 | 16416 | 4147 | 2 | EL6021_M11 |  | BITVAL
SZI81031D2 | Pandora - 264.012.SDJ1031/LOC ONDULEUR 12 - Z10 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2517 | 7 | 14361 | 14 | 16416 | 4145 | 6 | EL6021_M11 |  | BITVAL
SZI81029W | Pandora - 264.013.SDJ1029/LOC Batterie 13 - Z11 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2518 | 15 | 14364 | 14 | 16416 | 4151 | 6 | EL6021_M11 |  | BITVAL
SZI81029D1 | Pandora - 264.013.SDJ1029/LOC Batterie 13 - Z11 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2518 | 13 | 14364 | 10 | 16416 | 4151 | 2 | EL6021_M11 |  | BITVAL
SZI81029D2 | Pandora - 264.013.SDJ1029/LOC Batterie 13 - Z11 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2518 | 7 | 14363 | 14 | 16416 | 4149 | 6 | EL6021_M11 |  | BITVAL
SZI81026W | Pandora - 264.014.SDJ1026/LOC ONDULEUR 14 - Z12 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2519 | 15 | 14366 | 14 | 16416 | 4155 | 6 | EL6021_M11 |  | BITVAL
SZI81026D1 | Pandora - 264.014.SDJ1026/LOC ONDULEUR 14 - Z12 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2519 | 13 | 14366 | 10 | 16416 | 4155 | 2 | EL6021_M11 |  | BITVAL
SZI81026D2 | Pandora - 264.014.SDJ1026/LOC ONDULEUR 14 - Z12 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2519 | 7 | 14365 | 14 | 16416 | 4153 | 6 | EL6021_M11 |  | BITVAL
SZI81028W | Pandora - 264.015.SDJ1028/LOC Batterie 15 - Z13 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2520 | 15 | 14368 | 14 | 16416 | 4159 | 6 | EL6021_M11 |  | BITVAL
SZI6093D | DEFAUT DETECTEUR 1 FLAMME LOCAL 601 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 308 | 0 | 12442 | 0 | 16416 | 306 | 0 | EL6021_M176 |  | BITVAL
SZI6094D | DEFAUT DETECTEUR 2 FLAMME LOCAL 601 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 308 | 1 | 12442 | 2 | 16416 | 306 | 2 | EL6021_M176 |  | BITVAL
SZI6095D | DEFAUT DETECTEUR FLAMME LOCAL 701 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 308 | 2 | 12442 | 4 | 16416 | 306 | 4 | EL6021_M176 |  | BITVAL
SZI81028D1 | Pandora - 264.015.SDJ1028/LOC Batterie 15 - Z13 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2520 | 13 | 14368 | 10 | 16416 | 4159 | 2 | EL6021_M11 |  | BITVAL
SZI81028D2 | Pandora - 264.015.SDJ1028/LOC Batterie 15 - Z13 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2520 | 7 | 14367 | 14 | 16416 | 4157 | 6 | EL6021_M11 |  | BITVAL
SZI81020W | Pandora - 264.019.SDJ1020/Salle CONVIVIA 19-Z14 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2521 | 15 | 14370 | 14 | 16416 | 4163 | 6 | EL6021_M11 |  | BITVAL
SZI81020D1 | Pandora - 264.019.SDJ1020/Salle CONVIVIA 19-Z14 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2521 | 13 | 14370 | 10 | 16416 | 4163 | 2 | EL6021_M11 |  | BITVAL
SZI81020D2 | Pandora - 264.019.SDJ1020/Salle CONVIVIA 19-Z14 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2521 | 7 | 14369 | 14 | 16416 | 4161 | 6 | EL6021_M11 |  | BITVAL
SZI81018W | Pandora - 264.001.SDM1018/Salle Meteo 01 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2522 | 15 | 14372 | 14 | 16416 | 4167 | 6 | EL6021_M11 |  | BITVAL
SZI81018D1 | Pandora - 264.001.SDM1018/Salle Meteo 01 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2522 | 13 | 14372 | 10 | 16416 | 4167 | 2 | EL6021_M11 |  | BITVAL
SZI81018D2 | Pandora - 264.001.SDM1018/Salle Meteo 01 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2522 | 7 | 14371 | 14 | 16416 | 4165 | 6 | EL6021_M11 |  | BITVAL
SZI81017W | Pandora - 264.003.SDM1017/Accueil 03 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2523 | 15 | 14374 | 14 | 16416 | 4171 | 6 | EL6021_M11 |  | BITVAL
SZI81017D1 | Pandora - 264.003.SDM1017/Accueil 03 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2523 | 13 | 14374 | 10 | 16416 | 4171 | 2 | EL6021_M11 |  | BITVAL
SZI81017D2 | Pandora - 264.003.SDM1017/Accueil 03 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2523 | 7 | 14373 | 14 | 16416 | 4169 | 6 | EL6021_M11 |  | BITVAL
SZI81006W | Pandora - 264.007.SDM1006/SAS DAS et CDC 07 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2524 | 15 | 14376 | 14 | 16416 | 4175 | 6 | EL6021_M11 |  | BITVAL
SZI81006D1 | Pandora - 264.007.SDM1006/SAS DAS et CDC 07 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2524 | 13 | 14376 | 10 | 16416 | 4175 | 2 | EL6021_M11 |  | BITVAL
SZI81006D2 | Pandora - 264.007.SDM1006/SAS DAS et CDC 07 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2524 | 7 | 14375 | 14 | 16416 | 4173 | 6 | EL6021_M11 |  | BITVAL
SZI81024W | Pandora - 264.008.SDM1024/Salle Autorites 08 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2525 | 15 | 14378 | 14 | 16416 | 4179 | 6 | EL6021_M11 |  | BITVAL
SZI81024D1 | Pandora - 264.008.SDM1024/Salle Autorites 08 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2525 | 13 | 14378 | 10 | 16416 | 4179 | 2 | EL6021_M11 |  | BITVAL
SZI81024D2 | Pandora - 264.008.SDM1024/Salle Autorites 08 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2525 | 7 | 14377 | 14 | 16416 | 4177 | 6 | EL6021_M11 |  | BITVAL
SZI81002W | Pandora - 264.009.SDM1002/LOC CFS Banc de Controle 09 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2526 | 15 | 14380 | 14 | 16416 | 4183 | 6 | EL6021_M11 |  | BITVAL
SZI81002D1 | Pandora - 264.009.SDM1002/LOC CFS Banc de Controle 09 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2526 | 13 | 14380 | 10 | 16416 | 4183 | 2 | EL6021_M11 |  | BITVAL
SZI81002D2 | Pandora - 264.009.SDM1002/LOC CFS Banc de Controle 09 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2526 | 7 | 14379 | 14 | 16416 | 4181 | 6 | EL6021_M11 |  | BITVAL
SZI81003W | Pandora - 264.010.SDM1003/LOC TELECOM/CFS 10 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2527 | 15 | 14382 | 14 | 16416 | 4187 | 6 | EL6021_M11 |  | BITVAL
SZI81003D1 | Pandora - 264.010.SDM1003/LOC TELECOM/CFS 10 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2527 | 13 | 14382 | 10 | 16416 | 4187 | 2 | EL6021_M11 |  | BITVAL
SZI81003D2 | Pandora - 264.010.SDM1003/LOC TELECOM/CFS 10 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2527 | 7 | 14381 | 14 | 16416 | 4185 | 6 | EL6021_M11 |  | BITVAL
SZI81034W | Pandora - 264.011.SDM1034/LOC Energie 11 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2528 | 15 | 14384 | 14 | 16416 | 4191 | 6 | EL6021_M11 |  | BITVAL
SZI81034D1 | Pandora - 264.011.SDM1034/LOC Energie 11 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2528 | 13 | 14384 | 10 | 16416 | 4191 | 2 | EL6021_M11 |  | BITVAL
SZI81034D2 | Pandora - 264.011.SDM1034/LOC Energie 11 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2528 | 7 | 14383 | 14 | 16416 | 4189 | 6 | EL6021_M11 |  | BITVAL
SZI81032W | Pandora - 264.012.SDM1032/LOC ONDULEUR 12 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2529 | 15 | 14386 | 14 | 16416 | 4195 | 6 | EL6021_M11 |  | BITVAL
SZI81032D1 | Pandora - 264.012.SDM1032/LOC ONDULEUR 12 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2529 | 13 | 14386 | 10 | 16416 | 4195 | 2 | EL6021_M11 |  | BITVAL
SZI81032D2 | Pandora - 264.012.SDM1032/LOC ONDULEUR 12 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI84 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2529 | 7 | 14385 | 14 | 16416 | 4193 | 6 | EL6021_M11 |  | BITVAL
SZI81030W | Pandora - 264.013.SDM1030/LOC Batterie 13 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2530 | 15 | 14388 | 14 | 16416 | 4199 | 6 | EL6021_M11 |  | BITVAL
SZI81030D1 | Pandora - 264.013.SDM1030/LOC Batterie 13 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2530 | 13 | 14388 | 10 | 16416 | 4199 | 2 | EL6021_M11 |  | BITVAL
SZI81030D2 | Pandora - 264.013.SDM1030/LOC Batterie 13 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2530 | 7 | 14387 | 14 | 16416 | 4197 | 6 | EL6021_M11 |  | BITVAL
SZI81025W | Pandora - 264.014.SDM1025/LOC ONDULEUR 14 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2531 | 15 | 14390 | 14 | 16416 | 4203 | 6 | EL6021_M11 |  | BITVAL
SZI81025D1 | Pandora - 264.014.SDM1025/LOC ONDULEUR 14 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2531 | 13 | 14390 | 10 | 16416 | 4203 | 2 | EL6021_M11 |  | BITVAL
SZI81025D2 | Pandora - 264.014.SDM1025/LOC ONDULEUR 14 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2531 | 7 | 14389 | 14 | 16416 | 4201 | 6 | EL6021_M11 |  | BITVAL
SZI81027W | Pandora - 264.015.SDM1027/LOC LOC Batterie 15 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2532 | 15 | 14392 | 14 | 16416 | 4207 | 6 | EL6021_M11 |  | BITVAL
SZI81027D1 | Pandora - 264.015.SDM1027/LOC LOC Batterie 15 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2532 | 13 | 14392 | 10 | 16416 | 4207 | 2 | EL6021_M11 |  | BITVAL
SZI81027D2 | Pandora - 264.015.SDM1027/LOC LOC Batterie 15 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI85 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2532 | 7 | 14391 | 14 | 16416 | 4205 | 6 | EL6021_M11 |  | BITVAL
SZI81008W | Pandora - 264.020.SDJ1008/Salle de Crise 20 - Z15 Alarme Feu | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2533 | 15 | 14394 | 14 | 16416 | 4211 | 6 | EL6021_M11 |  | BITVAL
SZI81008D1 | Pandora - 264.020.SDJ1008/Salle de Crise 20 - Z15 Dérangement | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2533 | 13 | 14394 | 10 | 16416 | 4211 | 2 | EL6021_M11 |  | BITVAL
SZI81008D2 | Pandora - 264.020.SDJ1008/Salle de Crise 20 - Z15 Hors service | AL | N | RES | 3 | S | [12 empty] | S | [13 empty] | MTCP |  |  | DI83 | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 2533 | 7 | 14393 | 14 | 16416 | 4209 | 6 | EL6021_M11 |  | BITVAL
ZJG80237 | Pandora - NK8237 Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT |  |  | PANDORA Etat Centrale DI | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  |  |  | 12315 | 0 | 16416 | 52 | 0 |  |  | BITVAL
ZJG82020 | Pandora - FC2020 Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT |  |  | PANDORA Etat Centrale DI | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  |  |  | 12315 | 2 | 16416 | 52 | 2 |  |  | BITVAL
ZZZ8670M1 | VMC PANDORA API Front-End etat du module EL6070_M1 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13289 | NA | 16416 | 2000 | NA | EL6070_M1 |  | UINT
ZZZ8118M2 | VMC PANDORA API Front-End etat du module EL1018_M2 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13291 | NA | 16416 | 2004 | NA | EL1018_M2 |  | UINT
ZZZ8118M3 | VMC PANDORA API Front-End etat du module EL1018_M3 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13292 | NA | 16416 | 2006 | NA | EL1018_M3 |  | UINT
ZZZ8118M4 | VMC PANDORA API Front-End etat du module EL1018_M4 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13293 | NA | 16416 | 2008 | NA | EL1018_M4 |  | UINT
ZZZ8118M5 | VMC PANDORA API Front-End etat du module EL1018_M5 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13294 | NA | 16416 | 2010 | NA | EL1018_M5 |  | UINT
ZZZ8118M6 | VMC PANDORA API Front-End etat du module EL1018_M6 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13295 | NA | 16416 | 2012 | NA | EL1018_M6 |  | UINT
ZZZ8941M7 | VMC PANDORA API Front-End etat du module EL9410_M7 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13301 | NA | 16416 | 2024 | NA | EL9410_M7 |  | UINT
ZZZ8314M8 | VMC PANDORA API Front-End etat du module EL3144_M8 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13303 | NA | 16416 | 2028 | NA | EL3144_M8 |  | UINT
ZZZ8314M9 | VMC PANDORA API Front-End etat du module EL3144_M9 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13304 | NA | 16416 | 2030 | NA | EL3144_M9 |  | UINT
ZZZ8601M10 | VMC PANDORA API Front-End etat du module EL6001_M10 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13309 | NA | 16416 | 2040 | NA | EL6001_M10 |  | UINT
ZZZ8621M11 | VMC PANDORA API Front-End etat du module EL6021_M11 | AL | N | INT | 0 | Z | [9 empty] | x<>'OP' |  |  | Z | [13 empty] | POL |  |  | VMC06 Etat du Pandora |  | PANDORA | 11 |  |  |  |  | 13307 | NA | 16416 | 2036 | NA | EL6021_M11 |  | UINT
ZJP8001DMA | VMC FE PANDORA PLC MASTER ALARM | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ8670M1; ZZZ8118M2; ZZZ8118M3; ZZZ8118M4; ZZZ8118M5; ZZZ8118M6; ZZZ8941M7; ZZZ8314M8; ZZZ8314M9; ZZZ8601M10; ZZZ8621M11 | Y |  |  |  | VMC06 Etat du Pandora |  | PANDORA | 11
ZJE6103P1 | ETAT INTERFACE EAP1 | AL | N | INT | 0 | Z |  | R | [7 empty] | x==0 |  |  | Z | [13 empty] | NOT | 500 |  | VMC01 | VMC (Z) | NEW | 0 |  |  |  |  | 12313 | 0 | 16416 | 48 | 0 |  |  | BIT
ZJE6103P2 | ETAT INTERFACE EAP2 | AL | N | INT | 0 | Z |  | R | [7 empty] | x==0 |  |  | Z | [13 empty] | NOT | 500 |  | VMC01 | VMC (Z) | NEW | 0 |  |  |  |  | 12313 | 2 | 16416 | 48 | 2 |  |  | BIT
ZJA6103 | ETAT INHIBITION COMMANDE AUTORISE/INHIBEE | AL | N | INT | 0 | Z |  | R | [7 empty] | x==1 |  |  | Z | [13 empty] | NOT | 500 |  | VMC01 | VMC (Z) | NEW | 0 |  |  |  |  | 12314 | 0 | 16416 | 50 | 0 |  |  | BIT
ZJT6103 | ETAT COMMANDE RESET ON/OFF | AL | N | INT | 0 | Z |  | R | [10 empty] | Z | [13 empty] | NOT | 500 |  | VMC01 | VMC (Z) | NEW | 0 |  |  |  |  | 12313 | 8 | 16416 | 49 | 0 |  |  | BIT
WZC6000D | SYNTHESE DEFAUT API OPTIQUE VEGA | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 90 | 0 | 12369 | 0 | 16416 | 160 | 0 | EL6021_M176 |  | BITVAL
WBE6001AU | DEFAUT DISJONCTION SHELTER NORD VEGA | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 90 | 8 | 12370 | 0 | 16416 | 162 | 0 | EL6021_M176 |  | BITVAL
WBE6002AU | DEFAUT DISJONCTION SHELTER EST VEGA | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 90 | 9 | 12370 | 2 | 16416 | 162 | 2 | EL6021_M176 |  | BITVAL
WBE6003AU | DEFAUT DISJONCTION SHELTER OUEST | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 90 | 10 | 12370 | 4 | 16416 | 162 | 4 | EL6021_M176 |  | BITVAL
WCO6001N | DEFAUT TEMPS CN1 ATT SHELTER NORD | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 91 | 2 | 12371 | 4 | 16416 | 164 | 4 | EL6021_M176 |  | BITVAL
WCO6002N | DEFAUT TEMPS CN2 ATT SHELTER EST | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 91 | 6 | 12371 | 12 | 16416 | 165 | 4 | EL6021_M176 |  | BITVAL
WCO6003N | DEFAUT TEMPS CN3 POE SHELTER EST | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 91 | 8 | 12372 | 0 | 16416 | 166 | 0 | EL6021_M176 |  | BITVAL
WCO6004N | DEFAUT TEMPS CAMERA CN4 ATT SHELTER OUEST | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 91 | 10 | 12372 | 4 | 16416 | 166 | 4 | EL6021_M176 |  | BITVAL
WCO6005N | DEFAUT TEMPS CAMERA CN5 POE SHELTER OUEST | AL | N | RES | 1 | O | [12 empty] | O | [13 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 91 | 12 | 12372 | 8 | 16416 | 167 | 0 | EL6021_M176 |  | BITVAL
WZG6000 | OV PLC CPU Error | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 0 | 12373 | 0 | 16416 | 168 | 0 | EL6021_M176 |  | BITVAL
WZS6002 | Serial R0 Module 2 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 1 | 12373 | 2 | 16416 | 168 | 2 | EL6021_M176 |  | BITVAL
WZX6020 | Serial R0 Module 2 Channel 0 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 2 | 12373 | 4 | 16416 | 168 | 4 | EL6021_M176 |  | BITVAL
WZX6021 | Serial R0 Module 2 Channel 1Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 3 | 12373 | 6 | 16416 | 168 | 6 | EL6021_M176 |  | BITVAL
WZS6003 | Serial R0 Module 3 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 4 | 12373 | 8 | 16416 | 169 | 0 | EL6021_M176 |  | BITVAL
WZX6030 | Serial R0 Module 3 Channel 0 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 5 | 12373 | 10 | 16416 | 169 | 2 | EL6021_M176 |  | BITVAL
WZX6031 | Serial R0 Module 3 Channel 1 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 6 | 12373 | 12 | 16416 | 169 | 4 | EL6021_M176 |  | BITVAL
WZM6004 | Module R0 slot 4 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 7 | 12373 | 14 | 16416 | 169 | 6 | EL6021_M176 |  | BITVAL
WZM6005 | Module R0 slot 5 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 8 | 12374 | 0 | 16416 | 170 | 0 | EL6021_M176 |  | BITVAL
WZM6006 | Module R0 slot 6 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 9 | 12374 | 2 | 16416 | 170 | 2 | EL6021_M176 |  | BITVAL
WZM6007 | Module R0 slot 7 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 10 | 12374 | 4 | 16416 | 170 | 4 | EL6021_M176 |  | BITVAL
WZM6010 | Module R1 slot 0 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 11 | 12374 | 6 | 16416 | 170 | 6 | EL6021_M176 |  | BITVAL
WZM6011 | Module R1 slot 1 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 12 | 12374 | 8 | 16416 | 171 | 0 | EL6021_M176 |  | BITVAL
WZM6012 | Module R1 slot 2 Error | AL | N | RES | 1 | O;A | [12 empty] | O;A | [13 empty] | NOT | 1000 |  | W60 | Optique et Video VEGA (W) | CCS | 2 |  |  | 92 | 13 | 12374 | 10 | 16416 | 171 | 2 | EL6021_M176 |  | BITVAL
SZP6003 | READ Fx DETG1 Failure | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 299 | 0 | 12426 | 0 | 16416 | 274 | 0 | EL6021_M176 |  | BITVAL
SZP6005 | READ Fx DETG3 Failure | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 299 | 1 | 12426 | 2 | 16416 | 274 | 2 | EL6021_M176 |  | BITVAL
SZP6006 | READ Fx DETG4 Failure | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 299 | 2 | 12426 | 4 | 16416 | 274 | 4 | EL6021_M176 |  | BITVAL
SCG6012D | DEFAUT RELAIS RESEAU DETG MR1 SBE-1601-01 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 0 | 12428 | 0 | 16416 | 278 | 0 | EL6021_M176 |  | BITVAL
SCG6014D | DEFAUT RELAIS RESEAU DETG MR2 SBE-1601-01 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 1 | 12428 | 2 | 16416 | 278 | 2 | EL6021_M176 |  | BITVAL
SCG6015D | DEFAUT RELAIS RESEAU DETG MR3 SBE-1601-01 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 2 | 12428 | 4 | 16416 | 278 | 4 | EL6021_M176 |  | BITVAL
SCG6016D | DEFAUT RELAIS RESEAU DETG MR4 SMA-1602-01 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 3 | 12428 | 6 | 16416 | 278 | 6 | EL6021_M176 |  | BITVAL
SCG6010D | DEFAUT SYSTEME COMMUNICATION DETG | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 4 | 12428 | 8 | 16416 | 279 | 0 | EL6021_M176 |  | BITVAL
SCG6013D | DEFAUT SAFEBOX DETG | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6006 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 5 | 12428 | 10 | 16416 | 279 | 2 | EL6021_M176 |  | BITVAL
SCG6017D | DEFAUT RELAIS RESEAU DETG MR5 MECH LOCAL 501 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 6 | 12428 | 12 | 16416 | 279 | 4 | EL6021_M176 |  | BITVAL
SCG6018D | DEFAUT RELAIS RESEAU DETG MR6 MECH LOCAL 501 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 7 | 12428 | 14 | 16416 | 279 | 6 | EL6021_M176 |  | BITVAL
SCG6019D | DEFAUT RELAIS RESEAU DETG MR7 MECH LOCAL 501 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 8 | 12429 | 0 | 16416 | 280 | 0 | EL6021_M176 |  | BITVAL
SCG6020D | DEFAUT RELAIS RESEAU DETG MR8 MECH LOCAL 501 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6005 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 300 | 9 | 12429 | 2 | 16416 | 280 | 2 | EL6021_M176 |  | BITVAL
SZI6093W | ALARME FEU DETECTEUR 1 FLAMME LOCAL 601 | AL | N | RES | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 | SZP6003 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 300 | 10 | 12429 | 4 | 16416 | 280 | 4 | EL6021_M176 |  | BITVAL
SZI6094W | ALARME FEU DETECTEUR 2 FLAMME LOCAL 601 | AL | N | RES | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 | SZP6003 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 300 | 11 | 12429 | 6 | 16416 | 280 | 6 | EL6021_M176 |  | BITVAL
SZI6095W | ALARME FEU DETECTEUR FLAMME LOCAL 701 | AL | N | RES | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 | SZP6003 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 300 | 12 | 12429 | 8 | 16416 | 281 | 0 | EL6021_M176 |  | BITVAL
SDO6001D | DEFAUT DETECT.O2 LOCAL 126 CTRL CLIM | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 0 | 12430 | 0 | 16416 | 282 | 0 | EL6021_M176 |  | BITVAL
SDO6001W | ALARME O2 LOCAL 126 CTRL CLIM | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 1 | 12430 | 2 | 16416 | 282 | 2 | EL6021_M176 |  | BITVAL
SDO6002D | DEFAUT DETECT.O2 LOCAL 116 HT | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 2 | 12430 | 4 | 16416 | 282 | 4 | EL6021_M176 |  | BITVAL
SDO6002W | ALARME O2 LOCAL 116 HT | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 3 | 12430 | 6 | 16416 | 282 | 6 | EL6021_M176 |  | BITVAL
SDO6003D | DEFAUT DETECT.O2 LOCAL 115 TGBT | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 4 | 12430 | 8 | 16416 | 283 | 0 | EL6021_M176 |  | BITVAL
SDO6003W | ALARME O2 LOCAL 115 TGBT | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 5 | 12430 | 10 | 16416 | 283 | 2 | EL6021_M176 |  | BITVAL
SDO6004D | DEFAUT DETECT.O2 LOCAL 111 BAT. 2 CAT.III | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 6 | 12430 | 12 | 16416 | 283 | 4 | EL6021_M176 |  | BITVAL
SDO6004W | ALARME O2 LOCAL 111 BAT. 2 CAT.III | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 7 | 12430 | 14 | 16416 | 283 | 6 | EL6021_M176 |  | BITVAL
SDO6005D | DEFAUT DETECT.O2 LOCAL 112 BAT. 1 CAT.III | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 8 | 12431 | 0 | 16416 | 284 | 0 | EL6021_M176 |  | BITVAL
SDO6005W | ALARME O2 LOCAL 112 BAT. 1 CAT.III | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 9 | 12431 | 2 | 16416 | 284 | 2 | EL6021_M176 |  | BITVAL
SDO6006D | DEFAUT DETECT.O2 LOCAL 113 CAT.III | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 10 | 12431 | 4 | 16416 | 284 | 4 | EL6021_M176 |  | BITVAL
SDO6006W | ALARME O2 LOCAL 113 CAT.III | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 11 | 12431 | 6 | 16416 | 284 | 6 | EL6021_M176 |  | BITVAL
SDO6007D | DEFAUT DETECT.O2 LOCAL 108 FLUIDE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 12 | 12431 | 8 | 16416 | 285 | 0 | EL6021_M176 |  | BITVAL
SDO6007W | ALARME O2 LOCAL 108 FLUIDE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 13 | 12431 | 10 | 16416 | 285 | 2 | EL6021_M176 |  | BITVAL
SDO6008D | DEFAUT DETECT.O2 LOCAL 101 BAIES CU | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 14 | 12431 | 12 | 16416 | 285 | 4 | EL6021_M176 |  | BITVAL
SDO6008W | ALARME O2 LOCAL 101 BAIES CU | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 301 | 15 | 12431 | 14 | 16416 | 285 | 6 | EL6021_M176 |  | BITVAL
SDO6009D | DEFAUT DETECT.O2 LOCAL 100 CONNEC. PORTIQUE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 0 | 12432 | 0 | 16416 | 286 | 0 | EL6021_M176 |  | BITVAL
SDO6009W | ALARME O2 LOCAL 100 CONNEC. PORTIQUE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG62 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 1 | 12432 | 2 | 16416 | 286 | 2 | EL6021_M176 |  | BITVAL
SDO6010D | DEFAUT DETECT.O2 LOCAL 103 BCV/CCS | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61;DG62;DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 2 | 12432 | 4 | 16416 | 286 | 4 | EL6021_M176 |  | BITVAL
SDO6010W | ALARME O2 LOCAL 103 BCV/CCS | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61;DG62;DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 3 | 12432 | 6 | 16416 | 286 | 6 | EL6021_M176 |  | BITVAL
SDO6011D | DEFAUT DETECT.O2 MAT NIV. 24.000 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 4 | 12432 | 8 | 16416 | 287 | 0 | EL6021_M176 |  | BITVAL
SDO6011W | ALARME O2 LOCAL MAT NIV. 24.000 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 5 | 12432 | 10 | 16416 | 287 | 2 | EL6021_M176 |  | BITVAL
SDO6012D | DEFAUT DETECT.O2 MAT NIV. 18.400 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 6 | 12432 | 12 | 16416 | 287 | 4 | EL6021_M176 |  | BITVAL
SDO6012W | ALARME O2 LOCAL MAT NIV. 18.400 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 7 | 12432 | 14 | 16416 | 287 | 6 | EL6021_M176 |  | BITVAL
SDO6013D | DEFAUT DETECT.O2 PIED DE MAT | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 8 | 12433 | 0 | 16416 | 288 | 0 | EL6021_M176 |  | BITVAL
SDO6013W | ALARME O2 PIED DE MAT | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 9 | 12433 | 2 | 16416 | 288 | 2 | EL6021_M176 |  | BITVAL
SDO6014D | DEFAUT DETECT.O2 LOCAL 007 CAT.III CU | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 10 | 12433 | 4 | 16416 | 288 | 4 | EL6021_M176 |  | BITVAL
SDO6014W | ALARME O2 LOCAL 007 CAT.III CU | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 11 | 12433 | 6 | 16416 | 288 | 6 | EL6021_M176 |  | BITVAL
SDO6015D | DEFAUT DETECT.O2 LOCAL 009 BATTERIES CUB | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 12 | 12433 | 8 | 16416 | 289 | 0 | EL6021_M176 |  | BITVAL
SDO6015W | ALARME O2 LOCAL 009 BATTERIES CUB | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 13 | 12433 | 10 | 16416 | 289 | 2 | EL6021_M176 |  | BITVAL
SDO6016D | DEFAUT DETECT.O2 LOCAL 008 BATTERIES CUH | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 14 | 12433 | 12 | 16416 | 289 | 4 | EL6021_M176 |  | BITVAL
SDO6016W | ALARME O2 LOCAL 008 BATTERIES CUH | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 302 | 15 | 12433 | 14 | 16416 | 289 | 6 | EL6021_M176 |  | BITVAL
SDO6017D | DEFAUT DETECT.O2 LOCAL 013 PROCESS VES | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 0 | 12434 | 0 | 16416 | 290 | 0 | EL6021_M176 |  | BITVAL
SDO6017W | ALARME O2 LOCAL 013 PROCESS VES | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 1 | 12434 | 2 | 16416 | 290 | 2 | EL6021_M176 |  | BITVAL
SDO6018D | DEFAUT DETECT.O2 LOCAL 002 LIBRE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 2 | 12434 | 4 | 16416 | 290 | 4 | EL6021_M176 |  | BITVAL
SDO6018W | ALARME O2 LOCAL 002 LIBRE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 3 | 12434 | 6 | 16416 | 290 | 6 | EL6021_M176 |  | BITVAL
SDO6019D | DEFAUT DETECT.O2 LOCAL 003 GALERIE TECHNIQUE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 4 | 12434 | 8 | 16416 | 291 | 0 | EL6021_M176 |  | BITVAL
SDO6019W | ALARME O2 LOCAL 003 GALERIE TECHNIQUE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 5 | 12434 | 10 | 16416 | 291 | 2 | EL6021_M176 |  | BITVAL
SDO6020D | DEFAUT DETECT.O2 LOCAL 004 COMMUNICATION | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 6 | 12434 | 12 | 16416 | 291 | 4 | EL6021_M176 |  | BITVAL
SDO6020W | ALARME O2 LOCAL 004 COMMUNICATION | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 7 | 12434 | 14 | 16416 | 291 | 6 | EL6021_M176 |  | BITVAL
SDO6021D | DEFAUT DETECT.O2 NIV 18.400 LOCAL ENERGIE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 8 | 12435 | 0 | 16416 | 292 | 0 | EL6021_M176 |  | BITVAL
SDO6021W | ALARME O2 NIV 18.400 LOCAL ENERGIE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 9 | 12435 | 2 | 16416 | 292 | 2 | EL6021_M176 |  | BITVAL
SDO6022D | DEFAUT DETECT.O2 NIV 21.200 SAUVEGARDE CFS | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 10 | 12435 | 4 | 16416 | 292 | 4 | EL6021_M176 |  | BITVAL
SDO6022W | ALARME O2 NIV 21.200 SAUVEGARDE CFS | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 11 | 12435 | 6 | 16416 | 292 | 6 | EL6021_M176 |  | BITVAL
SDO6023D | DEFAUT DETECT.O2 NIV 29.200 LOCAL BCV/INTF | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 12 | 12435 | 8 | 16416 | 293 | 0 | EL6021_M176 |  | BITVAL
SDO6023W | ALARME O2 NIV 29.200 LOCAL BCV/INTF | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 13 | 12435 | 10 | 16416 | 293 | 2 | EL6021_M176 |  | BITVAL
SDO6024D | DEFAUT DETECT.O2 NIV 29.200 LOCAL DVT | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 14 | 12435 | 12 | 16416 | 293 | 4 | EL6021_M176 |  | BITVAL
SDO6024W | ALARME O2 NIV 29.200 LOCAL DVT | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 303 | 15 | 12435 | 14 | 16416 | 293 | 6 | EL6021_M176 |  | BITVAL
SDO6025D | DEFAUT DETECT.O2 NIV 31.800 LOCAL FLUIDE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 0 | 12436 | 0 | 16416 | 294 | 0 | EL6021_M176 |  | BITVAL
SDO6025W | ALARME O2 NIV 31.800 LOCAL FLUIDE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 1 | 12436 | 2 | 16416 | 294 | 2 | EL6021_M176 |  | BITVAL
SDO6026D | DEFAUT DETECT.O2 NIV 31.800 LOCAL UDMH ATEX | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 2 | 12436 | 4 | 16416 | 294 | 4 | EL6021_M176 |  | BITVAL
SDO6026W | ALARME O2 NIV 31.800 LOCAL UDMH ATEX | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 3 | 12436 | 6 | 16416 | 294 | 6 | EL6021_M176 |  | BITVAL
SDO6027D | DEFAUT DETECT.O2 NIV 34.400 LOCAL FLUIDE | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 4 | 12436 | 8 | 16416 | 295 | 0 | EL6021_M176 |  | BITVAL
SDO6027W | ALARME O2 NIV 34.400 LOCAL FLUIDE | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 5 | 12436 | 10 | 16416 | 295 | 2 | EL6021_M176 |  | BITVAL
SDO6028D | DEFAUT DETECT.O2 NIV 34.400 LOCAL N2O4 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 6 | 12436 | 12 | 16416 | 295 | 4 | EL6021_M176 |  | BITVAL
SDO6028W | ALARME O2 NIV 34.400 LOCAL N2O4 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG63 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 7 | 12436 | 14 | 16416 | 295 | 6 | EL6021_M176 |  | BITVAL
SDO6029D | DEFAUT DETECT.O2 LOCAL 010 ESCALIER | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 8 | 12437 | 0 | 16416 | 296 | 0 | EL6021_M176 |  | BITVAL
SDO6029W | ALARME O2 LOCAL 010 ESCALIER | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61 | Detection Gaz (DG) | CCS | 1 |  |  | 305 | 9 | 12437 | 2 | 16416 | 296 | 2 | EL6021_M176 |  | BITVAL
SDU6032D | DEFAUT DETECT. U SDU-1602-03 CL8-1 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 305 | 14 | 12437 | 12 | 16416 | 297 | 4 | EL6021_M176 |  | BITVAL
SDU6032W | ALARME U SDU-1602-03 CL8-1 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 305 | 15 | 12437 | 14 | 16416 | 297 | 6 | EL6021_M176 |  | BITVAL
SDU6033D | DEFAUT DETECT. U SDU-1602-04 CL8-1 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 0 | 12438 | 0 | 16416 | 298 | 0 | EL6021_M176 |  | BITVAL
SDU6033W | ALARME U SDU-1602-04 CL8-1 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 1 | 12438 | 2 | 16416 | 298 | 2 | EL6021_M176 |  | BITVAL
SDU6036D | DEFAUT DETECT. U SDU-1602-07 CL8-2 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 6 | 12438 | 12 | 16416 | 299 | 4 | EL6021_M176 |  | BITVAL
SDU6036W | ALARME U SDU-1602-07 CL8-2 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 7 | 12438 | 14 | 16416 | 299 | 6 | EL6021_M176 |  | BITVAL
SDU6037D | DEFAUT DETECT. U SDU-1602-08 CL8-2 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 8 | 12439 | 0 | 16416 | 300 | 0 | EL6021_M176 |  | BITVAL
SDU6037W | ALARME U SDU-1602-08 CL8-2 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 9 | 12439 | 2 | 16416 | 300 | 2 | EL6021_M176 |  | BITVAL
SDU6040D | DEFAUT DETECT. U SDU-1602-11 CL8-3 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 14 | 12439 | 12 | 16416 | 301 | 4 | EL6021_M176 |  | BITVAL
SDU6040W | ALARME U SDU-1602-11 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 306 | 15 | 12439 | 14 | 16416 | 301 | 6 | EL6021_M176 |  | BITVAL
SDU6041D | DEFAUT DETECT. U SDU-1602-12 CL8-3 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 0 | 12440 | 0 | 16416 | 302 | 0 | EL6021_M176 |  | BITVAL
SDU6041W | ALARME U SDU-1602-12 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 1 | 12440 | 2 | 16416 | 302 | 2 | EL6021_M176 |  | BITVAL
SDU6044D | DEFAUT DETECT. U SDU-1602-15 CL8-4 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 6 | 12440 | 12 | 16416 | 303 | 4 | EL6021_M176 |  | BITVAL
SDU6044W | ALARME U SDU-1602-15 CL8-4 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 7 | 12440 | 14 | 16416 | 303 | 6 | EL6021_M176 |  | BITVAL
SDU6045D | DEFAUT DETECT. U SDU-1602-16 CL8-4 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 8 | 12441 | 0 | 16416 | 304 | 0 | EL6021_M176 |  | BITVAL
SDU6045W | ALARME U SDU-1602-16 CL8-4 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 9 | 12441 | 2 | 16416 | 304 | 2 | EL6021_M176 |  | BITVAL
SDU6046D | DEFAUT DETECT. U SDU-1602-17 LOCAL 501 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 10 | 12441 | 4 | 16416 | 304 | 4 | EL6021_M176 |  | BITVAL
SDU6046W | ALARME U SDU-1602-17 LOCAL 501 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 11 | 12441 | 6 | 16416 | 304 | 6 | EL6021_M176 |  | BITVAL
SDU6047D | DEFAUT DETECT. U SDU-1602-18 LOCAL 501 | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 12 | 12441 | 8 | 16416 | 305 | 0 | EL6021_M176 |  | BITVAL
SDU6047W | ALARME U SDU-1602-18 LOCAL 501 | AL | N | RES | 1 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 13 | 12441 | 10 | 16416 | 305 | 2 | EL6021_M176 |  | BITVAL
SCG6021D | DEFAUT COMMUNICATION API - UC DETG | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SZP6003 | DG61;DG62;DG63;DG65 | Detection Gaz (DG); Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 307 | 15 | 12441 | 14 | 16416 | 305 | 6 | EL6021_M176 |  | BITVAL
SZP6004 | READ Fx DETG2 Failure | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 321 | 0 | 12462 | 0 | 16416 | 346 | 0 | EL6021_M176 |  | BITVAL
SCK6001DT | CENTRALE DI ZLV DEFAUT TRANSMISSION | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6001 | DI61;DI62;DI63;DI64;DI65;DI70 | Detection Incendie (DI) | NEW | 1 |  |  | 400 | 0 | 12512 | 0 | 16416 | 446 | 0 | EL6021_M176 |  | BITVAL
SCK6001DA | CENTRALE DI ZLV DEFAUT ALIMENTATION | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6001 | DI61;DI62;DI63;DI64;DI65;DI70 | Detection Incendie (DI) | NEW | 1 |  |  | 400 | 1 | 12512 | 2 | 16416 | 446 | 2 | EL6021_M176 |  | BITVAL
SCK6001D | CENTRALE DI ZLV SYNTHESE DEFAUT | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6001 | DI61;DI62;DI63;DI64;DI65;DI70 | Detection Incendie (DI) | NEW | 1 |  |  | 400 | 2 | 12512 | 4 | 16416 | 446 | 4 | EL6021_M176 |  | BITVAL
SZI6000D | CENTRALE DI ZLV DERANGEMENT ZONE | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6001 | DI61;DI62;DI63;DI64;DI65;DI70 | Detection Incendie (DI) | NEW | 1 |  |  | 400 | 3 | 12512 | 6 | 16416 | 446 | 6 | EL6021_M176 |  | BITVAL
SZG6000 | DETG DI PLC CPU Error | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 4 | 12512 | 8 | 16416 | 447 | 0 | EL6021_M176 |  | BITVAL
SZS6002 | Serial Module 2 Error | AL | N | RES | 1 | S;A | [12 empty] | S;A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 5 | 12512 | 10 | 16416 | 447 | 2 | EL6021_M176 |  | BITVAL
SZX6020 | Serial Module 2 Channel 0 Error | AL | N | RES | 1 | S;A | [12 empty] | S;A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 6 | 12512 | 12 | 16416 | 447 | 4 | EL6021_M176 |  | BITVAL
SZX6021 | Serial Module 2 Channel 1 Error | AL | N | RES | 1 | S;A | [12 empty] | S;A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 7 | 12512 | 14 | 16416 | 447 | 6 | EL6021_M176 |  | BITVAL
SZS6003 | Serial Module 3 Error | AL | N | RES | 1 | S;A | [12 empty] | S;A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 8 | 12513 | 0 | 16416 | 448 | 0 | EL6021_M176 |  | BITVAL
SZX6030 | Serial Module 3 Channel 0 Error | AL | N | RES | 1 | S;A | [12 empty] | S;A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 9 | 12513 | 2 | 16416 | 448 | 2 | EL6021_M176 |  | BITVAL
SZX6031 | Serial Module 3 Channel 1 Error | AL | N | RES | 1 | S;A | [12 empty] | S;A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 10 | 12513 | 4 | 16416 | 448 | 4 | EL6021_M176 |  | BITVAL
SZR6001 | READ Fx DI1 Failure | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 11 | 12513 | 6 | 16416 | 448 | 6 | EL6021_M176 |  | BITVAL
SZR6002 | READ Fx DI2 Failure | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | DG60 | Detection Gaz (DG) | NEW | 1 |  |  | 400 | 12 | 12513 | 8 | 16416 | 449 | 0 | EL6021_M176 |  | BITVAL
SZI6001W | ALARME FEU MASSIF ZLV LOCAL 001 PIED DE MAT | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63 | Detection Incendie (DI) | CCS | 1 |  |  | 401 | 0 | 12514 | 0 | 16416 | 450 | 0 | EL6021_M176 |  | BITVAL
SZI6002W | ALARME FEU MASSIF ZLV LOCAL 002 A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63 | Detection Incendie (DI) | CCS | 1 |  |  | 401 | 1 | 12514 | 2 | 16416 | 450 | 2 | EL6021_M176 |  | BITVAL
SZI6003W | ALARME FEU MASSIF ZLV LOCAL 003 GALERIE TECH | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63 | Detection Incendie (DI) | CCS | 1 |  |  | 401 | 2 | 12514 | 4 | 16416 | 450 | 4 | EL6021_M176 |  | BITVAL
SZI6004W | ALARME FEU MASSIF ZLV LOCAL 006 TECHNIQUE | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI72 | Detection Incendie (DI) | CCS | 1 |  |  | 401 | 3 | 12514 | 6 | 16416 | 450 | 6 | EL6021_M176 |  | BITVAL
SZI6005W | ALARME FEU MASSIF ZLV LOCAL 012 MOY SECURITE | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI72 | Detection Incendie (DI) | CCS | 1 |  |  | 401 | 4 | 12514 | 8 | 16416 | 451 | 0 | EL6021_M176 |  | BITVAL
SZI6006W | ALARME FEU MASSIF ZLV LOCAL 004 COM A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 5 | 12514 | 10 | 16416 | 451 | 2 | EL6021_M176 |  | BITVAL
SZI6007W | ALARME FEU MASSIF ZLV LOCAL 004 COM A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 6 | 12514 | 12 | 16416 | 451 | 4 | EL6021_M176 |  | BITVAL
SZI6008W | ALARME FEU MASSIF ZLV LOCAL 007 CATIII CU A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 7 | 12514 | 14 | 16416 | 451 | 6 | EL6021_M176 |  | BITVAL
SZI6009W | ALARME FEU MASSIF ZLV LOCAL 007 CATIII CU A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 8 | 12515 | 0 | 16416 | 452 | 0 | EL6021_M176 |  | BITVAL
SZI6010W | ALARME FEU MASSIF ZLV LOCAL 008 BAT CUH A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 9 | 12515 | 2 | 16416 | 452 | 2 | EL6021_M176 |  | BITVAL
SZI6011W | ALARME FEU MASSIF ZLV LOCAL 008 BAT CUH A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 10 | 12515 | 4 | 16416 | 452 | 4 | EL6021_M176 |  | BITVAL
SZI6012W | ALARME FEU MASSIF ZLV LOCAL 009 BAT CUB A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 11 | 12515 | 6 | 16416 | 452 | 6 | EL6021_M176 |  | BITVAL
SZI6013W | ALARME FEU MASSIF ZLV LOCAL 009 BAT CUB A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 12 | 12515 | 8 | 16416 | 453 | 0 | EL6021_M176 |  | BITVAL
SZI6014W | ALARME FEU MASSIF ZLV LOCAL 013 VES A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 13 | 12515 | 10 | 16416 | 453 | 2 | EL6021_M176 |  | BITVAL
SZI6015W | ALARME FEU MASSIF ZLV LOCAL 013 VES A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 14 | 12515 | 12 | 16416 | 453 | 4 | EL6021_M176 |  | BITVAL
SZI6016W | ALARME FEU MASSIF ZLV LOCAL 013 VES FP1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 401 | 15 | 12515 | 14 | 16416 | 453 | 6 | EL6021_M176 |  | BITVAL
SZI6017W | ALARME FEU MASSIF ZLV LOCAL 013 VES FP2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 402 | 0 | 12516 | 0 | 16416 | 454 | 0 | EL6021_M176 |  | BITVAL
SZI6022W | ALARME FEU MASSIF ZLV LOCAL 100 CONNECTION | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 1 | 12516 | 2 | 16416 | 454 | 2 | EL6021_M176 |  | BITVAL
SZI6023W | ALARME FEU MASSIF ZLV LOCAL 104 N2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 2 | 12516 | 4 | 16416 | 454 | 4 | EL6021_M176 |  | BITVAL
SZI6024W | ALARME FEU MASSIF ZLV LOCAL 105 TECHNIQUE | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 3 | 12516 | 6 | 16416 | 454 | 6 | EL6021_M176 |  | BITVAL
SZI6025W | ALARME FEU MASSIF ZLV LOCAL 106 REPLI | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 4 | 12516 | 8 | 16416 | 455 | 0 | EL6021_M176 |  | BITVAL
SZI6026W | ALARME FEU MASSIF ZLV LOCAL 107 N2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 5 | 12516 | 10 | 16416 | 455 | 2 | EL6021_M176 |  | BITVAL
SZI6027W | ALARME FEU MASSIF ZLV LOCAL 108 FLUIDE | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 6 | 12516 | 12 | 16416 | 455 | 4 | EL6021_M176 |  | BITVAL
SZI6028W | ALARME FEU MASSIF ZLV LOCAL 117 DEGAGEMENT | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 7 | 12516 | 14 | 16416 | 455 | 6 | EL6021_M176 |  | BITVAL
SZI6029W | ALARME FEU MASSIF ZLV LOCAL 118 CLIM | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 8 | 12517 | 0 | 16416 | 456 | 0 | EL6021_M176 |  | BITVAL
SZI6030W | ALARME FEU MASSIF ZLV LOCAL 121 PLOMBERIE | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 9 | 12517 | 2 | 16416 | 456 | 2 | EL6021_M176 |  | BITVAL
SZI6031W | ALARME FEU MASSIF ZLV LOCAL 122 OUTILS MECA | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 10 | 12517 | 4 | 16416 | 456 | 4 | EL6021_M176 |  | BITVAL
SZI6032W | ALARME FEU MASSIF ZLV LOCAL 127 LT CLIM | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 402 | 11 | 12517 | 6 | 16416 | 456 | 6 | EL6021_M176 |  | BITVAL
SZI6038W | ALARME FEU MASSIF ZLV LOCAL 101 BAIES CU A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 402 | 12 | 12517 | 8 | 16416 | 457 | 0 | EL6021_M176 |  | BITVAL
SZI6039W | ALARME FEU MASSIF ZLV LOCAL 101 BAIES CU A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 402 | 13 | 12517 | 10 | 16416 | 457 | 2 | EL6021_M176 |  | BITVAL
SZI6040W | ALARME FEU MASSIF ZLV LOCAL 101 BAIES CU FP1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 402 | 14 | 12517 | 12 | 16416 | 457 | 4 | EL6021_M176 |  | BITVAL
SZI6041W | ALARME FEU MASSIF ZLV LOCAL 101 BAIES CU FP2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 402 | 15 | 12517 | 14 | 16416 | 457 | 6 | EL6021_M176 |  | BITVAL
SZI6042W | ALARME FEU MASSIF ZLV LOCAL 103 BCV CCS A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 0 | 12518 | 0 | 16416 | 458 | 0 | EL6021_M176 |  | BITVAL
SZI6043W | ALARME FEU MASSIF ZLV LOCAL 103 BCV CCS A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 1 | 12518 | 2 | 16416 | 458 | 2 | EL6021_M176 |  | BITVAL
SZI6044W | ALARME FEU MASSIF ZLV LOCAL 103 BCV CCS FP1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 2 | 12518 | 4 | 16416 | 458 | 4 | EL6021_M176 |  | BITVAL
SZI6045W | ALARME FEU MASSIF ZLV LOCAL 103 BCV CCS FP2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 3 | 12518 | 6 | 16416 | 458 | 6 | EL6021_M176 |  | BITVAL
SZI6046W | ALARME FEU MASSIF ZLV LOCAL 111 CAT.III 2 A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 4 | 12518 | 8 | 16416 | 459 | 0 | EL6021_M176 |  | BITVAL
SZI6047W | ALARME FEU MASSIF ZLV LOCAL 111 CAT.III 2 A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 5 | 12518 | 10 | 16416 | 459 | 2 | EL6021_M176 |  | BITVAL
SZI6048W | ALARME FEU MASSIF ZLV LOCAL 112 CAT.III 1 A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 6 | 12518 | 12 | 16416 | 459 | 4 | EL6021_M176 |  | BITVAL
SZI6049W | ALARME FEU MASSIF ZLV LOCAL 112 CAT.III 1 A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 7 | 12518 | 14 | 16416 | 459 | 6 | EL6021_M176 |  | BITVAL
SZI6050W | ALARME FEU MASSIF ZLV LOCAL 113 CAT.III A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 8 | 12519 | 0 | 16416 | 460 | 0 | EL6021_M176 |  | BITVAL
SZI6051W | ALARME FEU MASSIF ZLV LOCAL 113 CAT.III A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 9 | 12519 | 2 | 16416 | 460 | 2 | EL6021_M176 |  | BITVAL
SZI6052W | ALARME FEU MASSIF ZLV LOCAL 115 TGBT A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 10 | 12519 | 4 | 16416 | 460 | 4 | EL6021_M176 |  | BITVAL
SZI6053W | ALARME FEU MASSIF ZLV LOCAL 115 TGBT A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 11 | 12519 | 6 | 16416 | 460 | 6 | EL6021_M176 |  | BITVAL
SZI6054W | ALARME FEU MASSIF ZLV LOCAL 116 HT A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 12 | 12519 | 8 | 16416 | 461 | 0 | EL6021_M176 |  | BITVAL
SZI6055W | ALARME FEU MASSIF ZLV LOCAL 116 HT A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 13 | 12519 | 10 | 16416 | 461 | 2 | EL6021_M176 |  | BITVAL
SZI6056W | ALARME FEU MASSIF ZLV LOCAL 126 SCC CLIM A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 14 | 12519 | 12 | 16416 | 461 | 4 | EL6021_M176 |  | BITVAL
SZI6057W | ALARME FEU MASSIF ZLV LOCAL 126 SCC CLIM A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 403 | 15 | 12519 | 14 | 16416 | 461 | 6 | EL6021_M176 |  | BITVAL
SZI6058W | ALARME FEU MAT ZLV NIV 18400 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 0 | 12520 | 0 | 16416 | 462 | 0 | EL6021_M176 |  | BITVAL
SZI6059W | ALARME FEU MAT ZLV NIV 26600 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 1 | 12520 | 2 | 16416 | 462 | 2 | EL6021_M176 |  | BITVAL
SZI6060W | ALARME FEU MAT ZLV NIV 34400 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 2 | 12520 | 4 | 16416 | 462 | 4 | EL6021_M176 |  | BITVAL
SZI6061W | ALARME FEU MAT ZLV NIV 42200 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 3 | 12520 | 6 | 16416 | 462 | 6 | EL6021_M176 |  | BITVAL
SZI6064W | ALARME FEU PORTIQUE ZLV NIV. 14200 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 4 | 12520 | 8 | 16416 | 463 | 0 | EL6021_M176 |  | BITVAL
SZI6065W | ALARME FEU PORTIQUE ZLV NIV. 18400 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 5 | 12520 | 10 | 16416 | 463 | 2 | EL6021_M176 |  | BITVAL
SZI6066W | ALARME FEU PORTIQUE ZLV LOCAL 101 A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 404 | 6 | 12520 | 12 | 16416 | 463 | 4 | EL6021_M176 |  | BITVAL
SZI6067W | ALARME FEU PORTIQUE ZLV LOCAL 101 A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 404 | 7 | 12520 | 14 | 16416 | 463 | 6 | EL6021_M176 |  | BITVAL
SZI6068W | ALARME FEU PORTIQUE ZLV LOCAL 102 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 8 | 12521 | 0 | 16416 | 464 | 0 | EL6021_M176 |  | BITVAL
SZI6069W | ALARME FEU PORTIQUE ZLV NIV. 21200 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 9 | 12521 | 2 | 16416 | 464 | 2 | EL6021_M176 |  | BITVAL
SZI6070W | ALARME FEU PORTIQUE ZLV LOCAL 201 A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 404 | 10 | 12521 | 4 | 16416 | 464 | 4 | EL6021_M176 |  | BITVAL
SZI6071W | ALARME FEU PORTIQUE ZLV LOCAL 201 A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 404 | 11 | 12521 | 6 | 16416 | 464 | 6 | EL6021_M176 |  | BITVAL
SZI6072W | ALARME FEU PORTIQUE ZLV LOCAL 202 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 12 | 12521 | 8 | 16416 | 465 | 0 | EL6021_M176 |  | BITVAL
SZI6073W | ALARME FEU PORTIQUE ZLV NIV. 24000 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 13 | 12521 | 10 | 16416 | 465 | 2 | EL6021_M176 |  | BITVAL
SZI6074W | ALARME FEU PORTIQUE ZLV LOCAL 301 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 14 | 12521 | 12 | 16416 | 465 | 4 | EL6021_M176 |  | BITVAL
SZI6075W | ALARME FEU PORTIQUE ZLV NIV. 26600 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 404 | 15 | 12521 | 14 | 16416 | 465 | 6 | EL6021_M176 |  | BITVAL
SZI6076W | ALARME FEU PORTIQUE ZLV LOCAL 401 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 0 | 12522 | 0 | 16416 | 466 | 0 | EL6021_M176 |  | BITVAL
SZI6077W | ALARME FEU PORTIQUE ZLV NIV. 29200 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 1 | 12522 | 2 | 16416 | 466 | 2 | EL6021_M176 |  | BITVAL
SZI6078W | ALARME FEU PORTIQUE ZLV LOCAL 501 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 2 | 12522 | 4 | 16416 | 466 | 4 | EL6021_M176 |  | BITVAL
SZI6079W | ALARME FEU PORTIQUE ZLV LOCAL 502 A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 405 | 3 | 12522 | 6 | 16416 | 466 | 6 | EL6021_M176 |  | BITVAL
SZI6080W | ALARME FEU PORTIQUE ZLV LOCAL 502 A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 405 | 4 | 12522 | 8 | 16416 | 467 | 0 | EL6021_M176 |  | BITVAL
SZI6081W | ALARME FEU PORTIQUE ZLV NIV. 31800 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 5 | 12522 | 10 | 16416 | 467 | 2 | EL6021_M176 |  | BITVAL
SZI6082W | ALARME FEU PORTIQUE ZLV NIV. 34400 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 6 | 12522 | 12 | 16416 | 467 | 4 | EL6021_M176 |  | BITVAL
SZI6083W | ALARME FEU PORTIQUE ZLV NIV. 37000 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 7 | 12522 | 14 | 16416 | 467 | 6 | EL6021_M176 |  | BITVAL
SZI6084W | ALARME FEU PORTIQUE ZLV LOCAL 801 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 8 | 12523 | 0 | 16416 | 468 | 0 | EL6021_M176 |  | BITVAL
SZI6085W | ALARME FEU PORTIQUE ZLV NIV. 39600 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 9 | 12523 | 2 | 16416 | 468 | 2 | EL6021_M176 |  | BITVAL
SZI6086W | ALARME FEU PORTIQUE ZLV LOCAL 901 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 10 | 12523 | 4 | 16416 | 468 | 4 | EL6021_M176 |  | BITVAL
SZI6087W | ALARME FEU PORTIQUE ZLV NIV. 42200 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 11 | 12523 | 6 | 16416 | 468 | 6 | EL6021_M176 |  | BITVAL
SZI6088W | ALARME FEU PORTIQUE ZLV NIV. 44800 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 12 | 12523 | 8 | 16416 | 469 | 0 | EL6021_M176 |  | BITVAL
SZI6089W | ALARME FEU PORTIQUE ZLV NIV. 47400 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 13 | 12523 | 10 | 16416 | 469 | 2 | EL6021_M176 |  | BITVAL
SZI6090W | ALARME FEU PORTIQUE ZLV NIV. 50000 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 14 | 12523 | 12 | 16416 | 469 | 4 | EL6021_M176 |  | BITVAL
SZI6091W | ALARME FEU PORTIQUE ZLV NIV. 53800 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 405 | 15 | 12523 | 14 | 16416 | 469 | 6 | EL6021_M176 |  | BITVAL
SZI6092W | ALARME FEU PORTIQUE ZLV GAINE CLIM | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 0 | 12524 | 0 | 16416 | 470 | 0 | EL6021_M176 |  | BITVAL
SZI6098W | ALARME FEU POSTE 1D60 ZLV | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 1 | 12524 | 2 | 16416 | 470 | 2 | EL6021_M176 |  | BITVAL
SZI6114W | ALARME FEU LOCAL 004 FX PL EST 1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 406 | 2 | 12524 | 4 | 16416 | 470 | 4 | EL6021_M176 |  | BITVAL
SZI6100W | ALARME FEU SHELTER NORD ZLV | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 3 | 12524 | 6 | 16416 | 470 | 6 | EL6021_M176 |  | BITVAL
SZI6103W | ALARME FEU SHELTER OUEST ZLV | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 4 | 12524 | 8 | 16416 | 471 | 0 | EL6021_M176 |  | BITVAL
SZI6102W | ALARME FEU SHELTER EST ZLV | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 5 | 12524 | 10 | 16416 | 471 | 2 | EL6021_M176 |  | BITVAL
SZI6096W | ALARME FEU PORTIQUE ZLV LOCAL 601 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 6 | 12524 | 12 | 16416 | 471 | 4 | EL6021_M176 |  | BITVAL
SZI6097W | ALARME FEU PORTIQUE ZLV LOCAL 701 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 7 | 12524 | 14 | 16416 | 471 | 6 | EL6021_M176 |  | BITVAL
SZI6104W | ALARME FEU DETECTEUR FLAMME CARBET N | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 8 | 12525 | 0 | 16416 | 472 | 0 | EL6021_M176 |  | BITVAL
SZI6105W | ALARME FEU DETECTEUR FLAMME CARBET U | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 9 | 12525 | 2 | 16416 | 472 | 2 | EL6021_M176 |  | BITVAL
SZI6106W | ALARME FEU DETECTEUR FLAMME 1 LOCAL 05 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI72 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 10 | 12525 | 4 | 16416 | 472 | 4 | EL6021_M176 |  | BITVAL
SZI6115W | ALARME FEU LOCAL 004 FX PL EST 2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 406 | 11 | 12525 | 6 | 16416 | 472 | 6 | EL6021_M176 |  | BITVAL
SZI6108W | ALARME FEU DETECTEUR FLAMME LOCAL 102 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 12 | 12525 | 8 | 16416 | 473 | 0 | EL6021_M176 |  | BITVAL
SZI6109W | ALARME FEU DETECTEUR FLAMME LOCAL 109 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 406 | 13 | 12525 | 10 | 16416 | 473 | 2 | EL6021_M176 |  | BITVAL
SZI6110W | ALARME FEU MASSIF ZLV LOCAL 002 A2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 406 | 14 | 12525 | 12 | 16416 | 473 | 4 | EL6021_M176 |  | BITVAL
SZI6111W | ALARME FEU MASSIF ZLV LOCAL 002 FF1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 406 | 15 | 12525 | 14 | 16416 | 473 | 6 | EL6021_M176 |  | BITVAL
SZI6112W | ALARME FEU MASSIF ZLV LOCAL 002 FF2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 407 | 0 | 12526 | 0 | 16416 | 474 | 0 | EL6021_M176 |  | BITVAL
SZI6113W | ALARME FEU LEVEL 47400 MAST A1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 407 | 1 | 12526 | 2 | 16416 | 474 | 2 | EL6021_M176 |  | BITVAL
SZI6116W | ALARME FEU LOCAL 004 FX PL OUEST 1 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 407 | 2 | 12526 | 4 | 16416 | 474 | 4 | EL6021_M176 |  | BITVAL
SZI6117W | ALARME FEU LOCAL 004 FX PL OUEST 2 | AL | N | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 407 | 3 | 12526 | 6 | 16416 | 474 | 6 | EL6021_M176 |  | BITVAL
ZZZ6030K00 | DÉFAUT GENERAL VEGA API FILAIRE | AL | N | RES | 1 | A |  | 8 | [10 empty] | A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 90 | 0 | 12590 | 0 | 16416 | 602 | 0 | EL6021_M177 |  | BITVAL
SAV6100D | DEFAUT COMMUNICATION SYSTEME DVT | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 91 | 0 | 12592 | 0 | 16416 | 606 | 0 | EL6021_M177 |  | BITVAL
SAV6102D | DEFAUT SYNTHESE DETECTEUR CL8-1 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 91 | 2 | 12592 | 4 | 16416 | 606 | 4 | EL6021_M177 |  | BITVAL |  |  | MOD
SAV6104D | DEFAUT SYNTHESE DETECTEUR CL8-2 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 91 | 4 | 12592 | 8 | 16416 | 607 | 0 | EL6021_M177 |  | BITVAL |  |  | MOD
SAV6106D | DEFAUT SYNTHESE DETECTEUR CL8-3 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 91 | 6 | 12592 | 12 | 16416 | 607 | 4 | EL6021_M177 |  | BITVAL
SAV6108D | DEFAUT SYNTHESE DETECTEUR CL8-4 | AL | N | RES | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 91 | 8 | 12593 | 0 | 16416 | 608 | 0 | EL6021_M177 |  | BITVAL
SAV6003W | ALARME UDMH/N2H4 LOCAL 501 DVT NIV 29.200 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 4 | 12594 | 8 | 16416 | 611 | 0 | EL6021_M177 |  | BITVAL
SAV6004W | ALARME N2H4 321-1 PANNEAUX ERGOLS NIV 37.000 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 5 | 12594 | 10 | 16416 | 611 | 2 | EL6021_M177 |  | BITVAL
SAV6005W | ALARME UDMH U300-3 PANNEAUX ERGOLS NIV 37.000 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 6 | 12594 | 12 | 16416 | 611 | 4 | EL6021_M177 |  | BITVAL
SAV6006W | ALARME UDMH LOCAL 601 NIV31.800 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 8 | 12595 | 0 | 16416 | 612 | 0 | EL6021_M177 |  | BITVAL
SAV6007W | ALARME UDMH/N2H4 AMBIANCE | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 9 | 12595 | 2 | 16416 | 612 | 2 | EL6021_M177 |  | BITVAL
SAV6008W | ALARME FUITE UDMH REMP. AVUM | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 12 | 12595 | 8 | 16416 | 613 | 0 | EL6021_M177 |  | BITVAL
SAV6009W | ALARME FUITE UDMH REMP. AVUM | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 13 | 12595 | 10 | 16416 | 613 | 2 | EL6021_M177 |  | BITVAL
SAV6010W | ALARME FUITE UDMH COIFFE | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 92 | 14 | 12595 | 12 | 16416 | 613 | 4 | EL6021_M177 |  | BITVAL
SAV6023W | ALARME FUITE UDMH U300-8 PANNEAUX ERGOLS NIV. 39.600 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 10000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | NEW | 3 |  |  | 92 | 15 | 12595 | 14 | 16416 | 613 | 6 | EL6021_M177 |  | BITVAL |  | Nuovo segnale VEGA C
SAV6011W | ALARME FUITE N2H4 REMP. AVUM | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 0 | 12596 | 0 | 16416 | 614 | 0 | EL6021_M177 |  | BITVAL
SAV6012W | ALARME FUITE N2H4 REMP. AVUM | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 1 | 12596 | 2 | 16416 | 614 | 2 | EL6021_M177 |  | BITVAL
SAV6013W | ALARME FUITE N2H4 COIFFE | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 2 | 12596 | 4 | 16416 | 614 | 4 | EL6021_M177 |  | BITVAL
SAV6024W | ALARME FUITE N2H4 321-8 PANNEAUX ERGOLS NIV. 39.600 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 10000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | NEW | 3 |  |  | 93 | 3 | 12596 | 6 | 16416 | 614 | 6 | EL6021_M177 |  | BITVAL |  | Nuovo Segnale VEGA C
SAV6014W | ALARME N2O4 LOCAL 501 DVT NIV 29.200 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 4 | 12596 | 8 | 16416 | 615 | 0 | EL6021_M177 |  | BITVAL
SAV6015W | ALARME N2O4 LOCAL 701 NIV 34.400 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 5 | 12596 | 10 | 16416 | 615 | 2 | EL6021_M177 |  | BITVAL
SAV6016W | ALARME N2O4 N200-3 PANNEAUX ERGOLS NIV 37.000 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 6 | 12596 | 12 | 16416 | 615 | 4 | EL6021_M177 |  | BITVAL
SAV6017W | ALARME N2O4 LOCAL 701 NIV 34.400 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 8 | 12597 | 0 | 16416 | 616 | 0 | EL6021_M177 |  | BITVAL
SAV6018W | ALARME N2O4 AMBIANCE CL8-3 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 9 | 12597 | 2 | 16416 | 616 | 2 | EL6021_M177 |  | BITVAL
SAV6019W | ALARME FUITE N2O4 REMP. AVUM CL8-4 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6108D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 12 | 12597 | 8 | 16416 | 617 | 0 | EL6021_M177 |  | BITVAL
SAV6020W | ALARME FUITE N2O4 REMP. AVUM CL8-4 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6108D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 13 | 12597 | 10 | 16416 | 617 | 2 | EL6021_M177 |  | BITVAL
SAV6021W | ALARME FUITE N2O4 COIFFE CL8-4 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 | SAV6108D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 93 | 14 | 12597 | 12 | 16416 | 617 | 4 | EL6021_M177 |  | BITVAL
SAV6022W | ALARME FUITE N2O4 N200-8 PANNEAUX ERGOLS NIV. 39.600 CL8-3 | AL | N | RES | 1 | S;F;D | PCP | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 10000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | NEW | 3 |  |  | 93 | 15 | 12597 | 14 | 16416 | 617 | 6 | EL6021_M177 |  | BITVAL |  | Nuovo Segnale VEGA C
JSY6002 | ALARME SYNTHESE CAR PORTIQUE ZLV | AL | N | RES | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 |  | MG68;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 94 | 0 | 12598 | 0 | 16416 | 618 | 0 | EL6021_M177 |  | BITVAL
OVP6315O | VANNE RINCAGE PORTIQUE OUVERTE | AL | N | RES | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 94 | 1 | 12598 | 2 | 16416 | 618 | 2 | EL6021_M177 |  | BITVAL
SCX6021GE | CYCLE EI NIV 18.400 LOC. 101 ENERGIE ENCL. | AL | N | RES | 1 | S | [9 empty] | x==1 |  |  | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 94 | 2 | 12598 | 4 | 16416 | 618 | 4 | EL6021_M177 |  | BITVAL
SBT6021O | EPANDAGE N2 NIV 18.400 LOCAL 101 ENERGIE | AL | O | RES | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 94 | 3 | 12598 | 6 | 16416 | 618 | 6 | EL6021_M177 |  | BITVAL
SCX6022GE | CYCLE EI NIV 21.200 SAUVEGARDE CFS ENCL. | AL | N | RES | 1 | S | [9 empty] | x==1 |  |  | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 94 | 6 | 12598 | 12 | 16416 | 619 | 4 | EL6021_M177 |  | BITVAL
SBT6022O | EPANDAGE N2 NIV 21.200 SAUVEGARDE CFS | AL | O | RES | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 94 | 7 | 12598 | 14 | 16416 | 619 | 6 | EL6021_M177 |  | BITVAL
JSY6911 | DEFAUT DISTRIBUTION 230V CAT.III A | AL | N | RES | 1 | F;E |  | 8 | [7 empty] | x==1 |  |  | F;E | [13 empty] | NOT | 1000 |  | VG09 | Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 94 | 8 | 12599 | 0 | 16416 | 620 | 0 | EL6021_M177 |  | BITVAL
JSY6912 | DEFAUT DISTRIBUTION 230V CAT.III B | AL | N | RES | 1 | F;E |  | 8 | [7 empty] | x==1 |  |  | F;E | [13 empty] | NOT | 1000 |  | VG09 | Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 94 | 9 | 12599 | 2 | 16416 | 620 | 2 | EL6021_M177 |  | BITVAL
JSY6913 | DEFAUT DISTRIBUTION 48V E/S MODULE 1 | AL | N | RES | 1 | F |  | 8 | [7 empty] | x==1 |  |  | F | [13 empty] | NOT | 1000 |  | VG09 | Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 94 | 10 | 12599 | 4 | 16416 | 620 | 4 | EL6021_M177 |  | BITVAL
JSY6914 | DEFAUT DISTRIBUTION 48V E/S MODULE 2 | AL | N | RES | 1 | F |  | 8 | [7 empty] | x==1 |  |  | F | [13 empty] | NOT | 1000 |  | VG09 | Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 94 | 11 | 12599 | 6 | 16416 | 620 | 6 | EL6021_M177 |  | BITVAL
SCX6023GE | CYCLE EI NIV 29.200 BCV/INTF ENCL. | AL | N | RES | 1 | S | [9 empty] | x==1 |  |  | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 94 | 12 | 12599 | 8 | 16416 | 621 | 0 | EL6021_M177 |  | BITVAL
SBT6023O | EPANDAGE N2 NIV 29.200 BCV/INTF | AL | O | RES | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 94 | 13 | 12599 | 10 | 16416 | 621 | 2 | EL6021_M177 |  | BITVAL
ESY6970W | DEFAUT DEPART CAT.II TDGA PORTIQUE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | VG09;E67 | Process Fluide et Energie VEGA (VG);Energy TD (E) | CCS | 3 |  |  | 95 | 0 | 12600 | 0 | 16416 | 622 | 0 | EL6021_M177 |  | BITVAL
ESY6980W | DEFAUT CONF.CAT.II TDGA PORTIQUE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | VG09;E67 | Process Fluide et Energie VEGA (VG);Energy TD (E) | CCS | 3 |  |  | 95 | 1 | 12600 | 2 | 16416 | 622 | 2 | EL6021_M177 |  | BITVAL
ZZS6002 | VEGA API FILAIRE DEF. CARTE SER BAC0 POS2 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 0 | 12602 | 0 | 16416 | 626 | 0 | EL6021_M177 |  | BITVAL
ZZS6003 | VEGA API FILAIRE DEF. CARTE SER BAC0 POS3 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 1 | 12602 | 2 | 16416 | 626 | 2 | EL6021_M177 |  | BITVAL
ZZE6004 | VEGA API FILAIRE DEF. CARTE ETOR BAC0 POS4 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 2 | 12602 | 4 | 16416 | 626 | 4 | EL6021_M177 |  | BITVAL
ZZE6005 | VEGA API FILAIRE DEF. CARTE ETOR BAC0 POS5 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 3 | 12602 | 6 | 16416 | 626 | 6 | EL6021_M177 |  | BITVAL
ZZE6006 | VEGA API FILAIRE DEF. CARTE ETOR BAC0 POS6 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 4 | 12602 | 8 | 16416 | 627 | 0 | EL6021_M177 |  | BITVAL
ZZE6007 | VEGA API FILAIRE DEF. CARTE ETOR BAC0 POS7 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 5 | 12602 | 10 | 16416 | 627 | 2 | EL6021_M177 |  | BITVAL
ZZE6008 | VEGA API FILAIRE DEF. CARTE ETOR BAC0 POS8 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 6 | 12602 | 12 | 16416 | 627 | 4 | EL6021_M177 |  | BITVAL
ZZE6010 | VEGA API FILAIRE DEF. CARTE ETOR BAC0 POS10 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 7 | 12602 | 14 | 16416 | 627 | 6 | EL6021_M177 |  | BITVAL
ZZT6010 | VEGA API FILAIRE DEF. CARTE STOR BAC1 POS0 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 8 | 12603 | 0 | 16416 | 628 | 0 | EL6021_M177 |  | BITVAL
ZZT6011 | VEGA API FILAIRE DEF. CARTE STOR BAC1 POS1 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 9 | 12603 | 2 | 16416 | 628 | 2 | EL6021_M177 |  | BITVAL
ZZT6012 | VEGA API FILAIRE DEF. CARTE STOR BAC1 POS2 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 10 | 12603 | 4 | 16416 | 628 | 4 | EL6021_M177 |  | BITVAL
ZZT6013 | VEGA API FILAIRE DEF. CARTE STOR BAC1 POS3 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 11 | 12603 | 6 | 16416 | 628 | 6 | EL6021_M177 |  | BITVAL
ZZN6014 | VEGA API FILAIRE DEF. CARTE EANA BAC1 POS4 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 12 | 12603 | 8 | 16416 | 629 | 0 | EL6021_M177 |  | BITVAL
ZZE6015 | VEGA API FILAIRE DEF. CARTE ETOR BAC1 POS5 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 1000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 13 | 12603 | 10 | 16416 | 629 | 2 | EL6021_M177 |  | BITVAL
ZZC6009 | VEGA API FILAIRE DEF. CARTE ENOC0301 ETH 2 AND ETH 3 LINKS BAC0 POS9 | AL | N | RES | 1 | F;A | [12 empty] | F;A | [13 empty] | NOT | 10000 |  | VG10 | Process Fluide et Energie Vega (VG) | NEW | 3 |  |  | 96 | 14 | 12603 | 12 | 16416 | 629 | 4 | EL6021_M177 |  | BITVAL |  | NUOVO ALLARME INTERNO WIRE PLC
SWE6021O | CR VANNE EI NIV 18.400 LOCAL 101 NRJ EVENT | AL | O | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 4 | 12612 | 8 | 16416 | 647 | 0 | EL6021_M177 |  | BITVAL
SWE6021F | CR VANNE EI NIV 18.400 LOCAL 101 ENERGIE | AL | O | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 5 | 12612 | 10 | 16416 | 647 | 2 | EL6021_M177 |  | BITVAL
SWE6022O | CR VANNE EI NIV 21.200 CFS EVENT | AL | O | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 12 | 12613 | 8 | 16416 | 649 | 0 | EL6021_M177 |  | BITVAL
SWE6022F | CR VANNE EI NIV 21.200 SAUVEGARDE CFS | AL | O | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 13 | 12613 | 10 | 16416 | 649 | 2 | EL6021_M177 |  | BITVAL
SWE6023O | CR VANNE EI NIV 29.200 BCV/INTF EVENT | AL | O | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 102 | 4 | 12614 | 8 | 16416 | 651 | 0 | EL6021_M177 |  | BITVAL
SWE6023F | CR VANNE EI NIV 29.200 BCV/INTF | AL | O | RES | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 102 | 5 | 12614 | 10 | 16416 | 651 | 2 | EL6021_M177 |  | BITVAL
ESA6132 | TD 1602-101-32 SD FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E67 | Energy TD (E) | ENE_MC | 3 |  |  | 105 | 9 | 12621 | 2 | 16416 | 664 | 2 | EL6021_M177 |  | BITVAL
ESA6133 | TD 1602-101-33 SD FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E67 | Energy TD (E) | ENE_MC | 3 |  |  | 105 | 10 | 12621 | 4 | 16416 | 664 | 4 | EL6021_M177 |  | BITVAL
EZC6325D121 | PM3250 1602-101-21 CAT II Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD CAT II 1602 101 21 (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 0 | 14510 | 0 | 16416 | 4442 | 0 | EL6021_M177 |  | BITVAL
EZC6325D120 | PM3250 1602-101-20 CAT II Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD CAT II 1602 101 20 (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 1 | 14510 | 2 | 16416 | 4442 | 2 | EL6021_M177 |  | BITVAL
EZC6325D130 | PM3250 1602-101-30 CAT IIIA Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 101 30 CAT IIIA (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 2 | 14510 | 4 | 16416 | 4442 | 4 | EL6021_M177 |  | BITVAL
EZC6325D131 | PM3250 1602-101-31 CAT IIIB Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 101 31 CAT IIIB (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 3 | 14510 | 6 | 16416 | 4442 | 6 | EL6021_M177 |  | BITVAL
EZC6325D230 | PM3250 1602-201-30 CAT IIIA Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 201 30 CAT IIIA (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 4 | 14510 | 8 | 16416 | 4443 | 0 | EL6021_M177 |  | BITVAL
EZC6325D231 | PM3250 1602-201-31 CAT IIIB Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 201 31 CAT IIIB (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 5 | 14510 | 10 | 16416 | 4443 | 2 | EL6021_M177 |  | BITVAL
EZC6325D530 | PM3250 1602-501-30 CAT IIIA Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 501 30 CAT IIIA (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 6 | 14510 | 12 | 16416 | 4443 | 4 | EL6021_M177 |  | BITVAL
EZC6325D531 | PM3250 1602-501-31 CATIIIB Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 501 31 CAT IIIB (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 7 | 14510 | 14 | 16416 | 4443 | 6 | EL6021_M177 |  | BITVAL
EZC6325D630 | PM3250 1602-502-30 CATIIIA Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 502 30 CAT IIIA (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 8 | 14511 | 0 | 16416 | 4444 | 0 | EL6021_M177 |  | BITVAL
EZC6325D631 | PM3250 1602-502-31 CATIIIB Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TDGA 1602 502 31 CAT IIIB (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 9 | 14511 | 2 | 16416 | 4444 | 2 | EL6021_M177 |  | BITVAL
EZC6325AD42 | PM3250 1602-401-002 CATIIIA Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD AXIMA 1602 401 002 CAT IIIA (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 10 | 14511 | 4 | 16416 | 4444 | 4 | EL6021_M177 |  | BITVAL
EZC6325BD42 | PM3250 1602-401-002 CATIIIB Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD AXIMA 1602 401 002 CAT IIIB (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 11 | 14511 | 6 | 16416 | 4444 | 6 | EL6021_M177 |  | BITVAL
EZC6325D41 | PM3250 1602-401-001 CATII Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD AXIMA 1602 401 001 CAT II (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 12 | 14511 | 8 | 16416 | 4445 | 0 | EL6021_M177 |  | BITVAL
EZC6325D43 | PM3250 1602-401-003 CATII Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD AXIMA 1602 401 003 CAT II (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 13 | 14511 | 10 | 16416 | 4445 | 2 | EL6021_M177 |  | BITVAL
EZC6325D132 | PM3250 1602-101-32 CATIIIA Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD3 Local 101 1602 101 32 CAT IIIA (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 14 | 14511 | 12 | 16416 | 4445 | 4 | EL6021_M177 |  | BITVAL
EZC6325D133 | PM3250 1602-101-33 CATIIIB Read Error | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | TD3 Local 101 1602 101 33 CAT IIIB (E67 popup) | Energie TD | ENE_MC | 3 |  |  | 900 | 15 | 14511 | 14 | 16416 | 4445 | 6 | EL6021_M177 |  | BITVAL
SFE6001M | ALERTE EVACUATION ZLV (ROUGE CLIGNOTANT) | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 14 | 16416 | 1105 | 6 | EL1134_M5 | 8 | BITVAL
SFE6002M | ACCES INTERDIT ZLV (ROUGE FIXE) | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12842 | 6 | 16416 | 1106 | 6 | EL1134_M6 | 8 | BITVAL
VSY6600W1 | ALARME DE NIVEAU 1 CLIM MASSIF ZLV VEGA | AL | O | FIL | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC01;HVAC02 | HVAC; Process Fluide et Energie General (VG) | CCS | [5 empty] | 12842 | 14 | 16416 | 1107 | 6 | EL1134_M7 | 8 | BITVAL
VSY6600W2 | ALARME DE NIVEAU 2 CLIM MASSIF ZLV VEGA | AL | O | FIL | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC01;HVAC02 | HVAC; Process Fluide et Energie General (VG) | CCS | [5 empty] | 12843 | 0 | 16416 | 1108 | 0 | EL1134_M8 | 1 | BITVAL
SWE6002O | CR VANNE EI LOCAL 004 COMM. POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12843 | 4 | 16416 | 1108 | 4 | EL1134_M8 | 4 | BITVAL
JSY6901 | **DEFAUT DISTRIBUTION 230V CAT.III A | AL | O | FIL | 1 | F;E |  | 8 | [8 empty] | 0 |  | F;E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12843 | 8 | 16416 | 1109 | 0 | EL1134_M9 | 1 | BITVAL
JSY6902 | **DEFAUT DISTRIBUTION 230 V CAT.III B | AL | O | FIL | 1 | F;E |  | 8 | [8 empty] | 0 |  | F;E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12843 | 10 | 16416 | 1109 | 2 | EL1134_M9 | 5 | BITVAL
JSY6907 | **DEFAUT DISTRIBUTION 48V E/S ANA MODULE 1 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12843 | 12 | 16416 | 1109 | 4 | EL1134_M9 | 4 | BITVAL
JSY6908 | **DEFAUT DISTRIBUTION 48V E/S ANA MODULE 2 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12843 | 14 | 16416 | 1109 | 6 | EL1134_M9 | 8 | BITVAL
JSY6903 | **DEFAUT DISTRIBUTION 48V E/S TOR MODULE 1 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12844 | 0 | 16416 | 1110 | 0 | EL1134_M10 | 1 | BITVAL
JSY6904 | **DEFAUT DISTRIBUTION 48V E/S TOR MODULE 2 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12844 | 2 | 16416 | 1110 | 2 | EL1134_M10 | 5 | BITVAL
JSY6905 | **DEFAUT DISTRIBUTION 48V CMDE TOR MODULE 1 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12844 | 4 | 16416 | 1110 | 4 | EL1134_M10 | 4 | BITVAL
JSY6906 | **DEFAUT DISTRIBUTION 48V CMDE TOR MODULE 2 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG08 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12845 | 0 | 16416 | 1112 | 0 | EL1134_M13 | 1 | BITVAL
SWE6003O | CR VANNE EI LOCAL 007 CAT.III CU POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12845 | 2 | 16416 | 1112 | 2 | EL1134_M13 | 5 | BITVAL
JSY6001 | **ALARME SYNTHESE CAR MASSIF ZLV | AL | O | FIL | 1 | S;F;D | [10 empty] | 0 |  | S;F;D | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG68;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12845 | 4 | 16416 | 1112 | 4 | EL1134_M13 | 4 | BITVAL
SCX6002GE | **CYCLE EI LOCAL 004 COMM. ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12845 | 14 | 16416 | 1113 | 6 | EL1134_M14 | 8 | BITVAL
SBT6002O | EPANDAGE N2 LOCAL 004 COMMUNICATION | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 0 | 16416 | 1114 | 0 | EL1134_M15 | 1 | BITVAL
SWE6002F | CR VANNE EI LOCAL 004 COMM. POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 4 | 16416 | 1114 | 4 | EL1134_M15 | 4 | BITVAL
SCX6003GE | **CYCLE EI LOCAL 007 CAT.III CU ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 12 | 16416 | 1115 | 4 | EL1134_M16 | 4 | BITVAL
SBT6003O | EPANDAGE N2 LOCAL 007 CAT.III CU | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 14 | 16416 | 1115 | 6 | EL1134_M16 | 8 | BITVAL
SWE6003F | CR VANNE EI LOCAL 007 CAT.III CU POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12847 | 8 | 16416 | 1117 | 0 | EL1134_M18 | 1 | BITVAL
SCX6004GE | **CYCLE EI LOCAL 008 BATTERIES CUH ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 0 | 16416 | 1118 | 0 | EL1134_M19 | 1 | BITVAL
SBT6004O | EPANDAGE N2 LOCAL 008 BATTERIES CUH | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 2 | 16416 | 1118 | 2 | EL1134_M19 | 5 | BITVAL
SWE6004F | CR VANNE EI LOCAL 008 BATT. CUH POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 6 | 16416 | 1118 | 6 | EL1134_M19 | 8 | BITVAL
SCX6005GE | **CYCLE EI LOCAL 009 BATTERIES CUB ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 14 | 16416 | 1119 | 6 | EL1134_M20 | 8 | BITVAL
SBT6005O | EPANDAGE N2 LOCAL 009 BATTERIES CUB | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12849 | 0 | 16416 | 1120 | 0 | EL1134_M21 | 1 | BITVAL
SWE6005F | CR VANNE EI LOCAL 009 BATT. CUB POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12849 | 4 | 16416 | 1120 | 4 | EL1134_M21 | 4 | BITVAL
SCX6001GE | **CYCLE EI LOCAL 013 ET 002 ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 6 | 16416 | 1122 | 6 | EL1134_M24 | 8 | BITVAL
SBT6001O | EPANDAGE N2 LOCAL 013 ET 002 | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 8 | 16416 | 1123 | 0 | EL1134_M25 | 1 | BITVAL
SWE6001F | CR VANNE EI LOCAL 013 ET 002 POSITION LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 12 | 16416 | 1123 | 4 | EL1134_M25 | 4 | BITVAL
SCX6006GE | **CYCLE EI LOCAL 101 BAIES CU ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12851 | 4 | 16416 | 1124 | 4 | EL1134_M26 | 4 | BITVAL
ESY6053D | **DEFAUT CONF. TD COLONNE DE LAVAGE UDMH | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12852 | 6 | 16416 | 1126 | 6 | EL1134_M28 | 8 | BITVAL
ESY6063D | **DEFAUT DEPART TD COLONNE DE LAVAGE UDMH | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12852 | 8 | 16416 | 1127 | 0 | EL1134_M29 | 1 | BITVAL
SWE6004O | CR VANNE EI LOCAL 008 BATT. CUH POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12852 | 10 | 16416 | 1127 | 2 | EL1134_M29 | 5 | BITVAL
ESY6070D | **DEFAUT CONF. BAIE ADAPT ET TD CUB ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12853 | 12 | 16416 | 1129 | 4 | EL1134_M31 | 4 | BITVAL
ESY6080D | **DEFAUT DEPART BAIE ADAPT ET TD CUB ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12853 | 14 | 16416 | 1129 | 6 | EL1134_M31 | 8 | BITVAL
ESY6090D | **DEFAUT CONF. BAIE ADAPT ET TD CUH ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12854 | 0 | 16416 | 1130 | 0 | EL1134_M32 | 1 | BITVAL
ESY6100D | **DEFAUT DEPART BAIE ADAPT ET TD CUH ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12854 | 2 | 16416 | 1130 | 2 | EL1134_M32 | 5 | BITVAL
UPP6301D | DEFAUT POMPE UPP6301 | AL | N | FIL | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 10 | 16416 | 1133 | 2 | EL1134_M36 | 5 | BITVAL
SWE6005O | CR VANNE EI LOCAL 009 BATT. CUB POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12856 | 2 | 16416 | 1134 | 2 | EL1134_M37 | 5 | BITVAL
SWE6001O | CR VANNE EI LOCAL 013 ET 002 POSITION EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12856 | 4 | 16416 | 1134 | 4 | EL1134_M37 | 4 | BITVAL
ESY6050D | **DEF.CONF.TD CAT III MASSIF 013,004,103,002 | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12856 | 6 | 16416 | 1134 | 6 | EL1134_M37 | 8 | BITVAL
ESY6060D | **DEF.DEP.TD CAT III MASSIF 013,004,103,002 | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12856 | 8 | 16416 | 1135 | 0 | EL1134_M38 | 1 | BITVAL
NVM6304O | VM NVM6304 (TRAITEMET N) OUVERTE | AL | N | FIL | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12857 | 6 | 16416 | 1136 | 6 | EL1134_M39 | 8 | BITVAL
ESY6051D | **DEFAUT CONF. TD CAT III B MASSIF (126) | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 |  | CCS | [5 empty] | 12858 | 8 | 16416 | 1139 | 0 | EL1134_M42 | 1 | BITVAL
ESY6061D | **DEFAUT DEPART TD CAT III B MASSIF(126) | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 |  | CCS | [5 empty] | 12858 | 10 | 16416 | 1139 | 2 | EL1134_M42 | 5 | BITVAL
ESY6030D | **DEFAUT CONFIGURATION TGBT CAT.IIIA ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12859 | 0 | 16416 | 1140 | 0 | EL1134_M43 | 1 | BITVAL
ESY6040D | **DEFAUT DEPART TGBT CAT.IIIA ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12859 | 2 | 16416 | 1140 | 2 | EL1134_M43 | 5 | BITVAL
ESY6031D | **DEFAUT CONFIGURATION TGBT CAT.IIIB ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12859 | 4 | 16416 | 1140 | 4 | EL1134_M43 | 4 | BITVAL
ESY6041D | **DEFAUT DEPART TGBT CAT.IIIB ZLV | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12860 | 0 | 16416 | 1142 | 0 | EL1134_M46 | 1 | BITVAL
ESY6052D | **DEFAUT CONF. TD COLONNE DE LAVAGE N2O4 | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12860 | 6 | 16416 | 1142 | 6 | EL1134_M46 | 8 | BITVAL
ESY6062D | **DEFAUT DEPART TD COLONNE DE LAVAGE N2O4 | AL | O | FIL | 1 | E |  | E | [8 empty] | 0 |  | E | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | VG07 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12860 | 8 | 16416 | 1143 | 0 | EL1134_M47 | 1 | BITVAL
SCE6001D | SYNTHESE DEFAUT EVACUATION ZLV | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12860 | 14 | 16416 | 1143 | 6 | EL1134_M47 | 8 | BITVAL
SSP6001D | DEFAUT SIRENE ZLV | AL | O | FIL | 1 | S;E |  | E | [10 empty] | S;E | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12861 | 6 | 16416 | 1144 | 6 | EL1134_M48 | 8 | BITVAL
SCE6002D | SYNTHESE DEFAUT REPLI ZLV | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12862 | 6 | 16416 | 1146 | 6 | EL1134_M50 | 8 | BITVAL
SBT6006O | EPANDAGE N2 LOCAL 101 BAIES CU | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 0 | 16416 | 1152 | 0 | EL1134_M57 | 1 | BITVAL
SWE6006F | CR VANNE EI LOCAL 101 BAIES CU POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 4 | 16416 | 1152 | 4 | EL1134_M57 | 4 | BITVAL
SCX6007GE | **CYCLE EI LOCAL 103 BCV/CCS ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 12 | 16416 | 1153 | 4 | EL1134_M58 | 4 | BITVAL
SBT6007O | EPANDAGE N2 LOCAL 103 BCV/CCS | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 14 | 16416 | 1153 | 6 | EL1134_M58 | 8 | BITVAL
SWE6007F | CR VANNE EI LOCAL 103 BCV/CCS POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 2 | 16416 | 1154 | 2 | EL1134_M59 | 5 | BITVAL
SCX6008GE | **CYCLE EI LOCAL 111 BATT. CAT.III ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 10 | 16416 | 1155 | 2 | EL1134_M60 | 5 | BITVAL
SBT6008O | EPANDAGE N2 LOCAL 111 BATT. CAT.III | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 12 | 16416 | 1155 | 4 | EL1134_M60 | 4 | BITVAL
SWE6008F | CR VANNE EI LOCAL 111 BATT.CAT.III POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12867 | 6 | 16416 | 1156 | 6 | EL1134_M61 | 8 | BITVAL
SCX6009GE | **CYCLE EI LOCAL 112 BATT. CAT.III ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12867 | 14 | 16416 | 1157 | 6 | EL1134_M62 | 8 | BITVAL
SBT6009O | EPANDAGE N2 LOCAL 112 BATT. CAT.III | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 0 | 16416 | 1158 | 0 | EL1134_M63 | 1 | BITVAL
SWE6009F | CR VANNE EI LOCAL 112 BATT.CAT.III POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 4 | 16416 | 1158 | 4 | EL1134_M63 | 4 | BITVAL
SCX6010GE | **CYCLE EI LOCAL 113 UPS ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 12 | 16416 | 1159 | 4 | EL1134_M64 | 4 | BITVAL
SBT6010O | EPANDAGE N2 LOCAL 113 UPS | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 14 | 16416 | 1159 | 6 | EL1134_M64 | 8 | BITVAL
SWE6010F | CR VANNE EI LOCAL 113 UPS POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12869 | 2 | 16416 | 1160 | 2 | EL1134_M65 | 5 | BITVAL
SCX6011GE | **CYCLE EI LOCAL 115 TGBT ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 4 | 16416 | 1162 | 4 | EL1134_M68 | 4 | BITVAL
SBT6011O | EPANDAGE N2 LOCAL 115 TGBT | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 6 | 16416 | 1162 | 6 | EL1134_M68 | 8 | BITVAL
SWE6011F | CR VANNE EI LOCAL 115 TGBT POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 10 | 16416 | 1163 | 2 | EL1134_M69 | 5 | BITVAL
SCX6012GE | **CYCLE EI LOCAL 116 HT ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 2 | 16416 | 1164 | 2 | EL1134_M70 | 5 | BITVAL
SBT6012O | EPANDAGE N2 LOCAL 116 HT | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 4 | 16416 | 1164 | 4 | EL1134_M70 | 4 | BITVAL
SWE6012F | CR VANNE EI LOCAL 116 HT POSITION LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 8 | 16416 | 1165 | 0 | EL1134_M71 | 1 | BITVAL
SCX6013GE | **CYCLE EI LOCAL 126 SCC CLIM ENCLENCHE | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12872 | 6 | 16416 | 1166 | 6 | EL1134_M72 | 8 | BITVAL
SBT6013O | EPANDAGE N2 LOCAL 126 SCC CLIM | AL | O | FIL | 1 | S | PCP | [11 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12872 | 8 | 16416 | 1167 | 0 | EL1134_M73 | 1 | BITVAL
SWE6013F | CR VANNE EI LOCAL 126 SCC CLIM POS LOCAL | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12872 | 12 | 16416 | 1167 | 4 | EL1134_M73 | 4 | BITVAL
SCG6000D | DEFAUT SYSTEME COMMUNICATION DETG | AL | O | FIL | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG61;DG62;DG63;DG65 | Detection Gaz (DG) | CCS | [5 empty] | 12872 | 14 | 16416 | 1167 | 6 | EL1134_M73 | 8 | BITVAL
SCG6001D | DEFAUT SYNTHESE ALIMENTATION COFFRET DETG | AL | O | FIL | 1 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | DG61;DG62;DG63;DG65 | Detection Gaz (DG) | CCS | [5 empty] | 12873 | 0 | 16416 | 1168 | 0 | EL1134_M74 | 1 | BITVAL
NNH6301 | LIMITE TROP PLEIN CUVE N2O4 | AL | N | FIL | 1 | F |  | 8 | [10 empty] | F | [13 empty] | NOT | 1000 |  | MG67;MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 2 | 16416 | 1168 | 2 | EL1134_M74 | 5 | BITVAL
NNH6302 | LIMITE EFFLUENTS TOXIQUES CUVE N2O4 | AL | N | FIL | 1 | F |  | 8 | [10 empty] | F | [13 empty] | NOT | 1000 |  | MG67;MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 4 | 16416 | 1168 | 4 | EL1134_M74 | 4 | BITVAL
ONH6301 | CAPTEUR NIVEAU HAUT 175M3 ZLV VEGA | AL | N | FIL | 1 | S;F;D |  | 8 | [10 empty] | S;F;D | [13 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 8 | 16416 | 1169 | 0 | EL1134_M75 | 1 | BITVAL
OPP6301D | DEFAUT POMPE OPP6301 | AL | N | FIL | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12874 | 2 | 16416 | 1170 | 2 | EL1134_M76 | 5 | BITVAL
OPP6302D | DEFAUT POMPE OPP6302 | AL | N | FIL | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG65;VG04;HVAC03 | Moyens Generaux (MG); Process Fluide et Energie General (VG); HVAC | CCS | [5 empty] | 12875 | 6 | 16416 | 1172 | 6 | EL1134_M79 | 8 | BITVAL
ZZP6002D | **DEFAUT SYNTHESE AMD SYSTEME SON MASSIF ZLV | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12875 | 12 | 16416 | 1173 | 4 | EL1134_M80 | 4 | BITVAL
SWE6006O | CR VANNE EI LOCAL 101 BAIES CU POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12876 | 0 | 16416 | 1174 | 0 | EL1134_M81 | 1 | BITVAL
SWE6007O | CR VANNE EI LOCAL 103 BCV/CCS POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12878 | 6 | 16416 | 1178 | 6 | EL1134_M85 | 8 | BITVAL
SWE6008O | CR VANNE EI LOCAL 111 BATT.CAT.III POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12878 | 8 | 16416 | 1179 | 0 | EL1134_M86 | 1 | BITVAL
SWE6009O | CR VANNE EI LOCAL 112 BATT.CAT.III POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12878 | 10 | 16416 | 1179 | 2 | EL1134_M86 | 5 | BITVAL
SWE6010O | CR VANNE EI LOCAL 113 UPS POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12878 | 12 | 16416 | 1179 | 4 | EL1134_M86 | 4 | BITVAL
SWE6011O | CR VANNE EI LOCAL 115 TGBT POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12878 | 14 | 16416 | 1179 | 6 | EL1134_M86 | 8 | BITVAL
SWE6012O | CR VANNE EI LOCAL 116 HT POSITION EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12879 | 0 | 16416 | 1180 | 0 | EL1134_M87 | 1 | BITVAL
SWE6013O | CR VANNE EI LOCAL 126 SCC CLIM POS EVENT | AL | O | FIL | 1 | S | [12 empty] | S | [13 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12879 | 2 | 16416 | 1180 | 2 | EL1134_M87 | 5 | BITVAL
OVM6356O | VM OVM6356 (CUVE 175M3) OUVERTE | AL | N | FIL | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12881 | 6 | 16416 | 1184 | 6 | EL1134_M92 | 8 | BITVAL
ZZP6001D | **DEFAUT SYNTHESE AMI SYSTEME SON MASSIF ZLV | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12887 | 6 | 16416 | 1196 | 6 | EL1134_M105 | 8 | BITVAL
UNH6301 | LIMITE TROP PLEIN CUVE UDMH | AL | N | FIL | 1 | F |  | 8 | [10 empty] | F | [13 empty] | NOT | 1000 |  | MG66;MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12887 | 8 | 16416 | 1197 | 0 | EL1134_M106 | 1 | BITVAL
UNH6302 | LIMITE EFFLUENTS TOXIQUES CUVE UDMH | AL | N | FIL | 1 | F |  | 8 | [10 empty] | F | [13 empty] | NOT | 1000 |  | MG66;MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12887 | 10 | 16416 | 1197 | 2 | EL1134_M106 | 5 | BITVAL
NMH6001D | **COLONNE LAVAGE N2O4 DEFAUT PH | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG67 | Moyens Generaux (MG); | CCS | [5 empty] | 12888 | 8 | 16416 | 1199 | 0 | EL1134_M108 | 1 | BITVAL
NCL6001D | **COLONNE LAVAGE N2O4 SYNTHESE DEFAUT | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG67 | Moyens Generaux (MG); | CCS | [5 empty] | 12888 | 10 | 16416 | 1199 | 2 | EL1134_M108 | 5 | BITVAL
UMH6001D | **COLONNE LAVAGE UDMH DEFAUT PH | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG66 | Moyens Generaux (MG); | CCS | [5 empty] | 12890 | 2 | 16416 | 1202 | 2 | EL1134_M112 | 5 | BITVAL
UCL6001D | **COLONNE LAVAGE UDMH SYNTHESE DEFAUT | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG66 | Moyens Generaux (MG); | CCS | [5 empty] | 12890 | 4 | 16416 | 1202 | 4 | EL1134_M112 | 4 | BITVAL
NCL6001WD | **COLONNE LAVAGE N2O4 MODE DEGRADE | AL | O | FIL | 1 | S;F;D |  | 8 | [8 empty] | 0 |  | S;F;D | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG67 | Moyens Generaux (MG); | CCS | [5 empty] | 12890 | 6 | 16416 | 1202 | 6 | EL1134_M112 | 8 | BITVAL
NCL6002D | **SYNTHESE DEFAUT CIRCUIT REFROID. N2O4 | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG67 | Moyens Generaux (MG | CCS | [5 empty] | 12890 | 8 | 16416 | 1203 | 0 | EL1134_M113 | 1 | BITVAL
UCL6001WD | **COLONNE LAVAGE UDMH MODE DEGRADE | AL | O | FIL | 1 | S;F;D |  | 8 | [8 empty] | 0 |  | S;F;D | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG66 | Moyens Generaux (MG); | CCS | [5 empty] | 12890 | 10 | 16416 | 1203 | 2 | EL1134_M113 | 5 | BITVAL
UCL6002D | **SYNTHESE DEFAUT CIRCUIT REFROID. UDMH | AL | O | FIL | 1 | F |  | 8 | [8 empty] | 0 |  | F | [9 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG66 | Moyens Generaux (MG); | CCS | [5 empty] | 12890 | 12 | 16416 | 1203 | 4 | EL1134_M113 | 4 | BITVAL
OVM6355O | VM VIDANGE CUVE 175M3 VEGA OUVERTE | AL | N | FIL | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12891 | 4 | 16416 | 1204 | 4 | EL1134_M114 | 4 | BITVAL
OVP6303O | VP DELUGE LANCEUR VEGA OUVERTE | AL | N | FIL | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12897 | 8 | 16416 | 1217 | 0 | EL1134_M128 | 1 | BITVAL
OVP6304O | VP DELUGE LANCEUR VEGA OUVERTE | AL | N | FIL | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12897 | 12 | 16416 | 1217 | 4 | EL1134_M128 | 4 | BITVAL
OVP6305O | VP DELUGE LANCEUR VEGA OUVERTE | AL | N | FIL | 1 | F | [12 empty] | F | [13 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12898 | 0 | 16416 | 1218 | 0 | EL1134_M129 | 1 | BITVAL
VSY6900W1 | ALARME DE NIVEAU 1 CLIM PORTIQUE ZLV VEGA | AL | O | FIL | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC01;HVAC02 | Moyens Generaux (MG); Process Fluide et Energie General (VG); HVAC | CCS | [5 empty] | 12898 | 2 | 16416 | 1218 | 2 | EL1134_M129 | 5 | BITVAL
VSY6900W2 | ALARME DE NIVEAU 2 CLIM PORTIQUE ZLV VEGA | AL | O | FIL | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC01;HVAC02 | Moyens Generaux (MG); Process Fluide et Energie General (VG); HVAC | CCS | [5 empty] | 12898 | 4 | 16416 | 1218 | 4 | EL1134_M129 | 4 | BITVAL
UVM6304O | VM UVM6304 (TRAITEMET U) OUVERTE | AL | N | FIL | 1 | S;F;D | [12 empty] | S;F;D | [13 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 14 | 16416 | 1223 | 6 | EL1134_M135 | 8 | BITVAL
EZC6115D | VEGA API TGBT SYNTHESE DEFAUT API | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 |  | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 0 | 13035 | 0 | 16416 | 1492 | 0 | EL6021_M178 |  | BITVAL
EZC6115SD | VEGA API TGBT DEF.CARTE SD | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 1 | 13035 | 2 | 16416 | 1492 | 2 | EL6021_M178 |  | BITVAL
EZC6115K2 | VEGA API TGBT DEF.CARTE BAC0 POS.2 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60; MG74 | Energie TGBT et UPS VEGA (E); Moyens Generaux (MG) | NEW | 4 |  |  | 3000 | 2 | 13035 | 4 | 16416 | 1492 | 4 | EL6021_M178 |  | BITVAL
EZC6115K3 | VEGA API TGBT DEF.CARTE BAC0 POS.3 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60; Départ Supplementaires (E60 popup) | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 3 | 13035 | 6 | 16416 | 1492 | 6 | EL6021_M178 |  | BITVAL
EZC6115K4 | VEGA API TGBT DEF.CARTE BAC0 POS.4 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 4 | 13035 | 8 | 16416 | 1493 | 0 | EL6021_M178 |  | BITVAL
EZC6115K5 | VEGA API TGBT DEF.CARTE BAC0 POS.5 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 5 | 13035 | 10 | 16416 | 1493 | 2 | EL6021_M178 |  | BITVAL
EZC6115K6 | VEGA API TGBT DEF.CARTE BAC0 POS.6 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 6 | 13035 | 12 | 16416 | 1493 | 4 | EL6021_M178 |  | BITVAL
EZC6115K7 | VEGA API TGBT DEF.CARTE BAC0 POS.7 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 7 | 13035 | 14 | 16416 | 1493 | 6 | EL6021_M178 |  | BITVAL
EZC6115K8 | VEGA API TGBT DEF.CARTE BAC0 POS.8 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 8 | 13036 | 0 | 16416 | 1494 | 0 | EL6021_M178 |  | BITVAL
EZC6115K9 | VEGA API TGBT DEF.CARTE BAC0 POS.9 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 9 | 13036 | 2 | 16416 | 1494 | 2 | EL6021_M178 |  | BITVAL
EZC6115K10 | VEGA API TGBT DEF.CARTE BAC0 POS.10 PM810 LINK and UPS 1&3 LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 10 | 13036 | 4 | 16416 | 1494 | 4 | EL6021_M178 |  | BITVAL
EZC6115K11 | VEGA API TGBT DEF.CARTE BAC0 POS.11 VMC LINK 1 et CCS M03 LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E60 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3000 | 11 | 13036 | 6 | 16416 | 1494 | 6 | EL6021_M178 |  | BITVAL
EZC6115K16 | VEGA API TGBT DEF.CARTE BAC1 POS.0 PM9C LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E61;E62;E63;E64;E65 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3001 | 0 | 13037 | 0 | 16416 | 1496 | 0 | EL6021_M178 |  | BITVAL
EZC6115K17 | VEGA API TGBT DEF.CARTE BAC1 POS.1 VMC LINK 2 | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E61;E62;E63;E64;E65 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3001 | 1 | 13037 | 2 | 16416 | 1496 | 2 | EL6021_M178 |  | BITVAL
EZC6115K18 | VEGA API TGBT DEF.CARTE BAC1 POS.2 UPS 2&4 LINK and CCS M04 LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E61;E62;E63;E64;E65 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3001 | 2 | 13037 | 4 | 16416 | 1496 | 4 | EL6021_M178 |  | BITVAL
EZC6115K19 | VEGA API TGBT DEF.CARTE BAC1 POS.3 UPS 5&6&7 LINK and CCS M05 LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6115D | E61;E62;E63;E64;E65 | Energie TGBT et UPS VEGA (E) | NEW | 4 |  |  | 3001 | 3 | 13037 | 6 | 16416 | 1496 | 6 | EL6021_M178 |  | BITVAL
EUB6000AU | TGBT ZLV ABSENCE TENSION JDB | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 0 | 13039 | 0 | 16416 | 1500 | 0 | EL6021_M178 |  | BITVAL
EUB6001AU | TGBT-C ZLV ABSENCE TENSION CAT.II | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 1 | 13039 | 2 | 16416 | 1500 | 2 | EL6021_M178 |  | BITVAL
EUB6002AU | TGBT ZLV ABSENCE TENSION CAT.II | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 2 | 13039 | 4 | 16416 | 1500 | 4 | EL6021_M178 |  | BITVAL
EUB6003AU | TGBT-C ZLV ABSENCE TENSION CAT.I | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 3 | 13039 | 6 | 16416 | 1500 | 6 | EL6021_M178 |  | BITVAL
EUB6004AU | TGBT ZLV ABSENCE TENSION CAT.I | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 4 | 13039 | 8 | 16416 | 1501 | 0 | EL6021_M178 |  | BITVAL
EUB6005AU | TGBT-C ZLV ABSENCE TENSION JDB | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 5 | 13039 | 10 | 16416 | 1501 | 2 | EL6021_M178 |  | BITVAL
ESO6002D | TGBT ZLV DEFAUT CAT.II EN SECOURS INVERSE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 8 | 13040 | 0 | 16416 | 1502 | 0 | EL6021_M178 |  | BITVAL
ESO6951D | TGBT-C ZLV DEFAUT CAT.II EN SECOURS INVERSE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 9 | 13040 | 2 | 16416 | 1502 | 2 | EL6021_M178 |  | BITVAL
ESA6001D | TGBT ZLV ALARM TGBT PF IMPROVING CAPACITOR | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 12 | 13040 | 8 | 16416 | 1503 | 0 | EL6021_M178 |  | BITVAL
ESA6951D | TGBT-C ZLV ALARM TGBT-C PF IMPROVING CAPACITOR | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3002 | 13 | 13040 | 10 | 16416 | 1503 | 2 | EL6021_M178 |  | BITVAL
ETH6001D1 | TGBT-C ZLV ALARM PROTECTION RELAY MB103 TM 7001 CAT.II 1st THRESHOLD | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 0 | 13041 | 0 | 16416 | 1504 | 0 | EL6021_M178 |  | BITVAL
ETH6001D2 | TGBT-C ZLV FAULT PROTECTION RELAY MB103 TM 7001 CAT.II | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 1 | 13041 | 2 | 16416 | 1504 | 2 | EL6021_M178 |  | BITVAL
ETH6001D3 | TGBT-C ZLV TRIP PROTECTION RELAY MB103 TM 7001 CAT.II 2nd THRESHOLD | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 2 | 13041 | 4 | 16416 | 1504 | 4 | EL6021_M178 |  | BITVAL
ETH6002D1 | TGBT ZLV ALARM PROTECTION RELAY MB103 TM 7002 CAT.II 1st THRESHOLD | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 3 | 13041 | 6 | 16416 | 1504 | 6 | EL6021_M178 |  | BITVAL
ETH6002D2 | TGBT ZLV FAULT PROTECTION RELAY MB103 TM 7002 CAT.II | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 4 | 13041 | 8 | 16416 | 1505 | 0 | EL6021_M178 |  | BITVAL
ETH6002D3 | TGBT ZLV TRIP PROTECTION RELAY MB103 TM 7002 CAT.I 2nd THRESHOLD | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 5 | 13041 | 10 | 16416 | 1505 | 2 | EL6021_M178 |  | BITVAL
ETH6003D1 | TGBT-C ZLV ALARM PROTECTION RELAY MB103 TM 7003 CAT.I 1st THRESHOLD | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 6 | 13041 | 12 | 16416 | 1505 | 4 | EL6021_M178 |  | BITVAL
ETH6003D2 | TGBT-C ZLV FAULT PROTECTION RELAY MB103 TM 7003 CAT.I | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 7 | 13041 | 14 | 16416 | 1505 | 6 | EL6021_M178 |  | BITVAL
ETH6003D3 | TGBT-C ZLV TRIP PROTECTION RELAY MB103 TM 7003 CAT.I 2nd THRESHOLD | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 8 | 13042 | 0 | 16416 | 1506 | 0 | EL6021_M178 |  | BITVAL
ETH6004D1 | TGBT ZLV ALARM PROTECTION RELAY MB103 TM 7004 CAT.I 1st THRESHOLD | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 9 | 13042 | 2 | 16416 | 1506 | 2 | EL6021_M178 |  | BITVAL
ETH6004D2 | TGBT ZLV FAULT PROTECTION RELAY MB103 TM 7004 CAT.I | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 10 | 13042 | 4 | 16416 | 1506 | 4 | EL6021_M178 |  | BITVAL
ETH6004D3 | TGBT ZLV TRIP PROTECTION RELAY MB103 TM 7004 CAT.I 2nd THRESHOLD | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3003 | 11 | 13042 | 6 | 16416 | 1506 | 6 | EL6021_M178 |  | BITVAL
EQF6001D | TGBT ZLV ARRIVEE TM 7002 CAT.II SD DISJ. QF7001 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 2 | 13043 | 4 | 16416 | 1508 | 4 | EL6021_M178 |  | BITVAL
EQF6002D | TGBT ZLV ARRIVEE TM 7004 CAT.I SD DISJ. QF7002 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 3 | 13043 | 6 | 16416 | 1508 | 6 | EL6021_M178 |  | BITVAL
EQF6001DE | TGBT ZLV ARRIVEE TM 7002 CAT.II DISJ. QF7001 DRAW IN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 4 | 13043 | 8 | 16416 | 1509 | 0 | EL6021_M178 |  | BITVAL
EQF6002DE | TGBT ZLV ARRIVEE TM 7004 CAT.I DISJ. QF7002 DRAW IN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 5 | 13043 | 10 | 16416 | 1509 | 2 | EL6021_M178 |  | BITVAL
EQF6950D | TGBT-C ZLV ARRIVEE TM 7001 CAT.II SD DISJ. QF7950 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 8 | 13044 | 0 | 16416 | 1510 | 0 | EL6021_M178 |  | BITVAL
EQF6951D | TGBT-C ZLV ARRIVEE TM 7003 CAT.I SD DISJ. QF7951 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 9 | 13044 | 2 | 16416 | 1510 | 2 | EL6021_M178 |  | BITVAL
EQF6950DE | TGBT-C ZLV ARRIVEE TM 7001 CAT.II DISJ. QF7950 DRAW IN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 10 | 13044 | 4 | 16416 | 1510 | 4 | EL6021_M178 |  | BITVAL
EQF6951DE | TGBT-C ZLV ARRIVEE TM 7003 CAT.I DISJ. QF7951 DRAW IN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3004 | 11 | 13044 | 6 | 16416 | 1510 | 6 | EL6021_M178 |  | BITVAL
EQF6003D | TGBT ZLV ARRIVEE GEN SET XS-7001 SD DISJ. QF7003 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3005 | 2 | 13045 | 4 | 16416 | 1512 | 4 | EL6021_M178 |  | BITVAL
EQF6952D | TGBT-C ZLV ARRIVEE GEN SET XS-7002 SD DISJ. QF7952 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3005 | 3 | 13045 | 6 | 16416 | 1512 | 6 | EL6021_M178 |  | BITVAL
EQF6003DE | TGBT ZLV ARRIVEE GEN SET XS-7001 DISJ. QF7003 DRAW IN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3005 | 4 | 13045 | 8 | 16416 | 1513 | 0 | EL6021_M178 |  | BITVAL
EQF6952DE | TGBT-C ZLV ARRIVEE GEN SET XS-7002 DISJ. QF7952 DRAW IN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3005 | 5 | 13045 | 10 | 16416 | 1513 | 2 | EL6021_M178 |  | BITVAL
EQF6001MO | ROOM 115 - LEVEL 14.2 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7001 AND QF7002 AND QF7003 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 0 | 13047 | 0 | 16416 | 1516 | 0 | EL6021_M178 |  | BITVAL
EQF6004MO | ROOM 155 - ROOM 109 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7004 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 1 | 13047 | 2 | 16416 | 1516 | 2 | EL6021_M178 |  | BITVAL
EQF6006MO | ROOM 101 - ROOM 014 - ROOM 103 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7006 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 2 | 13047 | 4 | 16416 | 1516 | 4 | EL6021_M178 |  | BITVAL
EQF6007MO | ROOM 010 - ROOM 102 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7007 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 3 | 13047 | 6 | 16416 | 1516 | 6 | EL6021_M178 |  | BITVAL
EQF6008MO | ROOM 108 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7008 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 4 | 13047 | 8 | 16416 | 1517 | 0 | EL6021_M178 |  | BITVAL
EQF6009MO | ROOM 115 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7009 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 5 | 13047 | 10 | 16416 | 1517 | 2 | EL6021_M178 |  | BITVAL
EQF6010MO | ROOM 115 - ROOM 118 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7010 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 6 | 13047 | 12 | 16416 | 1517 | 4 | EL6021_M178 |  | BITVAL
EQF6013MO | ROOM 121 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7013 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 7 | 13047 | 14 | 16416 | 1517 | 6 | EL6021_M178 |  | BITVAL
EQF6016MO | ZEPHIRE ZONE to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7016 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 8 | 13048 | 0 | 16416 | 1518 | 0 | EL6021_M178 |  | BITVAL
EQF6031MO | ROOM 005 - ROOM 109 to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7031 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 9 | 13048 | 2 | 16416 | 1518 | 2 | EL6021_M178 |  | BITVAL
EQF6032MO | CUVE UDMH ZONE to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7032 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 10 | 13048 | 4 | 16416 | 1518 | 4 | EL6021_M178 |  | BITVAL
EQF6033MO | CUVE N204 ZONE to TGBT ZLV EMERGENCY CUTOFF MX DISJ. QF7033 OPEN | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | Detail bobines MX Disjoncteurs (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3006 | 11 | 13048 | 6 | 16416 | 1518 | 6 | EL6021_M178 |  | BITVAL
ONB6922 | NIVEAU BAS CHATEAU D'EAU VEGA | AL | N | RES | 1 | I |  | 6 | [10 empty] | I | [13 empty] | NOT | 1000 |  | MG74 | Moyens Generaux VEGA (MG) |  | 4 |  |  | 3007 | 0 | 13049 | 0 | 16416 | 1520 | 0 | EL6021_M178 |  | BITVAL
ONH6922 | NIVEAU HAUT CHATEAU D'EAU VEGA | AL | N | RES | 1 | I |  | 6 | [10 empty] | I | [13 empty] | NOT | 1000 |  | MG74 | Moyens Generaux VEGA (MG) |  | 4 |  |  | 3007 | 1 | 13049 | 2 | 16416 | 1520 | 2 | EL6021_M178 |  | BITVAL
EQF6502D | TGBT CAT.IIIA to TGBT ZLV SYNTHESE SD 1601-113-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3008 | 0 | 13051 | 0 | 16416 | 1524 | 0 | EL6021_M178 |  | BITVAL
EQF6702D | TGBT CAT.IIIB to TGBT ZLV SYNTHESE SD 1601-113-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3008 | 1 | 13051 | 2 | 16416 | 1524 | 2 | EL6021_M178 |  | BITVAL
EQF6537D | TD1 004 IIIA to TGBT ZLV SYNTHESE SD 1601-004-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 2 | 13051 | 4 | 16416 | 1524 | 4 | EL6021_M178 |  | BITVAL
EQF6552D | TD2 004 IIIA to TGBT ZLV SYNTHESE SD 1601-004-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 3 | 13051 | 6 | 16416 | 1524 | 6 | EL6021_M178 |  | BITVAL
EQF6737D | TD1 004 IIIB to TGBT ZLV SD DISJ. QF7737 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 4 | 13051 | 8 | 16416 | 1525 | 0 | EL6021_M178 |  | BITVAL
EQF6752D | TD2 004 IIIB to TGBT ZLV SD DISJ. QF7752 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 5 | 13051 | 10 | 16416 | 1525 | 2 | EL6021_M178 |  | BITVAL
EQF6522D | TD 013 IIIA to TGBT ZLV SYNTHESE SD 1601-013-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 6 | 13051 | 12 | 16416 | 1525 | 4 | EL6021_M178 |  | BITVAL
EQF6722D | TD 013 IIIB to TGBT ZLV SYNTHESE SD 1601-013-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 7 | 13051 | 14 | 16416 | 1525 | 6 | EL6021_M178 |  | BITVAL
EQF6567D | TD1 103 IIIA to TGBT ZLV SYNTHESE SD 1601-103-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 8 | 13052 | 0 | 16416 | 1526 | 0 | EL6021_M178 |  | BITVAL
EQF6582D | TD2 103 IIIA to TGBT ZLV SYNTHESE SD 1601-103-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 9 | 13052 | 2 | 16416 | 1526 | 2 | EL6021_M178 |  | BITVAL
EQF6597D | TD3 103 IIIA to TGBT ZLV SYNTHESE SD 1601-103-32 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 10 | 13052 | 4 | 16416 | 1526 | 4 | EL6021_M178 |  | BITVAL
EQF6612D | TD4 103 IIIA to TGBT ZLV SYNTHESE SD 1601-103-33 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 11 | 13052 | 6 | 16416 | 1526 | 6 | EL6021_M178 |  | BITVAL
EQF6667D | TD1 103 IIIB to TGBT ZLV SD DISJ. QF7667 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 12 | 13052 | 8 | 16416 | 1527 | 0 | EL6021_M178 |  | BITVAL
EQF6782D | TD2 103 IIIB to TGBT ZLV SYNTHESE SD 1601-103-35 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 13 | 13052 | 10 | 16416 | 1527 | 2 | EL6021_M178 |  | BITVAL
EQF6797D | TD3 103 IIIB to TGBT ZLV SYNTHESE SD 1601-103-36 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 14 | 13052 | 12 | 16416 | 1527 | 4 | EL6021_M178 |  | BITVAL
EQF6812D | TD4 103 IIIB to TGBT ZLV SYNTHESE SD 1601-103-37 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3008 | 15 | 13052 | 14 | 16416 | 1527 | 6 | EL6021_M178 |  | BITVAL
EQF6902D | TD III CUB to TGBT ZLV SYNTHESE SD 1601-101-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3009 | 2 | 13053 | 4 | 16416 | 1528 | 4 | EL6021_M178 |  | BITVAL
EQF6917D | TD III CUH to TGBT ZLV LEVEL 21.2m SYNTHESE SD 1607-34000-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3009 | 3 | 13053 | 6 | 16416 | 1528 | 6 | EL6021_M178 |  | BITVAL
ESA6011D | T AUX 1 UPS CUB CUH to TGBT ZLV QM7011 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3009 | 4 | 13053 | 8 | 16416 | 1529 | 0 | EL6021_M178 |  | BITVAL
ESA6012D | T AUX 1 UPS CUB CUH to TGBT ZLV QM7012 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3009 | 5 | 13053 | 10 | 16416 | 1529 | 2 | EL6021_M178 |  | BITVAL
EQF6230D | T AUX 2 UPS CUB CUH to TGBT ZLV SD DISJ. QF7030 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3009 | 6 | 13053 | 12 | 16416 | 1529 | 4 | EL6021_M178 |  | BITVAL
EQF6232D | T AUX 2 UPS CUB CUH to TGBT ZLV SD DISJ. QF7032 FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3009 | 7 | 13053 | 14 | 16416 | 1529 | 6 | EL6021_M178 |  | BITVAL
EQF6632D | TDGA IIIA to TGBT ZLV SYNTHESE SD 1602-101-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 8 | 13054 | 0 | 16416 | 1530 | 0 | EL6021_M178 |  | BITVAL
EQF6832D | TDGA IIIB to TGBT ZLV SYNTHESE SD 1602-101-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 9 | 13054 | 2 | 16416 | 1530 | 2 | EL6021_M178 |  | BITVAL
EQF6642D | TD1 21200 IIIA to TGBT ZLV SYNTHESE SD 1602-201-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 10 | 13054 | 4 | 16416 | 1530 | 4 | EL6021_M178 |  | BITVAL
EQF6842D | TD1 21200 IIIB to TGBT ZLV SYNTHESE SD 1602-201-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 11 | 13054 | 6 | 16416 | 1530 | 6 | EL6021_M178 |  | BITVAL
EQF6657D | TD1 29200 IIIA to TGBT ZLV SYNTHESE SD 1602-501-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 12 | 13054 | 8 | 16416 | 1531 | 0 | EL6021_M178 |  | BITVAL
ESA6672D | TD2 29200 IIIA to TGBT ZLV SYNTHESE SD 1602-502-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 13 | 13054 | 10 | 16416 | 1531 | 2 | EL6021_M178 |  | BITVAL
EQF6857D | TD1 29200 IIIB to TGBT ZLV SYNTHESE SD 1602-501-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 14 | 13054 | 12 | 16416 | 1531 | 4 | EL6021_M178 |  | BITVAL
EQF6872D | TD2 29200 IIIB to TGBT ZLV SYNTHESE SD 1602-502-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E70;E67 | Energie TD |  | 4 |  |  | 3009 | 15 | 13054 | 14 | 16416 | 1531 | 6 | EL6021_M178 |  | BITVAL
EQF6162D | TD LOCAL 117 to TGBT ZLV SYNTHESE SD 1601-117-20 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3010 | 4 | 13055 | 8 | 16416 | 1533 | 0 | EL6021_M178 |  | BITVAL
EQF6627D | TD1 002 IIIA to TGBT ZLV SYNTHESE SD 1601-002-30 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3010 | 5 | 13055 | 10 | 16416 | 1533 | 2 | EL6021_M178 |  | BITVAL
EQF6922D | TD1 002 IIIB to TGBT ZLV SYNTHESE SD 1601-002-31 | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E70 | Energie TD |  | 4 |  |  | 3010 | 6 | 13055 | 12 | 16416 | 1533 | 4 | EL6021_M178 |  | BITVAL
ESY6081D | TGBT ZLV ARRIVEE TM 7002 CAT.II PM810 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K10 | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3011 | 0 | 13057 | 0 | 16416 | 1536 | 0 | EL6021_M178 |  | BITVAL
ESY6082D | TGBT ZLV ARRIVEE TM 7004 CAT.I PM810 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K10 | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3011 | 1 | 13057 | 2 | 16416 | 1536 | 2 | EL6021_M178 |  | BITVAL
ESY6083D | TGBT-C ZLV ARRIVEE TM 7001 CAT.II PM810 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K10 | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3011 | 2 | 13057 | 4 | 16416 | 1536 | 4 | EL6021_M178 |  | BITVAL
ESY6084D | TGBT-C ZLV ARRIVEE TM 7003 CAT.I PM810 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K10 | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3011 | 3 | 13057 | 6 | 16416 | 1536 | 6 | EL6021_M178 |  | BITVAL
ESY6091D | TGBT CAT.IIIA PM9C Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K16 | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3012 | 0 | 13059 | 0 | 16416 | 1540 | 0 | EL6021_M178 |  | BITVAL
ESY6092D | TGBT CAT.IIIB PM9C Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K16 | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3012 | 1 | 13059 | 2 | 16416 | 1540 | 2 | EL6021_M178 |  | BITVAL
EUL6071D1 | Onduleur IIIA-1 UL7001 Internal UPS hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 0 | 13061 | 0 | 16416 | 1544 | 0 | EL6021_M178 |  | BITVAL
EGB6071D1 | Onduleur IIIA-1 UL7001 Battery usage status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 1 | 13061 | 2 | 16416 | 1544 | 2 | EL6021_M178 |  | BITVAL
EKM6071D1 | Onduleur IIIA-1 UL7001 Bypass switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 2 | 13061 | 4 | 16416 | 1544 | 4 | EL6021_M178 |  | BITVAL
EVC6071D1 | Onduleur IIIA-1 UL7001 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 3 | 13061 | 6 | 16416 | 1544 | 6 | EL6021_M178 |  | BITVAL
EUL6071D2 | Onduleur IIIA-1 UL7001 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 4 | 13061 | 8 | 16416 | 1545 | 0 | EL6021_M178 |  | BITVAL
EUL6071D3 | Onduleur IIIA-1 UL7001 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 5 | 13061 | 10 | 16416 | 1545 | 2 | EL6021_M178 |  | BITVAL
EUL6071D4 | Onduleur IIIA-1 UL7001 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 6 | 13061 | 12 | 16416 | 1545 | 4 | EL6021_M178 |  | BITVAL
EUL6071D5 | Onduleur IIIA-1 UL7001 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 7 | 13061 | 14 | 16416 | 1545 | 6 | EL6021_M178 |  | BITVAL
EUL6071D6 | Onduleur IIIA-1 UL7001 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 8 | 13062 | 0 | 16416 | 1546 | 0 | EL6021_M178 |  | BITVAL
ESY6071D1 | Onduleur IIIA-1 UL7001 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K10 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3013 | 11 | 13062 | 6 | 16416 | 1546 | 6 | EL6021_M178 |  | BITVAL
EUL6072D1 | Onduleur IIIA-2 UL7002 Internal UPS hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 0 | 13063 | 0 | 16416 | 1548 | 0 | EL6021_M178 |  | BITVAL
EGB6072D1 | Onduleur IIIA-2 UL7002 Battery usage status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 1 | 13063 | 2 | 16416 | 1548 | 2 | EL6021_M178 |  | BITVAL
EKM6072D1 | Onduleur IIIA-2 UL7002 Bypass switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 2 | 13063 | 4 | 16416 | 1548 | 4 | EL6021_M178 |  | BITVAL
EVC6072D1 | Onduleur IIIA-2 UL7002 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 3 | 13063 | 6 | 16416 | 1548 | 6 | EL6021_M178 |  | BITVAL
EUL6072D2 | Onduleur IIIA-2 UL7002 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 4 | 13063 | 8 | 16416 | 1549 | 0 | EL6021_M178 |  | BITVAL
EUL6072D3 | Onduleur IIIA-2 UL7002 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 5 | 13063 | 10 | 16416 | 1549 | 2 | EL6021_M178 |  | BITVAL
EUL6072D4 | Onduleur IIIA-2 UL7002 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 6 | 13063 | 12 | 16416 | 1549 | 4 | EL6021_M178 |  | BITVAL
EUL6072D5 | Onduleur IIIA-2 UL7002 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 7 | 13063 | 14 | 16416 | 1549 | 6 | EL6021_M178 |  | BITVAL
EUL6072D6 | Onduleur IIIA-2 UL7002 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 8 | 13064 | 0 | 16416 | 1550 | 0 | EL6021_M178 |  | BITVAL
ESY6072D1 | Onduleur IIIA-2 UL7002 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K18 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3014 | 11 | 13064 | 6 | 16416 | 1550 | 6 | EL6021_M178 |  | BITVAL
EUL6073D1 | Onduleur IIIB-1 UL7003 Internal UPS hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 0 | 13065 | 0 | 16416 | 1552 | 0 | EL6021_M178 |  | BITVAL
EGB6073D1 | Onduleur IIIB-1 UL7003 Battery usage status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 1 | 13065 | 2 | 16416 | 1552 | 2 | EL6021_M178 |  | BITVAL
EKM6073D1 | Onduleur IIIB-1 UL7003 Bypass switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 2 | 13065 | 4 | 16416 | 1552 | 4 | EL6021_M178 |  | BITVAL
EVC6073D1 | Onduleur IIIB-1 UL7003 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 3 | 13065 | 6 | 16416 | 1552 | 6 | EL6021_M178 |  | BITVAL
EUL6073D2 | Onduleur IIIB-1 UL7003 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 4 | 13065 | 8 | 16416 | 1553 | 0 | EL6021_M178 |  | BITVAL
EUL6073D3 | Onduleur IIIB-1 UL7003 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 5 | 13065 | 10 | 16416 | 1553 | 2 | EL6021_M178 |  | BITVAL
EUL6073D4 | Onduleur IIIB-1 UL7003 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 6 | 13065 | 12 | 16416 | 1553 | 4 | EL6021_M178 |  | BITVAL
EUL6073D5 | Onduleur IIIB-1 UL7003 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 7 | 13065 | 14 | 16416 | 1553 | 6 | EL6021_M178 |  | BITVAL
EUL6073D6 | Onduleur IIIB-1 UL7003 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 8 | 13066 | 0 | 16416 | 1554 | 0 | EL6021_M178 |  | BITVAL
ESY6073D1 | Onduleur IIIB-1 UL7003 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K10 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3015 | 11 | 13066 | 6 | 16416 | 1554 | 6 | EL6021_M178 |  | BITVAL
EUL6074D1 | Onduleur IIIB-2 UL7004 Internal UPS hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 0 | 13067 | 0 | 16416 | 1556 | 0 | EL6021_M178 |  | BITVAL
EGB6074D1 | Onduleur IIIB-2 UL7004 Battery usage status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 1 | 13067 | 2 | 16416 | 1556 | 2 | EL6021_M178 |  | BITVAL
EKM6074D1 | Onduleur IIIB-2 UL7004 Bypass switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 2 | 13067 | 4 | 16416 | 1556 | 4 | EL6021_M178 |  | BITVAL
EVC6074D1 | Onduleur IIIB-2 UL7004 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 3 | 13067 | 6 | 16416 | 1556 | 6 | EL6021_M178 |  | BITVAL
EUL6074D2 | Onduleur IIIB-2 UL7004 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 4 | 13067 | 8 | 16416 | 1557 | 0 | EL6021_M178 |  | BITVAL
EUL6074D3 | Onduleur IIIB-2 UL7004 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 5 | 13067 | 10 | 16416 | 1557 | 2 | EL6021_M178 |  | BITVAL
EUL6074D4 | Onduleur IIIB-2 UL7004 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 6 | 13067 | 12 | 16416 | 1557 | 4 | EL6021_M178 |  | BITVAL
EUL6074D5 | Onduleur IIIB-2 UL7004 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 7 | 13067 | 14 | 16416 | 1557 | 6 | EL6021_M178 |  | BITVAL
EUL6074D6 | Onduleur IIIB-2 UL7004 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 8 | 13068 | 0 | 16416 | 1558 | 0 | EL6021_M178 |  | BITVAL
ESY6074D1 | Onduleur IIIB-2 UL7004 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K18 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3016 | 11 | 13068 | 6 | 16416 | 1558 | 6 | EL6021_M178 |  | BITVAL
EGB6075D1 | Onduleur III CUB UL7005 Battery usage status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 0 | 13069 | 0 | 16416 | 1560 | 0 | EL6021_M178 |  | BITVAL
EGB6075D2 | Onduleur III CUB UL7005 Battery low warning | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 1 | 13069 | 2 | 16416 | 1560 | 2 | EL6021_M178 |  | BITVAL
EGB6075D3 | Onduleur III CUB UL7005 Battery replacement | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 2 | 13069 | 4 | 16416 | 1560 | 4 | EL6021_M178 |  | BITVAL
EGB6075D4 | Onduleur III CUB UL7005 Battery test status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 3 | 13069 | 6 | 16416 | 1560 | 6 | EL6021_M178 |  | BITVAL
EGB6075D5 | Onduleur III CUB UL7005 Internal battery temperature status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 4 | 13069 | 8 | 16416 | 1561 | 0 | EL6021_M178 |  | BITVAL
EGB6075D6 | Onduleur III CUB UL7005 Battery switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 5 | 13069 | 10 | 16416 | 1561 | 2 | EL6021_M178 |  | BITVAL
EKM6075D1 | Onduleur III CUB UL7005 Bypass switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 6 | 13069 | 12 | 16416 | 1561 | 4 | EL6021_M178 |  | BITVAL
EVC6075D1 | Onduleur III CUB UL7005 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 7 | 13069 | 14 | 16416 | 1561 | 6 | EL6021_M178 |  | BITVAL
EUL6075D2 | Onduleur III CUB UL7005 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 8 | 13070 | 0 | 16416 | 1562 | 0 | EL6021_M178 |  | BITVAL
EUL6075D3 | Onduleur III CUB UL7005 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 9 | 13070 | 2 | 16416 | 1562 | 2 | EL6021_M178 |  | BITVAL
EUL6075D4 | Onduleur III CUB UL7005 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 10 | 13070 | 4 | 16416 | 1562 | 4 | EL6021_M178 |  | BITVAL
EUL6075D5 | Onduleur III CUB UL7005 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 11 | 13070 | 6 | 16416 | 1562 | 6 | EL6021_M178 |  | BITVAL
EUL6075D6 | Onduleur III CUB UL7005 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 12 | 13070 | 8 | 16416 | 1563 | 0 | EL6021_M178 |  | BITVAL
ESY6075D1 | Onduleur III CUB UL7005 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K19 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3017 | 14 | 13070 | 12 | 16416 | 1563 | 4 | EL6021_M178 |  | BITVAL
EGB6076D1 | Onduleur III CUH UL7006 Battery usage status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 0 | 13071 | 0 | 16416 | 1564 | 0 | EL6021_M178 |  | BITVAL
EGB6076D2 | Onduleur III CUH UL7006 Battery low warning | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 1 | 13071 | 2 | 16416 | 1564 | 2 | EL6021_M178 |  | BITVAL
EGB6076D3 | Onduleur III CUH UL7006 Battery replacement | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 2 | 13071 | 4 | 16416 | 1564 | 4 | EL6021_M178 |  | BITVAL
EGB6076D4 | Onduleur III CUH UL7006 Battery test status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 3 | 13071 | 6 | 16416 | 1564 | 6 | EL6021_M178 |  | BITVAL
EGB6076D5 | Onduleur III CUH UL7006 Internal battery temperature status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 4 | 13071 | 8 | 16416 | 1565 | 0 | EL6021_M178 |  | BITVAL
EGB6076D6 | Onduleur III CUH UL7006 Battery switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 5 | 13071 | 10 | 16416 | 1565 | 2 | EL6021_M178 |  | BITVAL
EKM6076D1 | Onduleur III CUH UL7006 Bypass switch status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 6 | 13071 | 12 | 16416 | 1565 | 4 | EL6021_M178 |  | BITVAL
EVC6076D1 | Onduleur III CUH UL7006 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 7 | 13071 | 14 | 16416 | 1565 | 6 | EL6021_M178 |  | BITVAL
EUL6076D2 | Onduleur III CUH UL7006 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 8 | 13072 | 0 | 16416 | 1566 | 0 | EL6021_M178 |  | BITVAL
EUL6076D3 | Onduleur III CUH UL7006 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 9 | 13072 | 2 | 16416 | 1566 | 2 | EL6021_M178 |  | BITVAL
EUL6076D4 | Onduleur III CUH UL7006 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 10 | 13072 | 4 | 16416 | 1566 | 4 | EL6021_M178 |  | BITVAL
EUL6076D5 | Onduleur III CUH UL7006 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 11 | 13072 | 6 | 16416 | 1566 | 6 | EL6021_M178 |  | BITVAL
EUL6076D6 | Onduleur III CUH UL7006 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 12 | 13072 | 8 | 16416 | 1567 | 0 | EL6021_M178 |  | BITVAL
ESY6076D1 | Onduleur III CUH UL7006 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K19 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3018 | 14 | 13072 | 12 | 16416 | 1567 | 4 | EL6021_M178 |  | BITVAL
EVC6077D1 | Frequency Converter UL7007 Charger hardware fault exists | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 0 | 13073 | 0 | 16416 | 1568 | 0 | EL6021_M178 |  | BITVAL
EUL6077D1 | Frequency Converter UL7007 Inverter major fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 1 | 13073 | 2 | 16416 | 1568 | 2 | EL6021_M178 |  | BITVAL
EUL6077D2 | Frequency Converter UL7007 Inverter overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 2 | 13073 | 4 | 16416 | 1568 | 4 | EL6021_M178 |  | BITVAL
EUL6077D3 | Frequency Converter UL7007 Inverter thermal overload status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 3 | 13073 | 6 | 16416 | 1568 | 6 | EL6021_M178 |  | BITVAL
EUL6077D4 | Frequency Converter UL7007 Inverter limitation status | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 4 | 13073 | 8 | 16416 | 1569 | 0 | EL6021_M178 |  | BITVAL
EUL6077D5 | Frequency Converter UL7007 Inverter fuse fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 5 | 13073 | 10 | 16416 | 1569 | 2 | EL6021_M178 |  | BITVAL
ESY6077D1 | Frequency Converter UL7007 Modbus Communication Failure | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6115K19 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3019 | 8 | 13074 | 0 | 16416 | 1570 | 0 | EL6021_M178 |  | BITVAL
ESY6101D | TD 013 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD 1601-013-30 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 0 | 13075 | 0 | 16416 | 1572 | 0 | EL6021_M178 |  | BITVAL
ESY6102D | TD 013 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD 1601-013-31 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 1 | 13075 | 2 | 16416 | 1572 | 2 |  |  | BITVAL
ESY6103D | TD1 004 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD1 1601-004-30 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 2 | 13075 | 4 | 16416 | 1572 | 4 |  |  | BITVAL
ESY6104D | TD2 004 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD2 1601-004-32 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 3 | 13075 | 6 | 16416 | 1572 | 6 |  |  | BITVAL
ESY6105D | TD1 004 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD1 1601-004-31 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 4 | 13075 | 8 | 16416 | 1573 | 0 |  |  | BITVAL
ESY6106D | TD2 004 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD2 1601-004-34 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 5 | 13075 | 10 | 16416 | 1573 | 2 |  |  | BITVAL
ESY6107D | TD1 103 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD1 1601-103-30 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 6 | 13075 | 12 | 16416 | 1573 | 4 |  |  | BITVAL
ESY6108D | TD2 103 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD2 1601-103-32 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 7 | 13075 | 14 | 16416 | 1573 | 6 |  |  | BITVAL
ESY6109D | TD3 103 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD3 1601-103-34 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 8 | 13076 | 0 | 16416 | 1574 | 0 |  |  | BITVAL
ESY6110D | TD4 103 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD4 1601-103-36 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 9 | 13076 | 2 | 16416 | 1574 | 2 |  |  | BITVAL
ESY6111D | TD1 103 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD1 1601-103-31 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 10 | 13076 | 4 | 16416 | 1574 | 4 |  |  | BITVAL
ESY6112D | TD2 103 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD2 1601-103-33 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 11 | 13076 | 6 | 16416 | 1574 | 6 |  |  | BITVAL
ESY6113D | TD3 103 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD3 1601-103-35 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 12 | 13076 | 8 | 16416 | 1575 | 0 |  |  | BITVAL
ESY6114D | TD4 103 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD4 1601-103-37 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 13 | 13076 | 10 | 16416 | 1575 | 2 |  |  | BITVAL
ESY6115D | TD 126 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3020 | 14 | 13076 | 12 | 16416 | 1575 | 4 |  |  | BITVAL
ESY6116D | TD 126 IIIB PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3020 | 15 | 13076 | 14 | 16416 | 1575 | 6 |  |  | BITVAL
ESY6117D | TD AUX CLIM LOCAL 126 SECT.1 PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD AXIMA 1601-126-001 Sect I (E70) | Energy TD |  | 4 |  |  | 3021 | 0 | 13077 | 0 | 16416 | 1576 | 0 | EL6021_M178 |  | BITVAL
ESY6118D | TD AUX CLIM LOCAL 126 SECT.3 PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD AXIMA 1601-126-003 Sect 3 (E70) | Energy TD |  | 4 |  |  | 3021 | 1 | 13077 | 2 | 16416 | 1576 | 2 |  |  | BITVAL
ESY6119D | TD LOCAL 117 PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K17 | TD 1601-117-20 (E70) | Energy TD |  | 4 |  |  | 3021 | 2 | 13077 | 4 | 16416 | 1576 | 4 |  |  | BITVAL
ESY6120D | TD1 002 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD1 1601-002-30 CAT IIIA (E70) | Energy TD |  | 4 |  |  | 3021 | 3 | 13077 | 6 | 16416 | 1576 | 6 |  |  | BITVAL
ESY6121D | TD2 002 IIIA PM3250 Modbus Communication Failure | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 | EZC6115K16 | TD1 1601-002-31 CAT IIIB (E70) | Energy TD |  | 4 |  |  | 3021 | 4 | 13077 | 8 | 16416 | 1577 | 0 |  |  | BITVAL
VFN6002D1 | Desenfumage 002 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 0 | 13079 | 0 | 16416 | 1580 | 0 | EL6021_M178 |  | BITVAL
VFN6004D1 | Desenfumage 004 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 1 | 13079 | 2 | 16416 | 1580 | 2 |  |  | BITVAL
VFN6007D1 | Desenfumage 007 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 2 | 13079 | 4 | 16416 | 1580 | 4 |  |  | BITVAL
VFN6008D1 | Desenfumage 008 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 3 | 13079 | 6 | 16416 | 1580 | 6 |  |  | BITVAL
VFN6009D1 | Desenfumage009 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 4 | 13079 | 8 | 16416 | 1581 | 0 |  |  | BITVAL
VFN6010D1 | Desenfumage 010 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 5 | 13079 | 10 | 16416 | 1581 | 2 |  |  | BITVAL
VFN6012D1 | Desenfumage 012 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 6 | 13079 | 12 | 16416 | 1581 | 4 |  |  | BITVAL
VFN6013D1 | Desenfumage 013 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 7 | 13079 | 14 | 16416 | 1581 | 6 |  |  | BITVAL
VFN6014D1 | Desenfumage014 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 8 | 13080 | 0 | 16416 | 1582 | 0 |  |  | BITVAL
VFN6101D1 | Desenfumage 101 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 9 | 13080 | 2 | 16416 | 1582 | 2 |  |  | BITVAL
VFN6109D1 | Desenfumage 109 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 10 | 13080 | 4 | 16416 | 1582 | 4 |  |  | BITVAL
VFN6111D1 | Desenfumage 111 Interrupteur alimentation FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 11 | 13080 | 6 | 16416 | 1582 | 6 |  |  | BITVAL
VFN6112D1 | Desenfumage 112 Interrupteur alimentation FAULT | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 12 | 13080 | 8 | 16416 | 1583 | 0 |  |  | BITVAL
VFN6113D1 | Desenfumage 113 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 13 | 13080 | 10 | 16416 | 1583 | 2 |  |  | BITVAL
VFN6117D1 | Desenfumage 117 Alimentation auxiliaires FAULT (48 V) | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3022 | 14 | 13080 | 12 | 16416 | 1583 | 4 |  |  | BITVAL
EZC6160D | VEGA PLC 1D60 SUMMARY PLC FAILURE | AL | N | RES | 1 | A |  | E | [10 empty] | A | [13 empty] | NOT | 1000 |  | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 0 | 13442 | 0 | 16416 | 2306 | 0 | EL6021_M179 |  | BITVAL
EZC6160SD | VEGA PLC 1D60 SD CARD FAILURE | AL | N | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | EZC6160D | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 1 | 13442 | 2 | 16416 | 2306 | 2 | EL6021_M179 |  | BITVAL
EZC6160K2 | VEGA PLC 1D60 BAC0 POS.2 CARD FAILURE VMC LINK 1 et SEPAM LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6160D | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 2 | 13442 | 4 | 16416 | 2306 | 4 | EL6021_M179 |  | BITVAL
EZC6160K3 | VEGA PLC 1D60 BAC0 POS.3 CARD FAILURE VMC LINK 2 and CCS LINK | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6160D | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 3 | 13442 | 6 | 16416 | 2306 | 6 | EL6021_M179 |  | BITVAL
EZC6160K5 | VEGA PLC 1D60 BAC0 POS.5 CARD FAILURE | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6160D | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 5 | 13442 | 10 | 16416 | 2307 | 2 | EL6021_M179 |  | BITVAL
EZC6160K6 | VEGA PLC 1D60 BAC0 POS.6 CARD FAILURE | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6160D | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 6 | 13442 | 12 | 16416 | 2307 | 4 | EL6021_M179 |  | BITVAL
EZC6160K7 | VEGA PLC 1D60 BAC0 POS.7 CARD FAILURE | AL | N | RES | 1 | E;A | [12 empty] | E;A | [13 empty] | NOT | 1000 | EZC6160D | E72 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3000 | 7 | 13442 | 14 | 16416 | 2307 | 6 | EL6021_M179 |  | BITVAL
ESY6001D | CAT.II 1D60 TO TGBT-C ZLV (1D61) COM. SEPAM FAILURE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6160K2 | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 3001 | 0 | 13444 | 0 | 16416 | 2310 | 0 | EL6021_M179 |  | BITVAL
ESY6002D | CAT.II 1D60 TO TGBT ZLV (1D61) COM. SEPAM FAILURE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6160K2 | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 3001 | 1 | 13444 | 2 | 16416 | 2310 | 2 | EL6021_M179 |  | BITVAL
ESY6003D | CAT.I 1D60 TO TGBT-C ZLV (1D61) COM. SEPAM FAILURE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6160K2 | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 3001 | 2 | 13444 | 4 | 16416 | 2310 | 4 | EL6021_M179 |  | BITVAL
ESY6004D | CAT.I 1D60 TO TGBT ZLV (1D61) COM. SEPAM FAILURE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6160K2 | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 3001 | 3 | 13444 | 6 | 16416 | 2310 | 6 | EL6021_M179 |  | BITVAL
ESY6142D | CAT.I 1D60 TO 1D42 COM. SEPAM FAILURE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6160K2 | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 3001 | 4 | 13444 | 8 | 16416 | 2311 | 0 | EL6021_M179 |  | BITVAL
ESY6242D | CAT.II 1D60 TO 1D42 COM. SEPAM FAILURE | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 | EZC6160K2 | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 3001 | 5 | 13444 | 10 | 16416 | 2311 | 2 | EL6021_M179 |  | BITVAL
EQM6001O | POSITION IM CAT.I 1D60 Disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 0 | 13446 | 0 | 16416 | 2314 | 0 | EL6021_M179 |  | BITVAL
EQM6002O | POSITION IM CAT.II 1D60 Disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 1 | 13446 | 2 | 16416 | 2314 | 2 | EL6021_M179 |  | BITVAL
EQD6142O | CAT.I 1D60 TO 1D42 Circuit breaker position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 2 | 13446 | 4 | 16416 | 2314 | 4 | EL6021_M179 |  | BITVAL
EQD6242O | CAT.II 1D60 TO 1D42 Circuit breaker position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 3 | 13446 | 6 | 16416 | 2314 | 6 | EL6021_M179 |  | BITVAL
EQL6142O | CAT.I 1D60 TO 1D42 Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 4 | 13446 | 8 | 16416 | 2315 | 0 | EL6021_M179 |  | BITVAL
EQL6242O | CAT.II 1D60 TO 1D42 Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 5 | 13446 | 10 | 16416 | 2315 | 2 | EL6021_M179 |  | BITVAL
EQD6001O | CAT.II 1D60 TO TGBT-C ZLV (1D61) Circuit breaker position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 6 | 13446 | 12 | 16416 | 2315 | 4 | EL6021_M179 |  | BITVAL
EQD6002O | CAT.II 1D60 TO TGBT ZLV (1D61) Circuit breaker position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 7 | 13446 | 14 | 16416 | 2315 | 6 | EL6021_M179 |  | BITVAL
EQD6003O | CAT.I 1D60 TO TGBT-C ZLV (1D61) Circuit breaker position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 8 | 13447 | 0 | 16416 | 2316 | 0 | EL6021_M179 |  | BITVAL
EQD6004O | CAT.I 1D60 TO TGBT ZLV (1D61) Circuit breaker position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 9 | 13447 | 2 | 16416 | 2316 | 2 | EL6021_M179 |  | BITVAL
EQL6001O | CAT.II 1D60 TO TGBT-C ZLV (1D61) Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 10 | 13447 | 4 | 16416 | 2316 | 4 | EL6021_M179 |  | BITVAL
EQL6002O | CAT.II 1D60 TO TGBT ZLV (1D61) Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 11 | 13447 | 6 | 16416 | 2316 | 6 | EL6021_M179 |  | BITVAL
EQL6003O | CAT.I 1D60 TO TGBT-C ZLV (1D61) Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 12 | 13447 | 8 | 16416 | 2317 | 0 | EL6021_M179 |  | BITVAL
EQL6004O | CAT.I 1D60 TO TGBT ZLV (1D61) Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 13 | 13447 | 10 | 16416 | 2317 | 2 | EL6021_M179 |  | BITVAL
EQL6160O | CAT.I CM 1D60 Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 14 | 13447 | 12 | 16416 | 2317 | 4 | EL6021_M179 |  | BITVAL
EQL6260O | CAT.II CM D60 Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3002 | 15 | 13447 | 14 | 16416 | 2317 | 6 | EL6021_M179 |  | BITVAL
EQL6005O | CAT.II QM 1D60 Line disconnector position | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3003 | 0 | 13448 | 0 | 16416 | 2318 | 0 | EL6021_M179 |  | BITVAL
ETV6005D | CAT.II QM 1D60 Blown fuse | AL | N | RES | 1 | E | [12 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3003 | 1 | 13448 | 2 | 16416 | 2318 | 2 | EL6021_M179 |  | BITVAL
ETH6005 | CAT2 TM7005 : Temperature auxiliary transformer fault | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E61;E62;E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3003 | 2 | 13448 | 4 | 16416 | 2318 | 4 | EL6021_M179 |  | BITVAL
ESY6000D | POSTE 1D60 CONFIGURATION FAULT | AL | N | RES | 1 | E |  | E | [10 empty] | E | [13 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 3003 | 3 | 13448 | 6 | 16416 | 2318 | 6 | EL6021_M179 |  | BITVAL
CPP6001D | VEGA BUNKER PLC : CHILLER 1 HOT WATER PUMP M01 (PRIMARY) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | GGF6012DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 0 | 13752 | 0 | 16416 | 2926 | 0 | EL6021_M180 |  | BITVAL
GPP6001D | VEGA BUNKER PLC : CHILLER 1 COLD WATER PUMP M01 (PRIMARY) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | GGF6012DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 1 | 13752 | 2 | 16416 | 2926 | 2 | EL6021_M180 |  | BITVAL
CPP6002D | VEGA BUNKER PLC : CHILLER 2 HOT WATER PUMP M02 (PRIMARY) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | GGF6012DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 2 | 13752 | 4 | 16416 | 2926 | 4 | EL6021_M180 |  | BITVAL
GPP6002D | VEGA BUNKER PLC : CHILLER 2 COLD WATER PUMP M02 (PRIMARY) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | GGF6012DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 3 | 13752 | 6 | 16416 | 2926 | 6 | EL6021_M180 |  | BITVAL
GCP6001D | VEGA BUNKER PLC : CHILLER 1 DEFAULT SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | GGF6012DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 4 | 13752 | 8 | 16416 | 2927 | 0 | EL6021_M180 |  | BITVAL
GCP6002D | VEGA BUNKER PLC : CHILLER 2 DEFAULT SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | GGF6012DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 5 | 13752 | 10 | 16416 | 2927 | 2 | EL6021_M180 |  | BITVAL
GCP6003D | VEGA BUNKER PLC : CHILLER 3 DEFAULT SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | GGF6003DC | HVAC03 | HVAC |  | 6 |  |  | 3000 | 6 | 13752 | 12 | 16416 | 2927 | 4 | EL6021_M180 |  | BITVAL
GPP6004D1 | VEGA BUNKER PLC : COLD WATER PUMP M04 (BUNKER) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3000 | 7 | 13752 | 14 | 16416 | 2927 | 6 | EL6021_M180 |  | BITVAL
GPP6004DI1 | VEGA BUNKER PLC : COLD WATER PUMP M04 (BUNKER) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3000 | 8 | 13753 | 0 | 16416 | 2928 | 0 | EL6021_M180 |  | BITVAL
GPP6001D2 | VEGA BUNKER PLC : COLD WATER PUMP P01 (GANTRY) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3000 | 9 | 13753 | 2 | 16416 | 2928 | 2 | EL6021_M180 |  | BITVAL
GPP6001DI2 | VEGA BUNKER PLC : COLD WATER PUMP P01 (GANTRY) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3000 | 10 | 13753 | 4 | 16416 | 2928 | 4 | EL6021_M180 |  | BITVAL
CPP6004D3 | VEGA BUNKER PLC : HOT WATER PUMP M04 (BUNKER/GANTRY) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3000 | 11 | 13753 | 6 | 16416 | 2928 | 6 | EL6021_M180 |  | BITVAL
CPP6004DI3 | VEGA BUNKER PLC : HOT WATER PUMP M04 (BUNKER/GANTRY) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3000 | 12 | 13753 | 8 | 16416 | 2929 | 0 | EL6021_M180 |  | BITVAL
VRP6127D1 | VEGA BUNKER PLC : LOCAL FRESH AIR MOTORISED DAMPER 127.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3000 | 13 | 13753 | 10 | 16416 | 2929 | 2 | EL6021_M180 |  | BITVAL
VRP6118D3 | VEGA BUNKER PLC : FRESH AIR MOTORISED DAMPER 118.3 (CTA 1) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3000 | 14 | 13753 | 12 | 16416 | 2929 | 4 | EL6021_M180 |  | BITVAL
VRP6118D4 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 118.4 (CTA 1) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04;HVAC05;HVAC06 | HVAC |  | 6 |  |  | 3000 | 15 | 13753 | 14 | 16416 | 2929 | 6 | EL6021_M180 |  | BITVAL
VCT6001D | VEGA BUNKER PLC : FAN CTA M01 DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 0 | 13754 | 0 | 16416 | 2930 | 0 | EL6021_M180 |  | BITVAL
VCT6001DI | VEGA BUNKER PLC : FAN CTA M01 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 1 | 13754 | 2 | 16416 | 2930 | 2 | EL6021_M180 |  | BITVAL
VCT6001DF | VEGA BUNKER PLC : FAN CTA M01 FILTER DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 2 | 13754 | 4 | 16416 | 2930 | 4 | EL6021_M180 |  | BITVAL
VCT6001DR | VEGA BUNKER PLC : FAN CTA M01 DEW POINT DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 3 | 13754 | 6 | 16416 | 2930 | 6 | EL6021_M180 |  | BITVAL
GPP6045DP1 | VEGA BUNKER PLC : COLD WATER PUMP M04/M05 (BUNKER) PRESSURE DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3001 | 4 | 13754 | 8 | 16416 | 2931 | 0 | EL6021_M180 |  | BITVAL
GPP6012DP3 | VEGA BUNKER PLC : COLD WATER PUMP P01/P02 (GANTRY) PRESSURE DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3001 | 5 | 13754 | 10 | 16416 | 2931 | 2 | EL6021_M180 |  | BITVAL
CPP6045DP3 | VEGA BUNKER PLC : HOT WATER PUMP M04/M05 (BUNKER/GANTRY) PRESSURE DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3001 | 6 | 13754 | 12 | 16416 | 2931 | 4 | EL6021_M180 |  | BITVAL
VAE6126D400 | VEGA BUNKER PLC : POWER SUPPLY 400V DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 6 |  |  | 3001 | 7 | 13754 | 14 | 16416 | 2931 | 6 | EL6021_M180 |  | BITVAL
VAE6126D3 | VEGA BUNKER PLC : POWER SUPPLY CAT 3 DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 6 |  |  | 3001 | 8 | 13755 | 0 | 16416 | 2932 | 0 | EL6021_M180 |  | BITVAL
VAE6126D24 | VEGA BUNKER PLC : POWER SUPPLY 24V DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 6 |  |  | 3001 | 9 | 13755 | 2 | 16416 | 2932 | 2 | EL6021_M180 |  | BITVAL
VAE6126D48 | VEGA BUNKER PLC : POWER SUPPLY 48V DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 6 |  |  | 3001 | 10 | 13755 | 4 | 16416 | 2932 | 4 | EL6021_M180 |  | BITVAL
VRP6127D2 | VEGA BUNKER PLC : DISTANT FRESH AIR MOTORISED DAMPER 127.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 11 | 13755 | 6 | 16416 | 2932 | 6 | EL6021_M180 |  | BITVAL
VFN6003D | VEGA BUNKER PLC : FRESH AIR FAN M03 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 12 | 13755 | 8 | 16416 | 2933 | 0 | EL6021_M180 |  | BITVAL
VFN6003DI | VEGA BUNKER PLC : FRESH AIR FAN M03 DISCORDANCE | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3001 | 13 | 13755 | 10 | 16416 | 2933 | 2 | EL6021_M180 |  | BITVAL
GRT6118D | VEGA BUNKER PLC : COLD WATER EXPANSION TANK DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3001 | 14 | 13755 | 12 | 16416 | 2933 | 4 | EL6021_M180 |  | BITVAL
CRT6118D | VEGA BUNKER PLC : HOT WATER EXPANSION TANK DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3001 | 15 | 13755 | 14 | 16416 | 2933 | 6 | EL6021_M180 |  | BITVAL
VFN6000D | VEGA BUNKER PLC : FAN EXTRACTOR SANITATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3002 | 0 | 13756 | 0 | 16416 | 2934 | 0 | EL6021_M180 |  | BITVAL
VFN6000DI | VEGA BUNKER PLC : FAN EXTRACTOR SANITATION DISCORDANCE | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3002 | 1 | 13756 | 2 | 16416 | 2934 | 2 | EL6021_M180 |  | BITVAL
VRP6004D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 004.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 2 | 13756 | 4 | 16416 | 2934 | 4 | EL6021_M180 |  | BITVAL
VRP6007D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 007.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 3 | 13756 | 6 | 16416 | 2934 | 6 | EL6021_M180 |  | BITVAL
VRP6008D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 008.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 4 | 13756 | 8 | 16416 | 2935 | 0 | EL6021_M180 |  | BITVAL
VRP6009D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 009.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 5 | 13756 | 10 | 16416 | 2935 | 2 | EL6021_M180 |  | BITVAL
VRP6013D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 013.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 6 | 13756 | 12 | 16416 | 2935 | 4 | EL6021_M180 |  | BITVAL
VRP6101D11 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 101.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 7 | 13756 | 14 | 16416 | 2935 | 6 | EL6021_M180 |  | BITVAL
VRP6103D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 103.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 8 | 13757 | 0 | 16416 | 2936 | 0 | EL6021_M180 |  | BITVAL
VRP6111D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 111.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 9 | 13757 | 2 | 16416 | 2936 | 2 | EL6021_M180 |  | BITVAL
VRP6112D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 112.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 10 | 13757 | 4 | 16416 | 2936 | 4 | EL6021_M180 |  | BITVAL
VRP6113D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 113.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 11 | 13757 | 6 | 16416 | 2936 | 6 | EL6021_M180 |  | BITVAL
VRP6115D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 115.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 12 | 13757 | 8 | 16416 | 2937 | 0 | EL6021_M180 |  | BITVAL
VRP6116D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 116.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3002 | 13 | 13757 | 10 | 16416 | 2937 | 2 | EL6021_M180 |  | BITVAL
VRP6106D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 106.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3002 | 14 | 13757 | 12 | 16416 | 2937 | 4 | EL6021_M180 |  | BITVAL
VRP6004D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 004.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3002 | 15 | 13757 | 14 | 16416 | 2937 | 6 | EL6021_M180 |  | BITVAL
VRP6007D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 007.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 0 | 13758 | 0 | 16416 | 2938 | 0 | EL6021_M180 |  | BITVAL
VRP6008D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 008.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 1 | 13758 | 2 | 16416 | 2938 | 2 | EL6021_M180 |  | BITVAL
VRP6009D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 009.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 2 | 13758 | 4 | 16416 | 2938 | 4 | EL6021_M180 |  | BITVAL
VRP6213D | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 002.2 (ROOMS 002 AND 013) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 3 | 13758 | 6 | 16416 | 2938 | 6 | EL6021_M180 |  | BITVAL
VRP6101D12 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 101.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 4 | 13758 | 8 | 16416 | 2939 | 0 | EL6021_M180 |  | BITVAL
VRP6103D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 103.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 5 | 13758 | 10 | 16416 | 2939 | 2 | EL6021_M180 |  | BITVAL
VRP6111D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 111.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 6 | 13758 | 12 | 16416 | 2939 | 4 | EL6021_M180 |  | BITVAL
VRP6112D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 112.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 7 | 13758 | 14 | 16416 | 2939 | 6 | EL6021_M180 |  | BITVAL
VRP6113D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 113.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 8 | 13759 | 0 | 16416 | 2940 | 0 | EL6021_M180 |  | BITVAL
VRP6115D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 115.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3003 | 9 | 13759 | 2 | 16416 | 2940 | 2 | EL6021_M180 |  | BITVAL
VRP6116D2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 116.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3003 | 10 | 13759 | 4 | 16416 | 2940 | 4 | EL6021_M180 |  | BITVAL
VRU6004D | VEGA BUNKER PLC : N2 INERTING ROOM 004 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3003 | 15 | 13759 | 14 | 16416 | 2941 | 6 | EL6021_M180 |  | BITVAL
VRU6007D | VEGA BUNKER PLC : N2 INERTING ROOM 007 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 0 | 13760 | 0 | 16416 | 2942 | 0 | EL6021_M180 |  | BITVAL
VRU6008D | VEGA BUNKER PLC : N2 INERTING ROOM 008 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 1 | 13760 | 2 | 16416 | 2942 | 2 | EL6021_M180 |  | BITVAL
VRU6009D | VEGA BUNKER PLC : N2 INERTING ROOM 009 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 2 | 13760 | 4 | 16416 | 2942 | 4 | EL6021_M180 |  | BITVAL
VRU6213D | VEGA BUNKER PLC : N2 INERTING ROOMS 002 AND 013 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 3 | 13760 | 6 | 16416 | 2942 | 6 | EL6021_M180 |  | BITVAL
VRU6101D1 | VEGA BUNKER PLC : N2 INERTING ROOM 101 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 4 | 13760 | 8 | 16416 | 2943 | 0 | EL6021_M180 |  | BITVAL
VRU6103D | VEGA BUNKER PLC : N2 INERTING ROOM 103 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 5 | 13760 | 10 | 16416 | 2943 | 2 | EL6021_M180 |  | BITVAL
VRU6111D | VEGA BUNKER PLC : N2 INERTING ROOM 111 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 6 | 13760 | 12 | 16416 | 2943 | 4 | EL6021_M180 |  | BITVAL
VRU6112D | VEGA BUNKER PLC : N2 INERTING ROOM 112 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 7 | 13760 | 14 | 16416 | 2943 | 6 | EL6021_M180 |  | BITVAL
VRU6113D | VEGA BUNKER PLC : N2 INERTING ROOM 113 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 8 | 13761 | 0 | 16416 | 2944 | 0 | EL6021_M180 |  | BITVAL
VRU6115D | VEGA BUNKER PLC : N2 INERTING ROOM 115 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3004 | 9 | 13761 | 2 | 16416 | 2944 | 2 | EL6021_M180 |  | BITVAL
VRU6116D | VEGA BUNKER PLC : N2 INERTING ROOM 116 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06;HVAC11 | HVAC |  | 6 |  |  | 3004 | 10 | 13761 | 4 | 16416 | 2944 | 4 | EL6021_M180 |  | BITVAL
CVM6001D | VEGA BUNKER PLC : HOT WATER VALVE CHILLER 1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3004 | 11 | 13761 | 6 | 16416 | 2944 | 6 | EL6021_M180 |  | BITVAL
CVM6002D | VEGA BUNKER PLC : HOT WATER VALVE CHILLER 2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3004 | 12 | 13761 | 8 | 16416 | 2945 | 0 | EL6021_M180 |  | BITVAL
CVM6003D | VEGA BUNKER PLC : HOT WATER VALVE CHILLER 3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3004 | 13 | 13761 | 10 | 16416 | 2945 | 2 | EL6021_M180 |  | BITVAL
GFF6118D | VEGA BUNKER PLC : FREON LEAKAGE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3004 | 14 | 13761 | 12 | 16416 | 2945 | 4 | EL6021_M180 |  | BITVAL
VVV6126DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 126.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3004 | 15 | 13761 | 14 | 16416 | 2945 | 6 | EL6021_M180 |  | BITVAL
VVV6118DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 0 | 13762 | 0 | 16416 | 2946 | 0 | EL6021_M180 |  | BITVAL
VVV6118DT4 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.4 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 1 | 13762 | 2 | 16416 | 2946 | 2 | EL6021_M180 |  | BITVAL
VVV6118DT5 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.5 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 2 | 13762 | 4 | 16416 | 2946 | 4 | EL6021_M180 |  | BITVAL
VVV6122DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 122.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3005 | 3 | 13762 | 6 | 16416 | 2946 | 6 | EL6021_M180 |  | BITVAL
VVV6121DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 121.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3005 | 4 | 13762 | 8 | 16416 | 2947 | 0 | EL6021_M180 |  | BITVAL
VVV6121DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 121.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3005 | 5 | 13762 | 10 | 16416 | 2947 | 2 | EL6021_M180 |  | BITVAL
VVV6120DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 120.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3005 | 6 | 13762 | 12 | 16416 | 2947 | 4 | EL6021_M180 |  | BITVAL
VVV6115DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 7 | 13762 | 14 | 16416 | 2947 | 6 | EL6021_M180 |  | BITVAL
VVV6115DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 8 | 13763 | 0 | 16416 | 2948 | 0 | EL6021_M180 |  | BITVAL
VVV6117DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 117.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 9 | 13763 | 2 | 16416 | 2948 | 2 | EL6021_M180 |  | BITVAL
VVV6108DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 108.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 10 | 13763 | 4 | 16416 | 2948 | 4 | EL6021_M180 |  | BITVAL
VVV6106DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 11 | 13763 | 6 | 16416 | 2948 | 6 | EL6021_M180 |  | BITVAL
VVV6106DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3005 | 12 | 13763 | 8 | 16416 | 2949 | 0 | EL6021_M180 |  | BITVAL
VVV6105DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 105.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3005 | 13 | 13763 | 10 | 16416 | 2949 | 2 | EL6021_M180 |  | BITVAL
VVV6012DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 012.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3005 | 14 | 13763 | 12 | 16416 | 2949 | 4 | EL6021_M180 |  | BITVAL
VVV6006DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 006.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3005 | 15 | 13763 | 14 | 16416 | 2949 | 6 | EL6021_M180 |  | BITVAL
VVV6004DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 004.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3006 | 0 | 13764 | 0 | 16416 | 2950 | 0 | EL6021_M180 |  | BITVAL
VVV6002DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 002.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC07;HVAC18 | HVAC |  | 6 |  |  | 3006 | 1 | 13764 | 2 | 16416 | 2950 | 2 | EL6021_M180 |  | BITVAL
VVV6100DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 100.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3006 | 2 | 13764 | 4 | 16416 | 2950 | 4 | EL6021_M180 |  | BITVAL
VCT6001DT | VEGA BUNKER PLC : FAN CTA M01 PULSE TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3006 | 3 | 13764 | 6 | 16416 | 2950 | 6 | EL6021_M180 |  | BITVAL
GPP6045DT1 | VEGA BUNKER PLC : COLD WATER M04/M05 TEMP DEF. | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03;HVAC04 | HVAC |  | 6 |  |  | 3006 | 4 | 13764 | 8 | 16416 | 2951 | 0 | EL6021_M180 |  | BITVAL
GPP6012DT2 | VEGA BUNKER PLC : COLD WATER P01/P02 (GANTRY) TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03;HVAC13;HVAC14 | HVAC |  | 6 |  |  | 3006 | 5 | 13764 | 10 | 16416 | 2951 | 2 | EL6021_M180 |  | BITVAL
CPP6045DT3 | VEGA BUNKER PLC : HOT WATER M04/M05 (BUNKER/GANTRY) TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3006 | 6 | 13764 | 12 | 16416 | 2951 | 4 | EL6021_M180 |  | BITVAL
GCP6001DI | VEGA BUNKER PLC : CHILLER 1 DISCORDANCE | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3006 | 7 | 13764 | 14 | 16416 | 2951 | 6 | EL6021_M180 |  | BITVAL
GCP6002DI | VEGA BUNKER PLC : CHILLER 2 DISCORDANCE | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3006 | 8 | 13765 | 0 | 16416 | 2952 | 0 | EL6021_M180 |  | BITVAL
GCP6003DI | VEGA BUNKER PLC : CHILLER 3 DISCORDANCE | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3006 | 9 | 13765 | 2 | 16416 | 2952 | 2 | EL6021_M180 |  | BITVAL
VCN6007DT1 | VEGA BUNKER PLC : AC CABINET (STULZ) 007.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6007DC1 | HVAC07 | HVAC |  | 6 |  |  | 3006 | 10 | 13765 | 4 | 16416 | 2952 | 4 | EL6021_M180 |  | BITVAL
VCN6013DT1 | VEGA BUNKER PLC : AC CABINET (STULZ) 013.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6013DC1 | HVAC07 | HVAC |  | 6 |  |  | 3006 | 11 | 13765 | 6 | 16416 | 2952 | 6 | EL6021_M180 |  | BITVAL
VCN6101DT1 | VEGA BUNKER PLC : AC CABINET (STULZ) 101.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6101DC1 | HVAC07 | HVAC |  | 6 |  |  | 3006 | 12 | 13765 | 8 | 16416 | 2953 | 0 | EL6021_M180 |  | BITVAL
VCN6103DT1 | VEGA BUNKER PLC : AC CABINET (STULZ) 103.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6103DC1 | HVAC07 | HVAC |  | 6 |  |  | 3006 | 13 | 13765 | 10 | 16416 | 2953 | 2 | EL6021_M180 |  | BITVAL
VCN6113DT1 | VEGA BUNKER PLC : AC CABINET (STULZ) 113.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6113DC1 | HVAC08 | HVAC |  | 6 |  |  | 3006 | 14 | 13765 | 12 | 16416 | 2953 | 4 | EL6021_M180 |  | BITVAL
VCN6116DT1 | VEGA BUNKER PLC : AC CABINET (STULZ) 116.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6116DC1 | HVAC08 | HVAC |  | 6 |  |  | 3006 | 15 | 13765 | 14 | 16416 | 2953 | 6 | EL6021_M180 |  | BITVAL
VCN6007DC1 | VEGA BUNKER PLC : AC CABINET (STULZ) 007.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC07 | HVAC |  | 6 |  |  | 3007 | 0 | 13766 | 0 | 16416 | 2954 | 0 | EL6021_M180 |  | BITVAL
VCN6013DC1 | VEGA BUNKER PLC : AC CABINET (STULZ) 013.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC07 | HVAC |  | 6 |  |  | 3007 | 1 | 13766 | 2 | 16416 | 2954 | 2 | EL6021_M180 |  | BITVAL
VCN6101DC1 | VEGA BUNKER PLC : AC CABINET (STULZ) 101.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC07 | HVAC |  | 6 |  |  | 3007 | 2 | 13766 | 4 | 16416 | 2954 | 4 | EL6021_M180 |  | BITVAL
VCN6103DC1 | VEGA BUNKER PLC : AC CABINET (STULZ) 103.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC07 | HVAC |  | 6 |  |  | 3007 | 3 | 13766 | 6 | 16416 | 2954 | 6 | EL6021_M180 |  | BITVAL
VCN6113DC1 | VEGA BUNKER PLC : AC CABINET (STULZ) 113.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC08 | HVAC |  | 6 |  |  | 3007 | 4 | 13766 | 8 | 16416 | 2955 | 0 | EL6021_M180 |  | BITVAL
VCN6116DC1 | VEGA BUNKER PLC : AC CABINET (STULZ) 116.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC08 | HVAC |  | 6 |  |  | 3007 | 5 | 13766 | 10 | 16416 | 2955 | 2 | EL6021_M180 |  | BITVAL
VCF6004D1 | VEGA BUNKER PLC : FIRE DAMPER 004.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC10 | HVAC |  | 6 |  |  | 3007 | 6 | 13766 | 12 | 16416 | 2955 | 4 | EL6021_M180 |  | BITVAL
VCF6007D1 | VEGA BUNKER PLC : FIRE DAMPER 007.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC10 | HVAC |  | 6 |  |  | 3007 | 7 | 13766 | 14 | 16416 | 2955 | 6 | EL6021_M180 |  | BITVAL
VCF6007D2 | VEGA BUNKER PLC : FIRE DAMPER 007.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 8 | 13767 | 0 | 16416 | 2956 | 0 | EL6021_M180 |  | BITVAL
VCF6008D1 | VEGA BUNKER PLC : FIRE DAMPER 008.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 9 | 13767 | 2 | 16416 | 2956 | 2 | EL6021_M180 |  | BITVAL
VCF6008D2 | VEGA BUNKER PLC : FIRE DAMPER 008.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 10 | 13767 | 4 | 16416 | 2956 | 4 | EL6021_M180 |  | BITVAL
VCF6009D1 | VEGA BUNKER PLC : FIRE DAMPER 009.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 11 | 13767 | 6 | 16416 | 2956 | 6 | EL6021_M180 |  | BITVAL
VCF6013D1 | VEGA BUNKER PLC : FIRE DAMPER 013.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 12 | 13767 | 8 | 16416 | 2957 | 0 | EL6021_M180 |  | BITVAL
VCF6013D2 | VEGA BUNKER PLC : FIRE DAMPER 013.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 13 | 13767 | 10 | 16416 | 2957 | 2 | EL6021_M180 |  | BITVAL
VCF6013D3 | VEGA BUNKER PLC : FIRE DAMPER 013.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 14 | 13767 | 12 | 16416 | 2957 | 4 | EL6021_M180 |  | BITVAL
VCF6103D1 | VEGA BUNKER PLC : FIRE DAMPER 103.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3007 | 15 | 13767 | 14 | 16416 | 2957 | 6 | EL6021_M180 |  | BITVAL
VCF6103D2 | VEGA BUNKER PLC : FIRE DAMPER 103.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 0 | 13768 | 0 | 16416 | 2958 | 0 | EL6021_M180 |  | BITVAL
VCF6106D1 | VEGA BUNKER PLC : FIRE DAMPER 106.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 1 | 13768 | 2 | 16416 | 2958 | 2 | EL6021_M180 |  | BITVAL
VCF6111D1 | VEGA BUNKER PLC : FIRE DAMPER 111.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 2 | 13768 | 4 | 16416 | 2958 | 4 | EL6021_M180 |  | BITVAL
VCF6111D2 | VEGA BUNKER PLC : FIRE DAMPER 111.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 3 | 13768 | 6 | 16416 | 2958 | 6 | EL6021_M180 |  | BITVAL
VZN6701D | VEGA GANTRY PLC : N2O4 LEAKAGE DEFAULT | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 3 | 14124 | 6 | 16416 | 3670 | 6 | EL6021_M181 |  | BITVAL
VZU6601D | VEGA GANTRY PLC : UDMH LEAKAGE DEFAULT | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 4 | 14124 | 8 | 16416 | 3671 | 0 | EL6021_M181 |  | BITVAL
VCF6112D1 | VEGA BUNKER PLC : FIRE DAMPER 112.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 4 | 13768 | 8 | 16416 | 2959 | 0 | EL6021_M180 |  | BITVAL
VCF6113D1 | VEGA BUNKER PLC : FIRE DAMPER 113.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 5 | 13768 | 10 | 16416 | 2959 | 2 | EL6021_M180 |  | BITVAL
VCF6115D1 | VEGA BUNKER PLC : FIRE DAMPER 115.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 6 | 13768 | 12 | 16416 | 2959 | 4 | EL6021_M180 |  | BITVAL
VCF6115D2 | VEGA BUNKER PLC : FIRE DAMPER 115.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 7 | 13768 | 14 | 16416 | 2959 | 6 | EL6021_M180 |  | BITVAL
VCF6115D3 | VEGA BUNKER PLC : FIRE DAMPER 115.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 8 | 13769 | 0 | 16416 | 2960 | 0 | EL6021_M180 |  | BITVAL
VCF6116D1 | VEGA BUNKER PLC : FIRE DAMPER 116.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 9 | 13769 | 2 | 16416 | 2960 | 2 | EL6021_M180 |  | BITVAL
VCF6118D1 | VEGA BUNKER PLC : FIRE DAMPER 118.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 10 | 13769 | 4 | 16416 | 2960 | 4 | EL6021_M180 |  | BITVAL
VCF6118D2 | VEGA BUNKER PLC : FIRE DAMPER 118.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3008 | 11 | 13769 | 6 | 16416 | 2960 | 6 | EL6021_M180 |  | BITVAL
VSY6126W1 | VEGA BUNKER PLC : LEVEL 1 ALARM SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3008 | 12 | 13769 | 8 | 16416 | 2961 | 0 | EL6021_M180 |  | BITVAL
VSY6126W2 | VEGA BUNKER PLC : LEVEL 2 ALARM SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3008 | 13 | 13769 | 10 | 16416 | 2961 | 2 | EL6021_M180 |  | BITVAL
VCN6002D1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.1 GENERAL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6002DC1 | HVAC07 | HVAC |  | 6 |  |  | 3008 | 14 | 13769 | 12 | 16416 | 2961 | 4 | EL6021_M180 |  | BITVAL
VCN6002DT1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6002DC1 | HVAC07 | HVAC |  | 6 |  |  | 3008 | 15 | 13769 | 14 | 16416 | 2961 | 6 | EL6021_M180 |  | BITVAL
VCN6002DC1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC07 | HVAC |  | 6 |  |  | 3009 | 0 | 13770 | 0 | 16416 | 2962 | 0 | EL6021_M180 |  | BITVAL
VCN6004D1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.1 GENERAL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6004DC1 | HVAC07 | HVAC |  | 6 |  |  | 3009 | 1 | 13770 | 2 | 16416 | 2962 | 2 | EL6021_M180 |  | BITVAL
VCN6004DT1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6004DC1 | HVAC07 | HVAC |  | 6 |  |  | 3009 | 2 | 13770 | 4 | 16416 | 2962 | 4 | EL6021_M180 |  | BITVAL
VCN6004DC1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.1 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC07 | HVAC |  | 6 |  |  | 3009 | 3 | 13770 | 6 | 16416 | 2962 | 6 | EL6021_M180 |  | BITVAL
VUM6126V | VEGA BUNKER PLC : LOCKING OF VMC COMMANDS BY LOCAL HVAC SUPERVISION | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3009 | 4 | 13770 | 8 | 16416 | 2963 | 0 | EL6021_M180 |  | BITVAL
GPP6002DC2 | VEGA BUNKER PLC : COLD WATER PUMP P02 (GANTRY) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01; HVAC03 | HVAC |  | 6 |  |  | 3009 | 6 | 13770 | 12 | 16416 | 2963 | 4 | EL6021_M180 |  | BITVAL
GPP6005DC1 | VEGA BUNKER PLC : COLD WATER PUMP M05 (BUNKER) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01; HVAC03 | HVAC |  | 6 |  |  | 3009 | 7 | 13770 | 14 | 16416 | 2963 | 6 | EL6021_M180 |  | BITVAL
VVU6106D | VEGA BUNKER PLC : INTERNAL HVAC (ROOM 106 : RELOCATION) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3010 | 0 | 13772 | 0 | 16416 | 2966 | 0 | EL6021_M180 |  | BITVAL
VVU6127D | VEGA BUNKER PLC : DISTANT FRESH AIR DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3010 | 1 | 13772 | 2 | 16416 | 2966 | 2 | EL6021_M180 |  | BITVAL
VVU6126D | VEGA BUNKER PLC : INTERNAL HVAC DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3010 | 2 | 13772 | 4 | 16416 | 2966 | 4 | EL6021_M180 |  | BITVAL
GPP6001DC2 | VEGA BUNKER PLC : COLD WATER PUMP P01 (GANTRY) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01; HVAC03 | HVAC |  | 6 |  |  | 3010 | 4 | 13772 | 8 | 16416 | 2967 | 0 | EL6021_M180 |  | BITVAL
GPP6004DC1 | VEGA BUNKER PLC : COLD WATER PUMP M04 (BUNKER) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01; HVAC03 | HVAC |  | 6 |  |  | 3010 | 5 | 13772 | 10 | 16416 | 2967 | 2 | EL6021_M180 |  | BITVAL
CPP6003D | VEGA BUNKER PLC : CHILLER 3 HOT WATER PUMP M03 (PRIMARY) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | GGF6003DC | HVAC03 | HVAC |  | 6 |  |  | 3011 | 0 | 13774 | 0 | 16416 | 2970 | 0 | EL6021_M180 |  | BITVAL
GPP6003D | VEGA BUNKER PLC : CHILLER 3 COLD WATER PUMP M03 (PRIMARY) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | GGF6003DC | HVAC03 | HVAC |  | 6 |  |  | 3011 | 1 | 13774 | 2 | 16416 | 2970 | 2 | EL6021_M180 |  | BITVAL
GPP6005D1 | VEGA BUNKER PLC : COLD WATER PUMP M05 (BUNKER) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3011 | 3 | 13774 | 6 | 16416 | 2970 | 6 | EL6021_M180 |  | BITVAL
GPP6005DI1 | VEGA BUNKER PLC : COLD WATER PUMP M05 (BUNKER) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3011 | 4 | 13774 | 8 | 16416 | 2971 | 0 | EL6021_M180 |  | BITVAL
GPP6002D2 | VEGA BUNKER PLC : COLD WATER PUMP P02 (GANTRY) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3011 | 5 | 13774 | 10 | 16416 | 2971 | 2 | EL6021_M180 |  | BITVAL
GPP6002DI2 | VEGA BUNKER PLC : COLD WATER PUMP P02 (GANTRY) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3011 | 6 | 13774 | 12 | 16416 | 2971 | 4 | EL6021_M180 |  | BITVAL
CPP6005D3 | VEGA BUNKER PLC : HOT WATER PUMP M05 (BUNKER/GANTRY) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3011 | 7 | 13774 | 14 | 16416 | 2971 | 6 | EL6021_M180 |  | BITVAL
CPP6005DI3 | VEGA BUNKER PLC : HOT WATER PUMP M05 (BUNKER/GANTRY) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3011 | 8 | 13775 | 0 | 16416 | 2972 | 0 | EL6021_M180 |  | BITVAL
VRP6118D1 | VEGA BUNKER PLC : FRESH AIR MOTORISED DAMPER 118.1 (CTA 2) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3011 | 10 | 13775 | 4 | 16416 | 2972 | 4 | EL6021_M180 |  | BITVAL
VRP6118D2 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 118.2 (CTA 2) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04;HVAC05;HVAC06 | HVAC |  | 6 |  |  | 3011 | 11 | 13775 | 6 | 16416 | 2972 | 6 | EL6021_M180 |  | BITVAL
VCT6002D | VEGA BUNKER PLC : FAN CTA M02 DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3011 | 12 | 13775 | 8 | 16416 | 2973 | 0 | EL6021_M180 |  | BITVAL
VCT6002DI | VEGA BUNKER PLC : FAN CTA M02 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3011 | 13 | 13775 | 10 | 16416 | 2973 | 2 | EL6021_M180 |  | BITVAL
VCT6002DF | VEGA BUNKER PLC : FAN CTA M02 FILTER DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3011 | 14 | 13775 | 12 | 16416 | 2973 | 4 | EL6021_M180 |  | BITVAL
VCT6002DR | VEGA BUNKER PLC : FAN CTA M02 DEW POINT DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3011 | 15 | 13775 | 14 | 16416 | 2973 | 6 | EL6021_M180 |  | BITVAL
GT6126V | VEGA BUNKER PLC : TEMPERATURE COLD WATER HIGH THRESHOLD DEFAULT STOPPING FAN COIL | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC03 | HVAC |  | 6 |  |  | 3012 | 0 | 13776 | 0 | 16416 | 2974 | 0 | EL6021_M180 |  | BITVAL
GGF6012DC | VEGA BUNKER PLC : CHILLER 1 AND 2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01; HVAC03 | HVAC |  | 6 |  |  | 3012 | 3 | 13776 | 6 | 16416 | 2974 | 6 | EL6021_M180 |  | BITVAL
VVV6126DC1 | VEGA BUNKER PLC : FAN COIL (AERMEC) (20 FAN COIL) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3012 | 4 | 13776 | 8 | 16416 | 2975 | 0 | EL6021_M180 |  | BITVAL
VRP6012D1 | VEGA BUNKER PLC : MOTORISED DAMPER 012.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 7 | 13776 | 14 | 16416 | 2975 | 6 | EL6021_M180 |  | BITVAL
VRP6100D2 | VEGA BUNKER PLC : MOTORISED DAMPER 100.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 8 | 13777 | 0 | 16416 | 2976 | 0 | EL6021_M180 |  | BITVAL
VRP6104D1 | VEGA BUNKER PLC : MOTORISED DAMPER 104.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 9 | 13777 | 2 | 16416 | 2976 | 2 | EL6021_M180 |  | BITVAL
VRP6107D1 | VEGA BUNKER PLC : MOTORISED DAMPER 107.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 10 | 13777 | 4 | 16416 | 2976 | 4 | EL6021_M180 |  | BITVAL
VRP6117D1 | VEGA BUNKER PLC : MOTORISED DAMPER 117.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 11 | 13777 | 6 | 16416 | 2976 | 6 | EL6021_M180 |  | BITVAL
VRP6012D2 | VEGA BUNKER PLC : MOTORISED DAMPER 012.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 12 | 13777 | 8 | 16416 | 2977 | 0 | EL6021_M180 |  | BITVAL
VRP6104D2 | VEGA BUNKER PLC : MOTORISED DAMPER 104.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 13 | 13777 | 10 | 16416 | 2977 | 2 | EL6021_M180 |  | BITVAL
VRP6107D2 | VEGA BUNKER PLC : MOTORISED DAMPER 107.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3012 | 14 | 13777 | 12 | 16416 | 2977 | 4 | EL6021_M180 |  | BITVAL
GGF6003DC | VEGA BUNKER PLC : CHILLER 3 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01; HVAC03 | HVAC |  | 6 |  |  | 3013 | 1 | 13778 | 2 | 16416 | 2978 | 2 | EL6021_M180 |  | BITVAL
VVV6126DC2 | VEGA BUNKER PLC : FAN COIL (AERMEC) (26 FAN COIL) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3013 | 2 | 13778 | 4 | 16416 | 2978 | 4 | EL6021_M180 |  | BITVAL
VVV6118DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 6 | 13778 | 12 | 16416 | 2979 | 4 | EL6021_M180 |  | BITVAL
VVV6118DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 7 | 13778 | 14 | 16416 | 2979 | 6 | EL6021_M180 |  | BITVAL
VVV6115DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 8 | 13779 | 0 | 16416 | 2980 | 0 | EL6021_M180 |  | BITVAL
VVV6115DT4 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.4 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 9 | 13779 | 2 | 16416 | 2980 | 2 | EL6021_M180 |  | BITVAL
VVV6117DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 117.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 10 | 13779 | 4 | 16416 | 2980 | 4 | EL6021_M180 |  | BITVAL
VVV6112DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 112.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 11 | 13779 | 6 | 16416 | 2980 | 6 | EL6021_M180 |  | BITVAL
VVV6111DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 111.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 12 | 13779 | 8 | 16416 | 2981 | 0 | EL6021_M180 |  | BITVAL
VVV6108DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 108.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 13 | 13779 | 10 | 16416 | 2981 | 2 | EL6021_M180 |  | BITVAL
VVV6108DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 108.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 14 | 13779 | 12 | 16416 | 2981 | 4 | EL6021_M180 |  | BITVAL
VVV6107DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 107.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3013 | 15 | 13779 | 14 | 16416 | 2981 | 6 | EL6021_M180 |  | BITVAL
VVV6106DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3014 | 0 | 13780 | 0 | 16416 | 2982 | 0 | EL6021_M180 |  | BITVAL
VVV6106DT4 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.4 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3014 | 1 | 13780 | 2 | 16416 | 2982 | 2 | EL6021_M180 |  | BITVAL
VVV6105DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 105.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 2 | 13780 | 4 | 16416 | 2982 | 4 | EL6021_M180 |  | BITVAL
VVV6121DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 121.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC09 | HVAC |  | 6 |  |  | 3014 | 3 | 13780 | 6 | 16416 | 2982 | 6 | EL6021_M180 |  | BITVAL
VVV6104DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 104.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 4 | 13780 | 8 | 16416 | 2983 | 0 | EL6021_M180 |  | BITVAL
VVV6100DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 100.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 5 | 13780 | 10 | 16416 | 2983 | 2 | EL6021_M180 |  | BITVAL
VVV6012DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 012.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 6 | 13780 | 12 | 16416 | 2983 | 4 | EL6021_M180 |  | BITVAL
VVV6006DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 006.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 8 | 13781 | 0 | 16416 | 2984 | 0 | EL6021_M180 |  | BITVAL
VVV6006DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 006.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 9 | 13781 | 2 | 16416 | 2984 | 2 | EL6021_M180 |  | BITVAL
VVV6004DT3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 004.3 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 10 | 13781 | 4 | 16416 | 2984 | 4 | EL6021_M180 |  | BITVAL
VVV6002DT2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 002.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 11 | 13781 | 6 | 16416 | 2984 | 6 | EL6021_M180 |  | BITVAL
VVV6001DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 001.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 13 | 13781 | 10 | 16416 | 2985 | 2 | EL6021_M180 |  | BITVAL
VVV6008DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 008.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3014 | 14 | 13781 | 12 | 16416 | 2985 | 4 | EL6021_M180 |  | BITVAL
VVV6009DT1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 009.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6126DC2 | HVAC07;HVAC18 | HVAC |  | 6 |  |  | 3014 | 15 | 13781 | 14 | 16416 | 2985 | 6 | EL6021_M180 |  | BITVAL
VCT6002DT | VEGA BUNKER PLC : FAN CTA M02 PULSE TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3015 | 0 | 13782 | 0 | 16416 | 2986 | 0 | EL6021_M180 |  | BITVAL
VCN6007DT2 | VEGA BUNKER PLC : AC CABINET (STULZ) 007.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6007DC2 | HVAC07 | HVAC |  | 6 |  |  | 3015 | 4 | 13782 | 8 | 16416 | 2987 | 0 | EL6021_M180 |  | BITVAL
VCN6101DT2 | VEGA BUNKER PLC : AC CABINET (STULZ) 101.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6101DC2 | HVAC07 | HVAC |  | 6 |  |  | 3015 | 5 | 13782 | 10 | 16416 | 2987 | 2 | EL6021_M180 |  | BITVAL
VCN6103DT2 | VEGA BUNKER PLC : AC CABINET (STULZ) 103.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6103DC2 | HVAC07 | HVAC |  | 6 |  |  | 3015 | 6 | 13782 | 12 | 16416 | 2987 | 4 | EL6021_M180 |  | BITVAL
VCN6113DT2 | VEGA BUNKER PLC : AC CABINET (STULZ) 113.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6113DC2 | HVAC08 | HVAC |  | 6 |  |  | 3015 | 7 | 13782 | 14 | 16416 | 2987 | 6 | EL6021_M180 |  | BITVAL
VCN6116DT2 | VEGA BUNKER PLC : AC CABINET (STULZ) 116.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6116DC2 | HVAC08 | HVAC |  | 6 |  |  | 3015 | 8 | 13783 | 0 | 16416 | 2988 | 0 | EL6021_M180 |  | BITVAL
VCN6007DC2 | VEGA BUNKER PLC : AC CABINET (STULZ) 007.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K08 | HVAC07 |  |  | 6 |  |  | 3015 | 9 | 13783 | 2 | 16416 | 2988 | 2 | EL6021_M180 |  | BITVAL
VCN6101DC2 | VEGA BUNKER PLC : AC CABINET (STULZ) 101.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC07 |  |  | 6 |  |  | 3015 | 10 | 13783 | 4 | 16416 | 2988 | 4 | EL6021_M180 |  | BITVAL
VCN6103DC2 | VEGA BUNKER PLC : AC CABINET (STULZ) 103.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC07 |  |  | 6 |  |  | 3015 | 11 | 13783 | 6 | 16416 | 2988 | 6 | EL6021_M180 |  | BITVAL
VCN6113DC2 | VEGA BUNKER PLC : AC CABINET (STULZ) 113.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC08 |  |  | 6 |  |  | 3015 | 12 | 13783 | 8 | 16416 | 2989 | 0 | EL6021_M180 |  | BITVAL
VCN6116DC2 | VEGA BUNKER PLC : AC CABINET (STULZ) 116.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC08 |  |  | 6 |  |  | 3015 | 13 | 13783 | 10 | 16416 | 2989 | 2 | EL6021_M180 |  | BITVAL
VCF6001D1 | VEGA BUNKER PLC : FIRE DAMPER 001.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3015 | 14 | 13783 | 12 | 16416 | 2989 | 4 | EL6021_M180 |  | BITVAL
VCF6012D1 | VEGA BUNKER PLC : FIRE DAMPER 012.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3015 | 15 | 13783 | 14 | 16416 | 2989 | 6 | EL6021_M180 |  | BITVAL
VCF6012D2 | VEGA BUNKER PLC : FIRE DAMPER 012.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 0 | 13784 | 0 | 16416 | 2990 | 0 | EL6021_M180 |  | BITVAL
VCF6012D3 | VEGA BUNKER PLC : FIRE DAMPER 012.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 1 | 13784 | 2 | 16416 | 2990 | 2 | EL6021_M180 |  | BITVAL
VCF6003D1 | VEGA BUNKER PLC : FIRE DAMPER 003.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 2 | 13784 | 4 | 16416 | 2990 | 4 | EL6021_M180 |  | BITVAL
VCF6003D2 | VEGA BUNKER PLC : FIRE DAMPER 003.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 3 | 13784 | 6 | 16416 | 2990 | 6 | EL6021_M180 |  | BITVAL
VCF6003D3 | VEGA BUNKER PLC : FIRE DAMPER 003.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 4 | 13784 | 8 | 16416 | 2991 | 0 | EL6021_M180 |  | BITVAL
VCF6006D1 | VEGA BUNKER PLC : FIRE DAMPER 006.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 5 | 13784 | 10 | 16416 | 2991 | 2 | EL6021_M180 |  | BITVAL
VCF6006D2 | VEGA BUNKER PLC : FIRE DAMPER 006.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 6 | 13784 | 12 | 16416 | 2991 | 4 | EL6021_M180 |  | BITVAL
VCF6100D1 | VEGA BUNKER PLC : FIRE DAMPER 100.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 7 | 13784 | 14 | 16416 | 2991 | 6 | EL6021_M180 |  | BITVAL
VCF6100D2 | VEGA BUNKER PLC : FIRE DAMPER 100.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 8 | 13785 | 0 | 16416 | 2992 | 0 | EL6021_M180 |  | BITVAL
VCF6108D1 | VEGA BUNKER PLC : FIRE DAMPER 108.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 9 | 13785 | 2 | 16416 | 2992 | 2 | EL6021_M180 |  | BITVAL
VCF6117D1 | VEGA BUNKER PLC : FIRE DAMPER 117.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 10 | 13785 | 4 | 16416 | 2992 | 4 | EL6021_M180 |  | BITVAL
VCF6117D2 | VEGA BUNKER PLC : FIRE DAMPER 117.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 11 | 13785 | 6 | 16416 | 2992 | 6 | EL6021_M180 |  | BITVAL
VCF6126D1 | VEGA BUNKER PLC : FIRE DAMPER 126.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3016 | 12 | 13785 | 8 | 16416 | 2993 | 0 | EL6021_M180 |  | BITVAL
VCN6002D2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.2 GENERAL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6002DC2 | HVAC07 |  |  | 6 |  |  | 3016 | 15 | 13785 | 14 | 16416 | 2993 | 6 | EL6021_M180 |  | BITVAL
VCN6002DT2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6002DC2 | HVAC07 | HVAC |  | 6 |  |  | 3017 | 0 | 13786 | 0 | 16416 | 2994 | 0 | EL6021_M180 |  | BITVAL
VCN6002DC2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC07 |  |  | 6 |  |  | 3017 | 1 | 13786 | 2 | 16416 | 2994 | 2 | EL6021_M180 |  | BITVAL
VRP6002D1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 002.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3017 | 2 | 13786 | 4 | 16416 | 2994 | 4 | EL6021_M180 |  | BITVAL
VCN6004D2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.2 GENERAL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6004DC2 | HVAC07 |  |  | 6 |  |  | 3017 | 3 | 13786 | 6 | 16416 | 2994 | 6 | EL6021_M180 |  | BITVAL
VCN6004DT2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VCN6004DC2 | HVAC07 | HVAC |  | 6 |  |  | 3017 | 4 | 13786 | 8 | 16416 | 2995 | 0 | EL6021_M180 |  | BITVAL
VCN6004DC2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.2 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6126K32 | HVAC07 |  |  | 6 |  |  | 3017 | 5 | 13786 | 10 | 16416 | 2995 | 2 | EL6021_M180 |  | BITVAL
VZC6126Z1 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE SUPPLY COLD WATER GANTRY | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 0 | 16040 | 0 | 16416 | 7502 | 0 | EL6021_M180 |  | BITVAL
VZC6126Z2 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE RETURN COLD WATER GANTRY | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 1 | 16040 | 2 | 16416 | 7502 | 2 | EL6021_M180 |  | BITVAL
VZC6126Z3 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE SUPPLY COLD WATER BUNKER | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 2 | 16040 | 4 | 16416 | 7502 | 4 | EL6021_M180 |  | BITVAL
VZC6126Z4 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE RETURN COLD WATER BUNKER | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 3 | 16040 | 6 | 16416 | 7502 | 6 | EL6021_M180 |  | BITVAL
VZC6126Z9 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE RETURN HOT WATER BUNKER | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 8 | 16041 | 0 | 16416 | 7504 | 0 | EL6021_M180 |  | BITVAL
VZC6126Z11 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE SUPPLY HOT WATER BUNKER/GANTRY | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 10 | 16041 | 4 | 16416 | 7504 | 4 | EL6021_M180 |  | BITVAL
VZC6126Z12 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE RETURN HOT WATER GANTRY | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 11 | 16041 | 6 | 16416 | 7504 | 6 | EL6021_M180 |  | BITVAL
VZC6126Z13 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE AFTER COOL BATTERY FAN CTA M01 | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 12 | 16041 | 8 | 16416 | 7505 | 0 | EL6021_M180 |  | BITVAL
VZC6126Z14 | VEGA BUNKER PLC : VALIDITY DEFAULT PULSE TEMPERATURE FAN CTA M01 | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3018 | 13 | 16041 | 10 | 16416 | 7505 | 2 | EL6021_M180 |  | BITVAL
VZC6126Z17 | VEGA BUNKER PLC : VALIDITY DEFAULT PRESSURE HOT WATER PUMP M04 (BUNKER/GANTRY) | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 |  |  |  |  | 6 |  |  | 3019 | 0 | 16042 | 0 | 16416 | 7506 | 0 | EL6021_M180 |  | BITVAL
VZC6126Z21 | VEGA BUNKER PLC : VALIDITY DEFAULT FLOW RETURN COLD WATER BUNKER | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3019 | 4 | 16042 | 8 | 16416 | 7507 | 0 | EL6021_M180 |  | BITVAL
VZC6126Z22 | VEGA BUNKER PLC : VALIDITY DEFAULT FLOW RETURN COLD WATER GANTRY | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3019 | 5 | 16042 | 10 | 16416 | 7507 | 2 | EL6021_M180 |  | BITVAL
VZC6126Z25 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE AFTER COOL BATTERY FAN CTA M02 | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3019 | 8 | 16043 | 0 | 16416 | 7508 | 0 | EL6021_M180 |  | BITVAL
VZC6126Z26 | VEGA BUNKER PLC : VALIDITY DEFAULT PULSE TEMPERATURE FAN CTA M02 | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3019 | 9 | 16043 | 2 | 16416 | 7508 | 2 | EL6021_M180 |  | BITVAL
VZC6126Z27 | VEGA BUNKER PLC : VALIDITY DEFAULT TEMPERATURE OUTSIDE | AL | N | RES | 1 | C | [12 empty] | C | [14 empty] | 1000 | VZC6126D |  |  |  | 6 |  |  | 3019 | 10 | 16043 | 4 | 16416 | 7508 | 4 | EL6021_M180 |  | BITVAL
VZC6126SD1 | VEGA BUNKER PLC X80-1 : SD CARD DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 0 | 13790 | 0 | 16416 | 3002 | 0 | EL6021_M180 |  | BITVAL
VZC6126D1 | VEGA BUNKER PLC X80-1 : CPU DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 1 | 13790 | 2 | 16416 | 3002 | 2 | EL6021_M180 |  | BITVAL
VZC6126K02 | VEGA BUNKER PLC X80-1 : CARD SLOT 2 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 2 | 13790 | 4 | 16416 | 3002 | 4 | EL6021_M180 |  | BITVAL
VZC6126K03 | VEGA BUNKER PLC X80-1 : CARD SLOT 3 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 3 | 13790 | 6 | 16416 | 3002 | 6 | EL6021_M180 |  | BITVAL
VZC6126SD2 | VEGA BUNKER PLC X80-2 : SD CARD DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 8 | 13791 | 0 | 16416 | 3004 | 0 | EL6021_M180 |  | BITVAL
VZC6126D2 | VEGA BUNKER PLC X80-2 : CPU DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 9 | 13791 | 2 | 16416 | 3004 | 2 | EL6021_M180 |  | BITVAL
VZC6126K04 | VEGA BUNKER PLC X80-2 : CARD SLOT 2 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 10 | 13791 | 4 | 16416 | 3004 | 4 | EL6021_M180 |  | BITVAL
VZC6126K05 | VEGA BUNKER PLC X80-2 : CARD SLOT 3 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3020 | 11 | 13791 | 6 | 16416 | 3004 | 6 | EL6021_M180 |  | BITVAL
VZC6126K06 | VEGA BUNKER PLC X80-3 : CARD SLOT 0 (CRA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 0 | 13792 | 0 | 16416 | 3006 | 0 | EL6021_M180 |  | BITVAL
VZC6126K07 | VEGA BUNKER PLC X80-3 : CARD SLOT 1 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 1 | 13792 | 2 | 16416 | 3006 | 2 | EL6021_M180 |  | BITVAL
VZC6126K08 | VEGA BUNKER PLC X80-3 : CARD SLOT 2 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 2 | 13792 | 4 | 16416 | 3006 | 4 | EL6021_M180 |  | BITVAL
VZC6126K10 | VEGA BUNKER PLC X80-3 : CARD SLOT 4 (SANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 4 | 13792 | 8 | 16416 | 3007 | 0 | EL6021_M180 |  | BITVAL
VZC6126K13 | VEGA BUNKER PLC X80-3 : CARD SLOT 7 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 7 | 13792 | 14 | 16416 | 3007 | 6 | EL6021_M180 |  | BITVAL
VZC6126K14 | VEGA BUNKER PLC X80-3 : CARD SLOT 8 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 8 | 13793 | 0 | 16416 | 3008 | 0 | EL6021_M180 |  | BITVAL
VZC6126K15 | VEGA BUNKER PLC X80-3 : CARD SLOT 9 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3021 | 9 | 13793 | 2 | 16416 | 3008 | 2 | EL6021_M180 |  | BITVAL
VZC6126K18 | VEGA BUNKER PLC X80-4 : CARD SLOT 0 (CRA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 0 | 13794 | 0 | 16416 | 3010 | 0 | EL6021_M180 |  | BITVAL
VZC6126K19 | VEGA BUNKER PLC X80-4 : CARD SLOT 1 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 1 | 13794 | 2 | 16416 | 3010 | 2 | EL6021_M180 |  | BITVAL
VZC6126K20 | VEGA BUNKER PLC X80-4 : CARD SLOT 2 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 2 | 13794 | 4 | 16416 | 3010 | 4 | EL6021_M180 |  | BITVAL
VZC6126K21 | VEGA BUNKER PLC X80-4 : CARD SLOT 3 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 3 | 13794 | 6 | 16416 | 3010 | 6 | EL6021_M180 |  | BITVAL
VZC6126K22 | VEGA BUNKER PLC X80-4 : CARD SLOT 4 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 4 | 13794 | 8 | 16416 | 3011 | 0 | EL6021_M180 |  | BITVAL
VZC6126K25 | VEGA BUNKER PLC X80-4 : CARD SLOT 7 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01); EI66; EI67; EI68; EI71 | HVAC; Extinction Incendie (EI) |  | 6 |  |  | 3022 | 7 | 13794 | 14 | 16416 | 3011 | 6 | EL6021_M180 |  | BITVAL
VZC6126K26 | VEGA BUNKER PLC X80-4 : CARD SLOT 8 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 8 | 13795 | 0 | 16416 | 3012 | 0 | EL6021_M180 |  | BITVAL
VZC6126K27 | VEGA BUNKER PLC X80-4 : CARD SLOT 9 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 9 | 13795 | 2 | 16416 | 3012 | 2 | EL6021_M180 |  | BITVAL
VZC6126K28 | VEGA BUNKER PLC X80-4 : CARD SLOT 10 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3022 | 10 | 13795 | 4 | 16416 | 3012 | 4 | EL6021_M180 |  | BITVAL
VZC6126K30 | VEGA BUNKER PLC X80-5 : CARD SLOT 0 (CRA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 0 | 13796 | 0 | 16416 | 3014 | 0 | EL6021_M180 |  | BITVAL
VZC6126K31 | VEGA BUNKER PLC X80-5 : CARD SLOT 1 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 1 | 13796 | 2 | 16416 | 3014 | 2 | EL6021_M180 |  | BITVAL
VZC6126K32 | VEGA BUNKER PLC X80-5 : CARD SLOT 2 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 2 | 13796 | 4 | 16416 | 3014 | 4 | EL6021_M180 |  | BITVAL
VZC6126K34 | VEGA BUNKER PLC X80-5 : CARD SLOT 4 (SANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 4 | 13796 | 8 | 16416 | 3015 | 0 | EL6021_M180 |  | BITVAL
VZC6126K35 | VEGA BUNKER PLC X80-5 : CARD SLOT 5 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 5 | 13796 | 10 | 16416 | 3015 | 2 | EL6021_M180 |  | BITVAL
VZC6126K36 | VEGA BUNKER PLC X80-5 : CARD SLOT 6 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 6 | 13796 | 12 | 16416 | 3015 | 4 | EL6021_M180 |  | BITVAL
VZC6126K38 | VEGA BUNKER PLC X80-5 : CARD SLOT 8 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 8 | 13797 | 0 | 16416 | 3016 | 0 | EL6021_M180 |  | BITVAL
VZC6126K39 | VEGA BUNKER PLC X80-5 : CARD SLOT 9 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 9 | 13797 | 2 | 16416 | 3016 | 2 | EL6021_M180 |  | BITVAL
VZC6126K40 | VEGA BUNKER PLC X80-5 : CARD SLOT 10 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3023 | 10 | 13797 | 4 | 16416 | 3016 | 4 | EL6021_M180 |  | BITVAL
VZC6126D | VEGA BUNKER PLC : PLC DEFAULT SYNTHESIS | AL |  | RES | 1 | A |  | K | [10 empty] | A | [13 empty] | NOT | 1000 |  | CV0B X80 HVAC Bunker PLC Infos (HVAC01) | HVAC |  | 6 |  |  | 3024 | 0 | 13798 | 0 | 16416 | 3018 | 0 | EL6021_M180 |  | BITVAL
VZC6126DC1 | VEGA BUNKER PLC : PRIMARY / SECONDARY STATUS LINK DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3024 | 1 | 13798 | 2 | 16416 | 3018 | 2 | EL6021_M180 |  | BITVAL
VZC6126DC2 | VEGA BUNKER PLC : PRIMARY / SECONDARY DATABASE SYNCHRONIZATION LINK DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3024 | 2 | 13798 | 4 | 16416 | 3018 | 4 | EL6021_M180 |  | BITVAL
VZC6126DC3 | VEGA BUNKER PLC : SECONDARY PLC / LOCAL SUPERVISION COMMUNICATION DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3024 | 3 | 13798 | 6 | 16416 | 3018 | 6 | EL6021_M180 |  | BITVAL
VZC6126DC4 | VEGA BUNKER PLC : GANTRY / BUNKER COMMUNICATION DEFAULT | AL |  | RES | 1 | A |  | K | [10 empty] | A | [13 empty] | NOT | 1000 | VZC6126D | HVAC01 | HVAC |  | 6 |  |  | 3024 | 4 | 13798 | 8 | 16416 | 3019 | 0 | EL6021_M180 |  | BITVAL
VRP6401D2 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 401.2 (CTA 1) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13;HVAC15 | HVAC |  | 7 |  |  | 3000 | 1 | 14122 | 2 | 16416 | 3666 | 2 | EL6021_M181 |  | BITVAL
VFN6401D1 | VEGA GANTRY PLC : FAN CTA P01 DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3000 | 2 | 14122 | 4 | 16416 | 3666 | 4 | EL6021_M181 |  | BITVAL
VFN6401DI1 | VEGA GANTRY PLC : FAN CTA P01 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3000 | 3 | 14122 | 6 | 16416 | 3666 | 6 | EL6021_M181 |  | BITVAL
VFN6401DF1 | VEGA GANTRY PLC : FAN CTA P01 FILTER DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3000 | 4 | 14122 | 8 | 16416 | 3667 | 0 | EL6021_M181 |  | BITVAL
VFN6401DR1 | VEGA GANTRY PLC : FAN CTA P01 DEW POINT DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3000 | 5 | 14122 | 10 | 16416 | 3667 | 2 | EL6021_M181 |  | BITVAL
VFN6102D | VEGA GANTRY PLC : FAN CTA P03 DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3000 | 6 | 14122 | 12 | 16416 | 3667 | 4 | EL6021_M181 |  | BITVAL
VFN6102DI | VEGA GANTRY PLC : FAN CTA P03 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3000 | 7 | 14122 | 14 | 16416 | 3667 | 6 | EL6021_M181 |  | BITVAL
VFN6102DF | VEGA GANTRY PLC : FAN CTA P03 FILTER DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3000 | 8 | 14123 | 0 | 16416 | 3668 | 0 | EL6021_M181 |  | BITVAL
VAE6401D400 | VEGA GANTRY PLC : POWER SUPPLY 400V DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 7 |  |  | 3000 | 9 | 14123 | 2 | 16416 | 3668 | 2 | EL6021_M181 |  | BITVAL
VAE6401D3 | VEGA GANTRY PLC : POWER SUPPLY CAT 3 DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 7 |  |  | 3000 | 10 | 14123 | 4 | 16416 | 3668 | 4 | EL6021_M181 |  | BITVAL
VAE6401D24 | VEGA GANTRY PLC : POWER SUPPLY 24V DEFAULT | AL |  | RES | 1 | C;A |  | K | [10 empty] | C;A | [13 empty] | NOT | 1000 |  | HVAC01 | HVAC |  | 7 |  |  | 3000 | 11 | 14123 | 6 | 16416 | 3668 | 6 | EL6021_M181 |  | BITVAL
VFN6102DR | VEGA GANTRY PLC : FAN CTA P03 DEW POINT DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3000 | 12 | 14123 | 8 | 16416 | 3669 | 0 | EL6021_M181 |  | BITVAL
VRP6102D5 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 102.5 (CTA 3) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14;HVAC15 | HVAC |  | 7 |  |  | 3000 | 13 | 14123 | 10 | 16416 | 3669 | 2 | EL6021_M181 |  | BITVAL
VRP6701D1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 701.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3000 | 14 | 14123 | 12 | 16416 | 3669 | 4 | EL6021_M181 |  | BITVAL
VRP6701D2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 701.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3000 | 15 | 14123 | 14 | 16416 | 3669 | 6 | EL6021_M181 |  | BITVAL
VFN6701DI | VEGA GANTRY PLC : FAN EXTRACTOR P06 (N2O4) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 0 | 14124 | 0 | 16416 | 3670 | 0 | EL6021_M181 |  | BITVAL
VFN6701D | VEGA GANTRY PLC : FAN EXTRACTOR P06 (N2O4) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 1 | 14124 | 2 | 16416 | 3670 | 2 | EL6021_M181 |  | BITVAL
VRP6701D3 | VEGA GANTRY PLC : HALL MOTORISED DAMPER 701.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 2 | 14124 | 4 | 16416 | 3670 | 4 | EL6021_M181 |  | BITVAL
VRP6601D1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 601.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 5 | 14124 | 10 | 16416 | 3671 | 2 | EL6021_M181 |  | BITVAL
VRP6601D2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 601.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 6 | 14124 | 12 | 16416 | 3671 | 4 | EL6021_M181 |  | BITVAL
VFN6601DI | VEGA GANTRY PLC : FAN EXTRACTOR P07 (UDMH) DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 7 | 14124 | 14 | 16416 | 3671 | 6 | EL6021_M181 |  | BITVAL
VFN6601D | VEGA GANTRY PLC : FAN EXTRACTOR P07 (UDMH) DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 8 | 14125 | 0 | 16416 | 3672 | 0 | EL6021_M181 |  | BITVAL
VRP6601D3 | VEGA GANTRY PLC : HALL MOTORISED DAMPER 601.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 9 | 14125 | 2 | 16416 | 3672 | 2 | EL6021_M181 |  | BITVAL
VRP6101D21 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 101.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 10 | 14125 | 4 | 16416 | 3672 | 4 | EL6021_M181 |  | BITVAL
VRP6201D3 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 201.3 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 11 | 14125 | 6 | 16416 | 3672 | 6 | EL6021_M181 |  | BITVAL
VRP6502D1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 502.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 12 | 14125 | 8 | 16416 | 3673 | 0 | EL6021_M181 |  | BITVAL
VRP6999D1 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER HALL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 13 | 14125 | 10 | 16416 | 3673 | 2 | EL6021_M181 |  | BITVAL
VRP6999D2 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER HALL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 14 | 14125 | 12 | 16416 | 3673 | 4 | EL6021_M181 |  | BITVAL
VFN6999DI | VEGA GANTRY PLC : FAN EXTRACTOR P08 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3001 | 15 | 14125 | 14 | 16416 | 3673 | 6 | EL6021_M181 |  | BITVAL
VFN6999D | VEGA GANTRY PLC : FAN EXTRACTOR P08 DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 0 | 14126 | 0 | 16416 | 3674 | 0 | EL6021_M181 |  | BITVAL
VRP6101D22 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 101.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 1 | 14126 | 2 | 16416 | 3674 | 2 | EL6021_M181 |  | BITVAL
VRP6201D2 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 201.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 2 | 14126 | 4 | 16416 | 3674 | 4 | EL6021_M181 |  | BITVAL
VRP6502D2 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 502.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 3 | 14126 | 6 | 16416 | 3674 | 6 | EL6021_M181 |  | BITVAL
VH6999WH | VEGA GANTRY PLC : HYGROMETRY HALL HIGH THRESHOLD DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3002 | 4 | 14126 | 8 | 16416 | 3675 | 0 | EL6021_M181 |  | BITVAL
VH6999WB | VEGA GANTRY PLC : HYGROMETRY HALL LOW THRESHOLD DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3002 | 5 | 14126 | 10 | 16416 | 3675 | 2 | EL6021_M181 |  | BITVAL
VT6999WH | VEGA GANTRY PLC : TEMPERATURE HALL HIGH THRESHOLD DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3002 | 6 | 14126 | 12 | 16416 | 3675 | 4 | EL6021_M181 |  | BITVAL
VT6999WB | VEGA GANTRY PLC : TEMPERATURE HALL LOW THRESHOLD DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3002 | 7 | 14126 | 14 | 16416 | 3675 | 6 | EL6021_M181 |  | BITVAL
GT6401V | VEGA GANTRY PLC : TEMPERATURE COLD WATER HIGH THRESHOLD DEFAULT STOPPING FAN COIL | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3002 | 8 | 14127 | 0 | 16416 | 3676 | 0 | EL6021_M181 |  | BITVAL
VRU6101D2 | VEGA GANTRY PLC : N2 INERTING ROOM 101 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 10 | 14127 | 4 | 16416 | 3676 | 4 | EL6021_M181 |  | BITVAL
VRU6201D | VEGA GANTRY PLC : N2 INERTING ROOM 201 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 11 | 14127 | 6 | 16416 | 3676 | 6 | EL6021_M181 |  | BITVAL
VRU6502D | VEGA GANTRY PLC : N2 INERTING ROOM 502 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3002 | 12 | 14127 | 8 | 16416 | 3677 | 0 | EL6021_M181 |  | BITVAL
VCT6102DT | VEGA GANTRY PLC : FAN CTA P03 PULSE TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3002 | 13 | 14127 | 10 | 16416 | 3677 | 2 | EL6021_M181 |  | BITVAL
VCT6401DT1 | VEGA GANTRY PLC : FAN CTA P01 PULSE TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3002 | 14 | 14127 | 12 | 16416 | 3677 | 4 | EL6021_M181 |  | BITVAL
VT6401D1 | VEGA GANTRY PLC : AMBIENT TEMPERATURE 40M LEVEL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3002 | 15 | 14127 | 14 | 16416 | 3677 | 6 | EL6021_M181 |  | BITVAL
VH6401D1 | VEGA GANTRY PLC : AMBIENT HYGROMETRY 40M LEVEL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3003 | 0 | 14128 | 0 | 16416 | 3678 | 0 | EL6021_M181 |  | BITVAL
VT6102D | VEGA GANTRY PLC : AMBIENT TEMPERATURE 20M LEVEL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3003 | 1 | 14128 | 2 | 16416 | 3678 | 2 | EL6021_M181 |  | BITVAL
VH6102D | VEGA GANTRY PLC : AMBIENT HYGROMETRY 20M LEVEL DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3003 | 2 | 14128 | 4 | 16416 | 3678 | 4 | EL6021_M181 |  | BITVAL
VVV6502DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 502.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3003 | 3 | 14128 | 6 | 16416 | 3678 | 6 | EL6021_M181 |  | BITVAL
VVV6401DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 401.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3003 | 4 | 14128 | 8 | 16416 | 3679 | 0 | EL6021_M181 |  | BITVAL
VVV6301DT2 | VEGA GANTRY PLC : FAN COIL (CAREL) 301.2 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3003 | 5 | 14128 | 10 | 16416 | 3679 | 2 | EL6021_M181 |  | BITVAL
VVV6202DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 202.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3003 | 6 | 14128 | 12 | 16416 | 3679 | 4 | EL6021_M181 |  | BITVAL
VVV6102DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 102.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3003 | 7 | 14128 | 14 | 16416 | 3679 | 6 | EL6021_M181 |  | BITVAL
VVV6101DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 101.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3003 | 8 | 14129 | 0 | 16416 | 3680 | 0 | EL6021_M181 |  | BITVAL
VAR6102DT | VEGA GANTRY PLC : TEMPERATURE RETURN AIR DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3003 | 9 | 14129 | 2 | 16416 | 3680 | 2 | EL6021_M181 |  | BITVAL
VAR6102DH | VEGA GANTRY PLC : HYGROMETRY RETURN AIR DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3003 | 10 | 14129 | 4 | 16416 | 3680 | 4 | EL6021_M181 |  | BITVAL
VCT6401DP1 | VEGA GANTRY PLC : FAN CTA P01 DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3003 | 11 | 14129 | 6 | 16416 | 3680 | 6 | EL6021_M181 |  | BITVAL
VCT6102DP | VEGA GANTRY PLC : FAN CTA P03 DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3003 | 12 | 14129 | 8 | 16416 | 3681 | 0 | EL6021_M181 |  | BITVAL
VCT6701DP | VEGA GANTRY PLC : FAN CTA P06 (N2O4) DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3003 | 13 | 14129 | 10 | 16416 | 3681 | 2 | EL6021_M181 |  | BITVAL
VCT6601DP | VEGA GANTRY PLC : FAN CTA P07 (UDMH) DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3003 | 14 | 14129 | 12 | 16416 | 3681 | 4 | EL6021_M181 |  | BITVAL
VCT6999DP | VEGA GANTRY PLC : FAN CTA P08 DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3003 | 15 | 14129 | 14 | 16416 | 3681 | 6 | EL6021_M181 |  | BITVAL
VSY6401W1 | VEGA GANTRY PLC : LEVEL 1 ALARM SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3004 | 0 | 14130 | 0 | 16416 | 3682 | 0 | EL6021_M181 |  | BITVAL
VSY6401W2 | VEGA GANTRY PLC : LEVEL 2 ALARM SYNTHESIS | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3004 | 1 | 14130 | 2 | 16416 | 3682 | 2 | EL6021_M181 |  | BITVAL
VUM6401V | VEGA GANTRY PLC : LOCKING OF VMC COMMANDS BY LOCAL HVAC SUPERVISION | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3004 | 4 | 14130 | 8 | 16416 | 3683 | 0 | EL6021_M181 |  | BITVAL
VVV6401DC1 | VEGA GANTRY PLC : FAN COIL (CAREL) (6 FAN COIL) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3004 | 7 | 14130 | 14 | 16416 | 3683 | 6 | EL6021_M181 |  | BITVAL
VCT6401DC1 | VEGA GANTRY PLC : FAN CTA P01 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3004 | 8 | 14131 | 0 | 16416 | 3684 | 0 | EL6021_M181 |  | BITVAL
VCT6102DC | VEGA GANTRY PLC : FAN CTA P03 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3004 | 9 | 14131 | 2 | 16416 | 3684 | 2 | EL6021_M181 |  | BITVAL
VVV6401DC2 | VEGA GANTRY PLC : FAN COIL (CAREL) (4 FAN COIL) COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3004 | 12 | 14131 | 8 | 16416 | 3685 | 0 | EL6021_M181 |  | BITVAL
VCT6401DC2 | VEGA GANTRY PLC : FAN CTA P02 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3004 | 13 | 14131 | 10 | 16416 | 3685 | 2 | EL6021_M181 |  | BITVAL
VCT6202DC | VEGA GANTRY PLC : FAN CTA P04 COMMUNICATION DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D |  |  |  | 7 |  |  | 3004 | 14 | 14131 | 12 | 16416 | 3685 | 4 | EL6021_M181 |  | BITVAL
VZC6401SD1 | VEGA GANTRY PLC X80-1 : SD CARD DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 0 | 14132 | 0 | 16416 | 3686 | 0 | EL6021_M181 |  | BITVAL
VZC6401D1 | VEGA GANTRY PLC X80-1 : CPU DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 1 | 14132 | 2 | 16416 | 3686 | 2 | EL6021_M181 |  | BITVAL
VZC6401K02 | VEGA GANTRY PLC X80-1 : CARD SLOT 2 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 2 | 14132 | 4 | 16416 | 3686 | 4 | EL6021_M181 |  | BITVAL
VZC6401K03 | VEGA GANTRY PLC X80-1 : CARD SLOT 3 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 3 | 14132 | 6 | 16416 | 3686 | 6 | EL6021_M181 |  | BITVAL
VZC6401SD2 | VEGA GANTRY PLC X80-2 : SD CARD DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 8 | 14133 | 0 | 16416 | 3688 | 0 | EL6021_M181 |  | BITVAL
VZC6401D2 | VEGA GANTRY PLC X80-2 : CPU DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 9 | 14133 | 2 | 16416 | 3688 | 2 | EL6021_M181 |  | BITVAL
VZC6401K04 | VEGA GANTRY PLC X80-2 : CARD SLOT 2 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 10 | 14133 | 4 | 16416 | 3688 | 4 | EL6021_M181 |  | BITVAL
VZC6401K05 | VEGA GANTRY PLC X80-2 : CARD SLOT 3 (NOC) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3005 | 11 | 14133 | 6 | 16416 | 3688 | 6 | EL6021_M181 |  | BITVAL
VZC6401K06 | VEGA GANTRY PLC X80-3 : CARD SLOT 0 (CRA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 0 | 14134 | 0 | 16416 | 3690 | 0 | EL6021_M181 |  | BITVAL
VZC6401K07 | VEGA GANTRY PLC X80-3 : CARD SLOT 1 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 1 | 14134 | 2 | 16416 | 3690 | 2 | EL6021_M181 |  | BITVAL
VZC6401K08 | VEGA GANTRY PLC X80-3 : CARD SLOT 2 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 2 | 14134 | 4 | 16416 | 3690 | 4 | EL6021_M181 |  | BITVAL
VZC6401K10 | VEGA GANTRY PLC X80-3 : CARD SLOT 4 (SANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 4 | 14134 | 8 | 16416 | 3691 | 0 | EL6021_M181 |  | BITVAL
VZC6401K11 | VEGA GANTRY PLC X80-3 : CARD SLOT 5 (SANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 5 | 14134 | 10 | 16416 | 3691 | 2 | EL6021_M181 |  | BITVAL
VZC6401K12 | VEGA GANTRY PLC X80-3 : CARD SLOT 6 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 6 | 14134 | 12 | 16416 | 3691 | 4 | EL6021_M181 |  | BITVAL
VZC6401K13 | VEGA GANTRY PLC X80-3 : CARD SLOT 7 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3006 | 7 | 14134 | 14 | 16416 | 3691 | 6 | EL6021_M181 |  | BITVAL
VZC6401K18 | VEGA GANTRY PLC X80-4 : CARD SLOT 0 (CRA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3007 | 0 | 14136 | 0 | 16416 | 3694 | 0 | EL6021_M181 |  | BITVAL
VZC6401K19 | VEGA GANTRY PLC X80-4 : CARD SLOT 1 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3007 | 1 | 14136 | 2 | 16416 | 3694 | 2 | EL6021_M181 |  | BITVAL
VZC6401K20 | VEGA GANTRY PLC X80-4 : CARD SLOT 2 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3007 | 2 | 14136 | 4 | 16416 | 3694 | 4 | EL6021_M181 |  | BITVAL
VZC6401K21 | VEGA GANTRY PLC X80-4 : CARD SLOT 3 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3007 | 3 | 14136 | 6 | 16416 | 3694 | 6 | EL6021_M181 |  | BITVAL
VZC6401K27 | VEGA GANTRY PLC X80-4 : CARD SLOT 9 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3007 | 9 | 14137 | 2 | 16416 | 3696 | 2 | EL6021_M181 |  | BITVAL
VZC6401K28 | VEGA GANTRY PLC X80-4 : CARD SLOT 10 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01); EI69 | HVAC; Extinction Incendie (EI) |  | 7 |  |  | 3007 | 10 | 14137 | 4 | 16416 | 3696 | 4 | EL6021_M181 |  | BITVAL
VZC6401K30 | VEGA GANTRY PLC X80-5 : CARD SLOT 0 (CRA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 0 | 14138 | 0 | 16416 | 3698 | 0 | EL6021_M181 |  | BITVAL
VZC6401K31 | VEGA GANTRY PLC X80-5 : CARD SLOT 1 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 1 | 14138 | 2 | 16416 | 3698 | 2 | EL6021_M181 |  | BITVAL
VZC6401K32 | VEGA GANTRY PLC X80-5 : CARD SLOT 2 (NOM) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 2 | 14138 | 4 | 16416 | 3698 | 4 | EL6021_M181 |  | BITVAL
VZC6401K34 | VEGA GANTRY PLC X80-5 : CARD SLOT 4 (SANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 4 | 14138 | 8 | 16416 | 3699 | 0 | EL6021_M181 |  | BITVAL
VZC6401K35 | VEGA GANTRY PLC X80-5 : CARD SLOT 5 (SANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 5 | 14138 | 10 | 16416 | 3699 | 2 | EL6021_M181 |  | BITVAL
VZC6401K36 | VEGA GANTRY PLC X80-5 : CARD SLOT 6 (STOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 6 | 14138 | 12 | 16416 | 3699 | 4 | EL6021_M181 |  | BITVAL
VZC6401K38 | VEGA GANTRY PLC X80-5 : CARD SLOT 8 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 8 | 14139 | 0 | 16416 | 3700 | 0 | EL6021_M181 |  | BITVAL
VZC6401K39 | VEGA GANTRY PLC X80-5 : CARD SLOT 9 (EANA) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 9 | 14139 | 2 | 16416 | 3700 | 2 | EL6021_M181 |  | BITVAL
VZC6401K40 | VEGA GANTRY PLC X80-5 : CARD SLOT 10 (ETOR) DEFAULT | AL |  | RES | 1 | C;A | [12 empty] | C;A | [13 empty] | NOT | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3008 | 10 | 14139 | 4 | 16416 | 3700 | 4 | EL6021_M181 |  | BITVAL
VZC6401D | VEGA GANTRY PLC : PLC DEFAULT SYNTHESIS | AL |  | RES | 1 | A |  | K | [10 empty] | A | [13 empty] | NOT | 1000 |  | CV0G X80 HVAC Gantry PLC Infos (HVAC01) | HVAC |  | 7 |  |  | 3009 | 0 | 14140 | 0 | 16416 | 3702 | 0 | EL6021_M181 |  | BITVAL
VZC6401DC1 | VEGA GANTRY PLC : PRIMARY / SECONDARY STATUS LINK DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3009 | 1 | 14140 | 2 | 16416 | 3702 | 2 | EL6021_M181 |  | BITVAL
VZC6401DC2 | VEGA GANTRY PLC : PRIMARY / SECONDARY DATABASE SYNCHRONIZATION LINK DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3009 | 2 | 14140 | 4 | 16416 | 3702 | 4 | EL6021_M181 |  | BITVAL
VZC6401DC3 | VEGA GANTRY PLC : SECONDARY PLC / LOCAL SUPERVISION COMMUNICATION DEFAULT | AL |  | RES | 1 | A | [12 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3009 | 3 | 14140 | 6 | 16416 | 3702 | 6 | EL6021_M181 |  | BITVAL
VZC6401DC4 | VEGA GANTRY PLC : GANTRY / BUNKER COMMUNICATION DEFAULT | AL |  | RES | 1 | A |  | K | [10 empty] | A | [13 empty] | NOT | 1000 | VZC6401D | HVAC01 | HVAC |  | 7 |  |  | 3009 | 4 | 14140 | 8 | 16416 | 3703 | 0 | EL6021_M181 |  | BITVAL
VRP6401D3 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 401.3 (CTA 2) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3011 | 0 | 14143 | 0 | 16416 | 3708 | 0 | EL6021_M181 |  | BITVAL
VRP6401D4 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 401.4 (CTA 2) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13;HVAC15 | HVAC |  | 7 |  |  | 3011 | 1 | 14143 | 2 | 16416 | 3708 | 2 | EL6021_M181 |  | BITVAL
VFN6401D2 | VEGA GANTRY PLC : FAN CTA P02 DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3011 | 2 | 14143 | 4 | 16416 | 3708 | 4 | EL6021_M181 |  | BITVAL
VFN6401DI2 | VEGA GANTRY PLC : FAN CTA P02 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3011 | 3 | 14143 | 6 | 16416 | 3708 | 6 | EL6021_M181 |  | BITVAL
VFN6401DF2 | VEGA GANTRY PLC : FAN CTA P02 FILTER DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3011 | 4 | 14143 | 8 | 16416 | 3709 | 0 | EL6021_M181 |  | BITVAL
VFN6401DR2 | VEGA GANTRY PLC : FAN CTA P02 DEW POINT DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3011 | 5 | 14143 | 10 | 16416 | 3709 | 2 | EL6021_M181 |  | BITVAL
VFN6202D | VEGA GANTRY PLC : FAN CTA P04 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3011 | 6 | 14143 | 12 | 16416 | 3709 | 4 | EL6021_M181 |  | BITVAL
VFN6202DI | VEGA GANTRY PLC : FAN CTA P04 DISCORDANCE | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3011 | 7 | 14143 | 14 | 16416 | 3709 | 6 | EL6021_M181 |  | BITVAL
VFN6202DF | VEGA GANTRY PLC : FAN CTA P04 FILTER DEFAULT | AL |  | RES | 1 | C |  | K | [10 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3011 | 8 | 14144 | 0 | 16416 | 3710 | 0 | EL6021_M181 |  | BITVAL
VFN6202DR | VEGA GANTRY PLC : FAN CTA P04 DEW POINT DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3011 | 12 | 14144 | 8 | 16416 | 3711 | 0 | EL6021_M181 |  | BITVAL
VRP6201D5 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 201.5 (CTA 4) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14;HVAC15 | HVAC |  | 7 |  |  | 3011 | 13 | 14144 | 10 | 16416 | 3711 | 2 | EL6021_M181 |  | BITVAL
VRP6301D1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 301.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3011 | 14 | 14144 | 12 | 16416 | 3711 | 4 | EL6021_M181 |  | BITVAL
VRP6501D1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 501.1 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3011 | 15 | 14144 | 14 | 16416 | 3711 | 6 | EL6021_M181 |  | BITVAL
VRP6301D2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 301.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3012 | 0 | 14145 | 0 | 16416 | 3712 | 0 | EL6021_M181 |  | BITVAL
VRP6501D2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 501.2 DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3012 | 1 | 14145 | 2 | 16416 | 3712 | 2 | EL6021_M181 |  | BITVAL
VVV6501DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 501.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3012 | 4 | 14145 | 8 | 16416 | 3713 | 0 | EL6021_M181 |  | BITVAL
VVV6801DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 801.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3012 | 5 | 14145 | 10 | 16416 | 3713 | 2 | EL6021_M181 |  | BITVAL
VVV6301DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 301.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3012 | 6 | 14145 | 12 | 16416 | 3713 | 4 | EL6021_M181 |  | BITVAL
VVV6201DT1 | VEGA GANTRY PLC : FAN COIL (CAREL) 201.1 TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3012 | 7 | 14145 | 14 | 16416 | 3713 | 6 | EL6021_M181 |  | BITVAL
VCT6401DT2 | VEGA GANTRY PLC : FAN CTA P02 PULSE TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3012 | 8 | 14146 | 0 | 16416 | 3714 | 0 | EL6021_M181 |  | BITVAL
VCT6202DT | VEGA GANTRY PLC : FAN CTA P04 PULSE TEMPERATURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3012 | 9 | 14146 | 2 | 16416 | 3714 | 2 | EL6021_M181 |  | BITVAL
VFN6401DP2 | VEGA GANTRY PLC : FAN CTA P02 DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3012 | 10 | 14146 | 4 | 16416 | 3714 | 4 | EL6021_M181 |  | BITVAL
VFN6202DP | VEGA GANTRY PLC : FAN CTA P04 DIFFERENTIAL PRESSURE DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3012 | 11 | 14146 | 6 | 16416 | 3714 | 6 | EL6021_M181 |  | BITVAL
VVU6401D | VEGA GANTRY PLC : INTERNAL HVAC DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3013 | 0 | 14147 | 0 | 16416 | 3716 | 0 | EL6021_M181 |  | BITVAL
VZC6401Z1 | VEGA GANTRY PLC : VALIDITY DEFAULT TEMPERATURE RETURN AIR FAN CTA P03 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 0 | 14153 | 0 | 16416 | 3728 | 0 | EL6021_M181 |  | BITVAL
VZC6401Z2 | VEGA GANTRY PLC : VALIDITY DEFAULT HYGROMETRY RETURN AIR FAN CTA P03 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 1 | 14153 | 2 | 16416 | 3728 | 2 | EL6021_M181 |  | BITVAL
VZC6401Z3 | VEGA GANTRY PLC : VALIDITY DEFAULT AMBIENT HYGROMETRY FAN CTA P03 (LEVEL 20M) | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 2 | 14153 | 4 | 16416 | 3728 | 4 | EL6021_M181 |  | BITVAL
VZC6401Z4 | VEGA GANTRY PLC : VALIDITY DEFAULT AMBIENT TEMPERATURE FAN CTA P03 (LEVEL 20M) | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 3 | 14153 | 6 | 16416 | 3728 | 6 | EL6021_M181 |  | BITVAL
VZC6401Z5 | VEGA GANTRY PLC : VALIDITY DEFAULT DEW POINT TEMPERATURE FAN CTA P01 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 4 | 14153 | 8 | 16416 | 3729 | 0 | EL6021_M181 |  | BITVAL
VZC6401Z6 | VEGA GANTRY PLC : VALIDITY DEFAULT PULSE TEMPERATURE FAN CTA P01 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 5 | 14153 | 10 | 16416 | 3729 | 2 | EL6021_M181 |  | BITVAL
VZC6401Z7 | VEGA GANTRY PLC : VALIDITY DEFAULT DEW POINT TEMPERATURE FAN CTA P03 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 6 | 14153 | 12 | 16416 | 3729 | 4 | EL6021_M181 |  | BITVAL
VZC6401Z8 | VEGA GANTRY PLC : VALIDITY DEFAULT PULSE TEMPERATURE FAN CTA P03 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 7 | 14153 | 14 | 16416 | 3729 | 6 | EL6021_M181 |  | BITVAL
VZC6401Z9 | VEGA GANTRY PLC : VALIDITY DEFAULT AMBIENT TEMPERATURE FAN CTA P01 ROOMS ANNEXES (LEVEL 40M) | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 8 | 14154 | 0 | 16416 | 3730 | 0 | EL6021_M181 |  | BITVAL
VZC6401Z10 | VEGA GANTRY PLC : VALIDITY DEFAULT AMBIENT HYGROMETRY FAN CTA P01 ROOMS ANNEXES (LEVEL 40M) | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 9 | 14154 | 2 | 16416 | 3730 | 2 | EL6021_M181 |  | BITVAL
VZC6401Z11 | VEGA GANTRY PLC : VALIDITY DEFAULT POSITION COMMAND FRESH AIR MOTORISED DAMPER 102.1 (CTA 3) | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 10 | 14154 | 4 | 16416 | 3730 | 4 | EL6021_M181 |  | BITVAL
VZC6401Z12 | VEGA GANTRY PLC : VALIDITY DEFAULT POSITION COMMAND RETURN AIR MOTORISED DAMPER 102.3 (CTA 3) | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 11 | 14154 | 6 | 16416 | 3730 | 6 | EL6021_M181 |  | BITVAL
VZC6401Z13 | VEGA GANTRY PLC : VALIDITY DEFAULT AMBIENT TEMPERATURE FAN CTA P04 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 12 | 14154 | 8 | 16416 | 3731 | 0 | EL6021_M181 |  | BITVAL
VZC6401Z14 | VEGA GANTRY PLC : VALIDITY DEFAULT AMBIENT HYGROMETRY FAN CTA P04 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 13 | 14154 | 10 | 16416 | 3731 | 2 | EL6021_M181 |  | BITVAL
VZC6401Z15 | VEGA GANTRY PLC : VALIDITY DEFAULT POSITION COMMAND FRESH AIR MOTORISED DAMPER FAN CTA P04 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 14 | 14154 | 12 | 16416 | 3731 | 4 | EL6021_M181 |  | BITVAL
VZC6401Z16 | VEGA GANTRY PLC : VALIDITY DEFAULT POSITION COMMAND RETURN AIR MOTORISED DAMPER FAN CTA P04 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3018 | 15 | 14154 | 14 | 16416 | 3731 | 6 | EL6021_M181 |  | BITVAL
VZC6401Z17 | VEGA GANTRY PLC : VALIDITY DEFAULT DEW POINT TEMPERATURE FAN CTA P02 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3019 | 0 | 14155 | 0 | 16416 | 3732 | 0 | EL6021_M181 |  | BITVAL
VZC6401Z18 | VEGA GANTRY PLC : VALIDITY DEFAULT PULSE TEMPERATURE FAN CTA P02 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3019 | 1 | 14155 | 2 | 16416 | 3732 | 2 | EL6021_M181 |  | BITVAL
VZC6401Z19 | VEGA GANTRY PLC : VALIDITY DEFAULT DEW POINT TEMPERATURE FAN CTA P04 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3019 | 2 | 14155 | 4 | 16416 | 3732 | 4 | EL6021_M181 |  | BITVAL
VZC6401Z20 | VEGA GANTRY PLC : VALIDITY DEFAULT PULSE TEMPERATURE FAN CTA P04 | AL | N | RES | 1 | C | [12 empty] | C | [13 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3019 | 3 | 14155 | 6 | 16416 | 3732 | 6 | EL6021_M181 |  | BITVAL
ZSA6628SH1 | ETAT CONNEXION MODULE ALERT HLCS | AL | N | INT | 0 | Z | [12 empty] | Z | [13 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | Boolean
ZSA6629SH1 | FAULT SYNCHRONISATION MODULE SAAA HLCS-1 | AL | N | INT | 0 | Z | [12 empty] | Z | [13 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | Boolean
ZSA6633SH1 | FAULT COMMUNICATION AVEC ALERT LIEN | AL | N | INT | 0 | Z |  | R | [10 empty] | Z | [16 empty] | VMC03 External IF VMC | VMC (Z) | NEW
ZNC6633NH1 | FAULT COMMUNICATION AVEC SCSI LIEN 1 | AL | N | INT | 0 | Z | [12 empty] | Z | [16 empty] | VMC03 External IF VMC | VMC (Z)
SCG6DMA | DETG MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCG6000DMA; | Y |  |  |  | DG61 DG62 DG63 Detection Gaz (Node) | Detection Gaz (DG)
SCG6000DMA | MASTER ALARM DETG BUNKER ET GANTRY | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | DG61DMA; DG62DMA; DG63DMA; DG60DMA | Y |  |  |  | DETG Bunker et Gantry (group) | Detection Gaz (DG)
DG71DMA | SYNTHESE ALARME DETG LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCG7000DB ; SCG7000DH ; SCG7000D ; SCG7000DT ; SCG7000DA ; SCG7000DP ; SCG7000DA ; SCG7001DB ; SCG7001DH ; SCG7002DB ; SCG7002DH ; SCG7003DB ; SCG7003DH ; SCG7004DB ; SCG7004DH ; SDO7001W1 ; SDO7001W2 ; SDO7001N ; SDO7001D ; SDO7002W1 ; SDO7002W2 ; SDO7002N ; SDO7002D ; SDO7003W1 ; SDO7003W2 ; SDO7003N ; SDO7003D ; SDO7004W1 ; SDO7004W2 ; SDO7004N ; SDO7004D | Y |  |  |  | DG71 | Detection Gaz (DG)
DG60DMA | SYNTHESE DEFAUT API DETG DI | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZS6002 ; SZX6020 ; SZX6021 ; SZS6003 ; SZX6030 ; SZX6031 ; SZR001 ; SZR002 ; SZP6003 ; SZP6004 ; SZP6005 ; SZP6006 ; SZG6000; | Y |  |  |  | DG60; DG61; DG62; DG63; DG65; DI61; DI62; DI63; DI64; DI65; DI70; DI72; EI66; EI67; EI68; EI71 | Detection Gaz (DG); Detection Incendie (DI); Extinction Incendie (EI)
DG61DMA | MASTER ALARM DEFAUT DETG MAT ET SOUS SOL BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCG6012D ; SCG6014D ; SCG6015D ; SCG6016D ; SCG6010D ; SCG6013D ; SCG6017D ; SCG6018D ; SCG6019D ; SCG6020D ; SDO6010D ; SDO6010W ; SDO6011D ; SDO6011W ; SDO6012D ; SDO6012W ; SDO6013D ; SDO6013W ; SDO6014D ; SDO6014W ; SDO6015D ; SDO6015W ; SDO6016D ; SDO6016W ; SDO6017D ; SDO6017W ; SDO6018D ; SDO6018W ; SDO6019D ; SDO6019W ; SDO6020D ; SDO6020W ; SDO6029D ; SDO6029W ; SCG6021D ; SCG6000D ; SCG6001D ; SZP6003 ; SZP6005 ; SZP6006 | Y |  |  |  | DG61 | Detection Gaz (DG)
DG62DMA | MASTER ALARM DEFAUT DETG REZ DE CHAUSSEE BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SDO6001D ; SDO6001W ; SDO6002D ; SDO6002W ; SDO6003D ; SDO6003W ; SDO6004D ; SDO6004W ; SDO6005D ; SDO6005W ; SDO6006D ; SDO6006W ; SDO6007D ; SDO6007W ; SDO6008D ; SDO6008W ; SDO6009D ; SDO6009W ; SCG6012D ; SCG6014D ; SCG6015D ; SCG6016D ; SCG6010D ; SCG6013D ; SCG6017D ; SCG6018D ; SCG6019D ; SCG6020D ; SCG6021D ; SCG6000D ; SCG6001D ; SDO6010D ; SDO6010W ; SZP6003 ; SZP6005 ; SZP6006 | Y |  |  |  | DG62 | Detection Gaz (DG)
DG63DMA | MASTER ALARM DEFAUT DETG PORTIQUE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SDO6021D ; SDO6021W ; SDO6022D ; SDO6022W ; SDO6023D ; SDO6023W ; SDO6024D ; SDO6024W ; SDO6025D ; SDO6025W ; SDO6026D ; SDO6026W ; SDO6027D ; SDO6027W ; SDO6028D ; SDO6028W ; SCG6012D ; SCG6014D ; SCG6015D ; SCG6016D ; SCG6010D ; SCG6013D ; SCG6017D ; SCG6018D ; SCG6019D ; SCG6020D ; SCG6021D ; SCG6000D ; SCG6001D ; SDO6010D ; SDO6010W ; SZP6003 ; SZP6005 ; SZP6006 | Y |  |  |  | DG63 | Detection Gaz (DG)
SCK6DMA | DI MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCK6000DMA;SCK7000DMA; SCK8000DMA | Y |  |  |  | DI61 DI62 DI63 DI64 DI65 DI70 DI72 Detection Incendie (Node) Detin Pandora (group) | Detection Incendie (DI)
SCK6000DMA | MASTER ALARM DETIN BUNKER ET GANTRY | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | DI61DMA; DI62DMA; DI63DMA; DI64DMA; DI65DMA; DI70DMA; DI72DMA | Y |  |  |  | DETIN Bunker et Gantry (group) | Detection Incendie (DI)
SCK7000DMA | MASTER ALARM DETIN LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | DI73DMA; DI74DMA; DI75DMA; DI76DMA; DI77DMA; DI78DMA;DI79DMA | Y |  |  |  | DETIN Lagrange (group) | Detection Incendie (DI)
DI73DMA | SYNTHESE ALARME DETIN ZONES LAGRANGE 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7001W ; SZI7002W ; SZI7003W ; SZI7004W ; SZI7005W ; SZI7006W ; SZI7007W ; SZI7008W ; SZI7009W ; SZI7010W ; SZI7011W ; SZI7012W ; SCK7001D ; SZI7000D ; SZI7000DE ; SCK7000DH ; SCK7000D | Y |  |  |  | DI73 | Detection Incendie (DI)
DI74DMA | SYNTHESE ALARME DETIN ZONES LAGRANGE 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7013W ; SZI7014W ; SZI7015W ; SZI7016W ; SZI7017W ; SZI7018W ; SZI7019W ; SZI7020W ; SZI7021W ; SZI7022W ; SZI7023W ; SZI7024W ; SZI7025W ; SZI7026W ; SCK7001D ; SZI7000D ; SZI7000DE ; SCK7000DH ; SCK7000D | Y |  |  |  | DI74 | Detection Incendie (DI)
DI75DMA | SYNTHESE ALARME DETIN HA LAGRANGE 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7101W ; SZI7102W ; SZI7103W ; SZI7104W ; SZI7105W ; SZI7108W ; SZI7112W ; SZI7114W ; SZI7119W ; SZI7120W ; SZI7122W ; SZI7125W ; SZI7126W ; SZI7131W ; SCK7001D ; SZI7000D ; SZI7000DE ; SCK7000DH ; SCK7000D; | Y |  |  |  | DI75 | Detection Incendie (DI)
DI76DMA | SYNTHESE ALARME DETIN HA LAGRANGE 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7133W ; SZI7134W ; SZI7135W ; SZI7136W ; SZI7137W ; SZI7138W ; SZI7139W ; SZI7145W ; SZI7146W ; SZI7147W ; SZI7148W ; SZI7151W ; SZI7155W ; SZI7156W ; SCK7001D ; SZI7000D ; SZI7000DE ; SCK7000DH ; SCK7000D; | Y |  |  |  | DI76 | Detection Incendie (DI)
DI77DMA | SYNTHESE ALARME DETIN HA MAGAZINS ET ATELIERS LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7106W ; SZI7107W ; SZI7110W ; SZI7116W ; SZI7117W ; SZI7121W ; SZI7123W ; SZI7128W ; SZI7129W ; SZI7130W ; SZI7140W ; SZI7143W ; SZI7144W ; SCK7001D ; SZI7000D ; SZI7000DE ;SCK7000DH ; SCK7000D; | Y |  |  |  | DI77 | Detection Incendie (DI)
DI78DMA | SYNTHESE ALARME DETIN HA VESTIAIRES COULOIRS ET BUREAUX LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7109W ; SZI7111W ; SZI7113W ; SZI7115W ; SZI7118W ; SZI7124W ; SZI7127W ; SZI7132W ; SZI7141W ; SZI7142W ; SZI7149W ; SZI7150W ; SCK7001D ; SZI7000D ; SZI7000DE ; SCK7000DH ; SCK7000D; | Y |  |  |  | DI78 | Detection Incendie (DI)
DI61DMA | MASTER ALARM DETIN REX DE CHAUSSEE BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6038W ; SZI6039W ; SZI6040W ; SZI6041W ; SZI6042W ; SZI6043W ; SZI6044W ; SZI6045W ; SCK6001DT ; SCK6001DA ; SCK6001D ; SZI6000D ; SZI6022W ; SZI6023W ; SZI6024W ; SZI6025W ; SZI6026W ; SZI6027W ; SZI6108W ; SZI6109W ; SZR001 ; SZR002 | Y |  |  |  | DI61 | Detection Incendie (DI)
DI62DMA | MASTER ALARM DETIN REX DE CHAUSSEE BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6048W ; SZI6049W ; SZI6050W ; SZI6051W ; SZI6052W ; SZI6053W ; SZI6054W ; SZI6055W ; SZI6056W ; SZI6057W ; SZI6046W ; SZI6047W ; SZI6028W ; SZI6029W ; SZI6030W ; SZI6031W ; SZI6032W ; SCK6001DT ; SCK6001DA ; SCK6001D ; SZI6000D ; SZR6001 ; SZR6002 | Y |  |  |  | DI62 | Detection Incendie (DI)
DI63DMA | MASTER ALARM DETIN SOUS SOL BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6014W ; SZI6015W ; SZI6016W ; SZI6017W ; SZI6110W ; SZI6111W ; SZI6112W ; ; SZI6006W ; SZI6007W ; SZI6008W ; SZI6009W ; SZI6010W ; SZI6011W ; SZI6012W ; SZI6013W ; SZI6114W ; SZI6115W ; SZI6116W ; SZI6117W ; SZI6001W ; SZI6002W ; SZI6003W ; SCK6001DT ; SCK6001DA ; SCK6001D ; SZI6000D ; SZR6001 ; SZR6002 | Y |  |  |  | DI63 | Detection Incendie (DI)
DI64DMA | MASTER ALARM DETIN PORTIQUE MOBILE ZLV 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6066W ; SZI6067W ; SZI6070W ; SZI6071W ; SZI6079W ; SZI6080W ; SZI6058W ; SZI6059W ; SZI6064W ; SZI6065W ; SZI6068W ; SZI6069W ; SZI6072W ; SZI6073W ; SZI6074W ; SZI6075W ; SZI6076W ; SZI6077W ; SZI6078W ; SCK6001DT ; SCK6001DA ; SCK6001D ; SZI6000D ; SZR6001 ; SZR6002 | Y |  |  |  | DI64 | Detection Incendie (DI)
DI65DMA | MASTER ALARM DETIN PORTIQUE MOBILE ZLV 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6093W ; SZI6094W ; SZI6095W ; SZI6060W ; SZI6061W ; SZI6081W ; SZI6082W ; SZI6083W ; SZI6084W ; SZI6085W ; SZI6086W ; SZI6087W ; SZI6088W ; SZI6089W ; SZI6090W ; SZI6091W ; SZI6092W ; SZI6096W ; SZI6097W ; SCK6001DT ; SCK6001DA ; SCK6001D ; SZI6000D ; SZP6003 ; SZR6001 ; SZR6002; SZI6113W | Y |  |  |  | DI65 | Detection Incendie (DI)
DI70DMA | MASTER ALARM DETIN INTERSITE ZLV | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6098W ; SZI6100W ; SZI6103W ; SZI6102W ; SZI6104W ; SZI6105W ; SCK6001DT ; SCK6001DA ; SCK6001D ; SZR6001 ; SZR6002 ; SZI6000D | Y |  |  |  | DI70 | Detection Incendie (DI)
DI72DMA | MASTER ALARM DETIN SOUS SOL BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI6004W; SZI6005W; SZI6106W; SZR6002 | Y |  |  |  | DI72 | Detection Incendie (DI)
SCX6DMA | EXTI MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCX6000DMA;EI77DMA | Y |  |  |  | EI66 EI67 EI68 EI69 EI71 Extinction Incendie (Node) | Extinction Incendie (EI)
SCX6000DMA | MASTER ALARM EXTIN BUNKER ET GANTRY | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EI66DMA; EI67DMA; EI68DMA; EI69DMA; EI71DMA | Y |  |  |  | EXTIN Bunker et Gantry (group) | Extinction Incendie (EI)
EI77DMA | SYNTHESE ALARM EXTIN UPS BATT ET TECH LAU LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7016W; SZI7017W; SZI7004W; SZI7005W; SZI7001GE; SCX7002GE; SBT7001O; SBT7002O; SWE7001F; SWE7001O; SWE7002F1; SWE7002F2; SWE7002O1; SWE7002O2; | Y |  |  |  | EI77 | Extinction Incendie (EI)
EI66DMA | MASTER ALARM EXTIN REZ DE CHAUSSEE BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCX6006GE ; SBT6006O ; SCX6007GE ; SBT6007O ; SCX6008GE ; SBT6008O ; SZI6046W ; SZI6047W ; SZI6038W ; SZI6039W ; SZI6040W ; SZI6041W ; SZI6042W ; SZI6043W ; SZI6044W ; SZI6045W ; VRU6101D1 ; VRU6103D ; VRU6111D ; VZC6126K25 ; SZR6002 | Y |  |  |  | EI66 | Extinction Incendie (EI)
EI67DMA | MASTER ALARM EXTIN REZ DE CHAUSSEE BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCX6009GE ; SBT6009O ; SCX6010GE ; SBT6010O ; SCX6011GE ; SBT6011O ; SCX6012GE ; SBT6012O ; SCX6013GE ; SBT6013O ; SZI6048W ; SZI6049W ; SZI6050W ; SZI6051W ; SZI6052W ; SZI6053W ; SZI6054W ; SZI6055W ; SZI6056W ; SZI6057W ; VRU6112D ; VRU6113D ; VRU6115D ; VRU6116D ; VZC6126K25 ; SZR6002 | Y |  |  |  | EI67 | Extinction Incendie (EI)
EI68DMA | MASTER ALARM EXTIN SOUS SOL BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCX6002GE ; SBT6002O ; SCX6003GE ; SBT6003O ; SCX6004GE ; SBT6004O ; SCX6005GE ; SBT6005O ; SZI6006W ; SZI6007W ; SZI6008W ; SZI6009W ; SZI6010W ; SZI6011W ; SZI6012W ; SZI6013W ; SZI6114W ; SZI6115W ; SZI6116W ; SZI6117W ; SZR6002 ; VZC6126K25 ; VRU6004D ; VRU6007D ; VRU6008D ; VRU6009D | Y |  |  |  | EI68 | Extinction Incendie (EI)
EI69DMA | MASTER ALARM EXTIN PORTIQUE ZLV | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCX6021GE ; SBT6021O ; SCX6022GE ; SBT6022O ; SCX6023GE ; SBT6023O ; SZI6066W ; SZI6067W ; SZI6070W ; SZI6071W ; SZI6079W ; SZI6080W ; SZR6002 ; ZZE6004 ; ZZE6005 ; ZZE6006 ; VZC6401K28 ; VRU6101D2 ; VRU6201D ; VRU6502D | Y |  |  |  | EI69 | Extinction Incendie (EI)
EI71DMA | MASTER ALARM EXTIN SOUS SOL BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCX6001GE ; SBT6001O ; SZI6014W ; SZI6015W ; SZI6016W ; SZI6017W ; SZI6110W ; SZI6111W ; SZI6112W ; SZI6113W ; SZR6002 ; VZC6126K25 ; VRU6213D | Y |  |  |  | EI71 | Extinction Incendie (EI)
WZC6DMA | OEV MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | W60DMA ; W61DMA | Y |  |  |  | W61 Optique et Video (Node) | Optique et Video (W)
W60DMA | SYNTHESE DEFAUT API OPTIQUE ET VIDEO | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | WZS6002 ; WZX6020 ; WZX6021 ; WZS6003 ; WZX6030 ; WZX6031 ; WZM6004 ; WZM6005 ; WZM6006 ; WZM6007 ; WZM6010 ; WZM6011 ; WZM6012 ; WZG6000;ZJG6105 | Y |  |  |  | W60 | Optique et Video (W)
W61DMA | MASTER ALARM OPTIQUE SHELTERS VEGA | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | WZC6000D ; WBE6001AU ; WBE6002AU ; WBE6003AU ; WCO6001N ; WCO6002N ; WCO6003N ; WCO6004N ; WCO6005N ; WZM6004 ; WZM6005 ; WZM6006 | Y |  |  |  | W61 | Optique et Video (W)
SAV6DMA | DVT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | DG64DMA; DG65DMA | Y |  |  |  | DG64 DG65 Detection Vapeurs Toxiques (Node) | Detection Vapeurs Toxiques (DVT)
DG64DMA | SYNTHESE DEFAUT DVT PORTIQUE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SAV6015W ; SAV6017W ; SAV6004W ; SAV6006W ; SAV6014W ; SAV6003W ; SAV6021W ; SAV6020W ; SAV6019W ; SAV6018W ; SAV6016W ; SAV6005W ; SAV6007W ; SAV6011W ; SAV6008W ; SAV6012W ; SAV6009W ; SAV6013W ; SAV6010W ; SOR6003 ; SOR6004 ; SOR6005 ; SOR6006 ; SOR6007 ; SOR6008 ; SOR6009 ; SOR6010 ; SOR6011 ; SOR6012 ; SOR6013 ; SOR6014 ; SOR6015 ; SOR6016 ; SOR6017 ; SOR6018 ; SOR6019 ; SOR6020 ; SOR6021 ;SAV6022W; SOR6022; SAV6023W; SOR6023; SAV6024W; SOR6024 | Y |  |  |  | DG64 | Detection Vapeurs Toxiques (DVT)
DG65DMA | SYNTHESE DEFAUT DVT CONCENTRATION LIE CL8 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCG6000D ; SCG6001D ; SCG6010D ; SCG6021D ; SCG6013D ; SCG6012D ; SCG6014D ; SCG6015D ; SCG6016D ; SCG6017D ; SCG6018D ; SCG6019D ; SCG6020D ; SAV6102D ; SAV6104D ; SAV6106D ; SAV6108D ; SDU6032D ; SDU6033D ; SDU6036D ; SDU6037D ; SDU6040D ; SDU6041D ;SDU6044D ; SDU6045D ; SDU6046D ; SDU6047D ; SDU6047W ; SDU6046W ; SDU6045W ; SDU6044W ;SDU6041W ; SDU6040W ; SDU6037W ; SDU6036W ; SDU6033W ; SDU6032W ; SAV6100D ; SOR6102 ; SOR6202 ; SOR6104 ; SOR6204 ; SOR6106 ; SOR6206 ; SOR6108 ; SOR6208 ; SOR6109 ; SOR6209 ; SZP6003 ; SZP6004 ; SZP6005 ; SZP6006; ZZS6003 | Y |  |  |  | DG65 | Detection Vapeurs Toxiques (DVT)
JSYD6MA | MG WIRINGS MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | JSY6913 JSY6914 ZZZ6030K00 | Y |  |  |  | TBD | HVAC BNKR NODE
VZC6000DMA | SYNTHESE DEFAUT HVAC PLCs | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126DMA; VZC6401DMA; VSY6401W1 ; VSY6401W2 ; VSY6900W1 ; VSY6900W2 ; VSY6126W1 ; VSY6126W2 ; VSY6600W1 ; VSY6600W2 ; VAE6401D400 ; VAE6401D3 ; VAE6401D24 ; VZC6401DC1 ; VZC6401DC2 ; VZC6401DC3 ; VZC6401DC4 ; VAE6126D400 ; VAE6126D3 ; VAE6126D24 ; VAE6126D48 ; VZC6126DC1 ; VZC6126DC2 ; VZC6126DC3 ; VZC6126DC4 ; VVV6126DC1 ; VVV6401DC1 ; VVV6126DC2 ; VVV6401DC2 ; VZC6401D ; VZC6126D; GPP6001DC2; GPP6002DC2; GPP6004DC1; GPP6005DC1; GGF6012DC; GGF6003DC | Y |  |  |  | HVAC01 | HVAC
VZC6126DMA | SYNTHESE DEFAUT CV0B BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126SD1 VZC6126SD2 VZC6126D1 VZC6126D2 VZC6126K02 VZC6126K03 VZC6126K04 VZC6126K05 VZC6126K06 VZC6126K07 VZC6126K08 VZC6126K10 VZC6126K13 VZC6126K14 VZC6126K15 VZC6126K18 VZC6126K19 VZC6126K20 VZC6126K21 VZC6126K22 VZC6126K25 VZC6126K26 VZC6126K27 VZC6126K28 VZC6126K30 VZC6126K31 VZC6126K32 VZC6126K34 VZC6126K35 VZC6126K36 VZC6126K38 VZC6126K39 VZC6126K40;ZJG6109;ZJG6110 | Y |  |  |  | CV0B X80 HVAC Bunker PLC (HVAC01 popup) | HVAC
VZC6401DMA | SYNTHESE DEFAUT CV0G X80 GANTRY | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6401SD1 VZC6401SD2 VZC6401D1 VZC6401D2 VZC6401K02 VZC6401K03 VZC6401K04 VZC6401K05 VZC6401K06 VZC6401K07 VZC6401K08 VZC6401K09 VZC6401K11 VZC6401K12 VZC6401K13 VZC6401K05 VZC6401K18 VZC6401K19 VZC6401K20 VZC6401K21 VZC6401K27 VZC6401K28 VZC6401K05 VZC6401K30 VZC6401K31 VZC6401K32 VZC6401K34 VZC6401K05VZC6401K35 VZC6401K36 VZC6401K38 VZC6401K05VZC6401K39 VZC6401K40;ZJG6111;ZJG6112 | Y |  |  |  | CV0G X80 HVAC Gantry PLC (HVAC01 popup) | HVAC
HVAC02DMA | SYNTHESE DEFAUT SURVEILLANCE EQUIPEMENTS | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VSY6600W1 VSY6600W2; VSY6900W1; VSY6900W2 | Y |  |  |  | HVAC02 | HVAC
HVAC03DMA | SYNTHESE DEFAUT PRODUCTION EC EG | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | GGF6DMA; VZC6126K28 ; VZC6126Z9 ; VZC6126Z4 ; VZC6126Z1 ; VZC6126K19 ; VZC6126K20 ; VZC6126K25 ; VZC6126K26 ; VZC6126K39 ; VZC6126Z11 ; VZC6126Z12 ; VZC6126Z21 ; VZC6126Z17 ; VZC6126Z3 ; VZC6126Z22 ; GPP6012DT2 ; GPP6045DT1 ; CPP6045DT3 ; GPP6001D2 ; GPP6001DI2 ; GPP6012DP3 ; GPP6002D2 ; GPP6002DI2 ; GPP6004D1 ; GPP6004DI1 ; GPP6045DP1 ; GPP6005D1 ; GPP6005DI1 ; GRT6118D ; GPP6001D ; GPP6002D ; GPP6003D ; CPP6045DP3 ; GFF6118D ; CPP6004D3 ; CPP6004DI3 ; CPP6005D3 ; CPP6005DI3 ; GCP6001D ; GCP6002D ; GCP6003D ; CPP6001D ; CPP6002D ; CPP6003D ; CRT6118D ; GPP6001DC2 ; GPP6002DC2 ; GPP6004DC1 ; GPP6005DC1 ; GPP6001DI ; GPP6002DI ; GPP6003DI ; GGF6DMA ; CTR6001F1 ; GTR6001F1 ; GTR6034F2 ; GTR6012F2 ; GTR6045F1 ; CTR6045F3 ; CTR6034F2 ; GQR6001F1 ; GQR6034F2 ; CPR6004F3 ; GTR6001G1 ; GTR6002G1 ; GTR6003G1 ; GTR6001G2 ; GTR6002G2 ; GTR6003G2 ; GTR6001G3 ; GTR6002G3 ; GTR6003G3; GT6401V; GT6126V; CVM6001D; CVM6002D; CVM6003D; GCP6001DI; GCP6002DI; GCP6003DI | Y |  |  |  | HVAC03 | HVAC
GGF6DMA | GROUPES FROIDS MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | GGF6012DC GGF6003DCV | Y |  |  |  | Détails Groupes Froids (HVAC03 popup) | HVAC
HVAC04DMA | BUNKER CTA MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126K19 ; VZC6126K20 ; VZC6126K25 ; VZC6126K38 ; VZC6126K39 ; VZC6126Z2 ; VZC6126Z13 ; VZC6126Z14 ; VZC6126Z3 ; VZC6126Z25 ; VZC6126Z26 ; VZC6126Z27 ; GPP6045DT1 ; GPP6012DT2 ; VFN6003D ; VFN6003DI ; VRP6127D2 ; VRP6127D1 ; VRP6118D3 ; VCT6001DF ; VCT6001DR ; VCT6001D ; VCT6001DI ; VRP6118D4 ; VRP6118D1 ; VCT6002DF ; VCT6002DR ; VCT6002D ; VCT6002DI ; VRP6118D2 ; VCT6001DT ; VCT6002DT ; VFN6000D ; VFN6000DI ; GTR6045F1 ; GTR6034F2 ; GER6001T ; VTR6001T ; CER6001T ; GER6002T ; VTR6002T ; CER6002T ; VTR6001S ; VTR6002S | Y |  |  |  | HVAC04 | HVAC
HVAC05DMA | MASTER ALARM LOCAUX BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126K25 ; VZC6126K26 ; VZC6126K39 ; VRP6118D4 ; VRP6118D2 ; VRP6004D1 ; VRU6004D ; VRP6004D2 ; VRP6007D1 ; VRU6007D ; VRP6007D2 ; VRP6008D1 ; VRU6008D ; VRP6008D2 ; VRP6009D1 ; VRU6009D ; VRP6009D2 ; VRP6002D1 ; VRP6013D1 ; VRU6213D ; VRP6213D ; VRP6101D11 ; VRU6101D1 ; VRP6101D12 ; VRP6103D1 ; VRU6103D ; VRP6103D2 ; VRP6111D1 ; VRU6111D ; VRP6111D2 ; VRP6112D1 ; VRU6112D ; VRP6112D2 ; VRP6113D1 ; VRU6113D ; VRP6113D2 ; VRP6115D1 ; VRU6115D ; VRP6115D2 ; | Y |  |  |  | HVAC05 | HVAC
HVAC06DMA | MASTER ALARM LOCAUX BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126K25 ; VZC6126K26 ; VZC6126K39 ; VRP6118D4 ; VRP6118D2 ; VRP6116D1 ; VRU6116D ; VRP6116D2 ; VRP6106D1 ; VRP6100D2 ; VRP6104D1 ; VRP6104D2 ; VRP6107D1 ; VRP6107D2 ; VRP6117D1 ; VRP6012D1 ; VRP6012D2 ; | Y |  |  |  | HVAC06 | HVAC
HVAC07DMA | MASTER ALARM TEMPERATURE LOCAUX BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VCN6002DC1 ; VCN6002DC2 ; VCN6004DC1 ; VCN6004DC2 ; VCN6007DC1 ; VCN6007DC2 ; VCN6013DC1 ;VCN6101DC1 ; VCN6101DC2 ; VCN6103DC1 ; VCN6103DC2 ; VVV6001DT1 ; VVV6002DT3 ; VCN6002DT2 ; VVV6002DT2 ; VCN6002DT1 ; VVV6004DT1 ; VCN6004DT2 ;VVV6004DT3 ; VCN6004DT1 ;VCN6007DT1 ; VCN6007DT2 ;VVV6006DT1 ; VVV6006DT2 ;VVV6006DT3 ;VVV6008DT1 ; VVV6009DT1 ; VVV6012DT1 ; VVV6012DT2 ; VCN6013DT1 ; VVV6100DT1 ; VVV6100DT2 ; VCN6101DT2 ; VCN6101DT1 ; VCN6103DT1 ; VCN6103DT2 ; VVV6104DT1 ; VVV6105DT1 ; VVV6105DT2 ; VCN6002D1 ; VCN6002D2 ; VCN6004D1 ; VCN6004D2 ;VTR6001V1 ; VTR6002V3 ; VTR6002A2 ; VTR6002V2 ; VTR6002A1 ; VTR6004V1 ; VTR6004A2 ; VTR6004A1 ; VTR6004V3 ; VTR6006V1 ; VTR6006V2 ; VTR6006V3 ; VTR6007A1 ; VTR6007A2 ; VTR6008V1 ; VTR6009V1 ; VTR6012V1 ; VTR6012V2 ; VTR6013A1 ; VTR6100V1 ; VTR6100V2 ; VTR6101A1 ; VTR6101A2 ; VTR6103A1 ; VTR6103A2 ; VTR6104V1 ; VTR6105V1 ; VTR6105V2;VVV6106DT1 ; VVV6106DT2 ; VVV6106DT3 ; VVV6106DT4 ; VVV6107DT1 ; VVV6108DT1 ; VVV6108DT2 ; VVV6108DT3 ; VTR6106V1 ; VTR6106V2 ; VTR6106V3 ; VTR6106V4 ; VTR6107V1 ; VTR6108V1 ; VTR6108V2 ; VTR6108V3 | Y |  |  |  | HVAC07 | HVAC
HVAC08DMA | MASTER ALARM TEMPERATURE LOCAUX BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VCN6113DC1 ; VCN6113DC2 ; VCN6116DC1 ; VCN6116DC2;VVV6111DT1 ; VVV6112DT1 ; VCN6113DT2 ; VCN6113DT1 ; VVV6115DT1 ; VVV6115DT2 ; VVV6115DT3 ; VVV6115DT4 ; VCN6116DT1 ; VCN6116DT2 ; VVV6117DT1 ; VVV6117DT2 ; VVV6118DT1 ; VVV6118DT2 ; VVV6118DT3 ; VVV6118DT4 ; VVV6118DT5 VTR6111V1 ; VTR6112V1 ; VTR6113A2 ; VTR6113A1 ; VTR6115V1 ; VTR6115V2 ; VTR6115V3 ; VTR6115V4 ; VTR6116A1 ; VTR6116A2 ; VTR6117V1 ; VTR6117V2 ; VTR6118V1 ; VTR6118V2 ; VTR6118V3 ; VTR6118V4 ; VTR6118V5 | Y |  |  |  | HVAC08 | HVAC
HVAC09DMA | MASTER ALARM TEMPERATURE LOCAUX BUNKER 3 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VVV6120DT1 ; VVV6121DT1 ; VVV6121DT3 ; VVV6122DT1 ; VVV6121DT2 ; VVV6126DT1 ; VTR6120V1 ; VTR6121V1 ; VTR6121V3 ; VTR6122V1 ; VTR6121V2 ; VTR6126V1 ; | Y |  |  |  | HVAC09 | HVAC
HVAC10DMA | MASTER ALARM CLAPETS COUPE FEU | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126K27 ; VZC6126K40 ; VCF6003D1 ; VCF6004D1 ; VCF6006D1 ; VCF6012D1 ; VCF6012D3 ; VCF6013D3 ; VCF6100D1 ; VCF6103D1 ; VCF6103D2 ; VCF6111D1 ; VCF6117D2 ; VCF6117D1 ; VCF6118D1 ; VCF6001D1 ; VCF6003D3 ; VCF6003D2 ; VCF6006D2 ; VCF6007D1 ; VCF6007D2 ; VCF6008D1 ; VCF6008D2 ; VCF6009D1 ; VCF6012D2 ; VCF6013D1 ; VCF6013D2 ; VCF6100D2 ; VCF6106D1 ; VCF6108D1 ; VCF6111D2 ; VCF6112D1 ; VCF6113D1 ; VCF6115D1 ; VCF6115D2 ; VCF6115D3 ; VCF6116D1 ; VCF6118D2 ; VCF6126D1 ; | Y |  |  |  | HVAC10 | HVAC
HVAC11DMA | ALARMES NIVEAUX 1 ET 2 BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VRU6004D;VRU6007D;VRU6008D;VRU6009D;VRU6213D;VRU6101D1;VRU6103D;VRU6111D;VRU6112D;VRU6113D;VRU6115D;VRU6116D | Y |  |  |  | HVAC11 | HVAC
HVAC12DMA | MASTER ALARM COMMANDE ET CONFIGURATION BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126D ; VVU6126D ; VVU6106D ; VVU6127D ; VUM6126V | Y |  |  |  | HVAC12 | HVAC
HVAC13DMA | MASTER ALARM PORTIQUE CTA LOCAUX ANNEXES | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126K19 ; VZC6126Z1 ; VZC6126Z2 ; VZC6126Z27; VZC6401K20 ; VZC6401K27 ; VZC6401K28 ; VZC6401K40 ; VZC6401Z5 ; VZC6401Z6 ; VZC6401Z17 ; VZC6401Z18 ; GPP6012DT2 ; VRP6401D1 ; VFN6401DF1 ; VFN6401DR1 ; VFN6401D1 ; VFN6401DI1 ; VCT6401DP1 ; VRP6401D2 ; VRP6401D3 ; VFN6401DF2 ; VFN6401DR2 ; VFN6401D2 ; VFN6401DI2 ; VFN6401DP2 ; VRP6401D4 ; VCT6401DT1 ; VCT6401DT2 ; GTR6012F2 ; GTR6034F2; VTR6401 | Y |  |  |  | HVAC13 | HVAC
HVAC14DMA | MASTER ALARM PORTIQUE CTA HALL D INTEGRATION | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6126K19 ; VZC6126Z1 ; VZC6126Z2 ; VZC6126Z27 ; VZC6401K19 ; VZC6401K20 ; VZC6401K21 ; VZC6401K27 ; VZC6401K28 ; VZC6401K40 ; VZC6401Z1 ; VZC6401Z2 ; VZC6401Z3 ; VZC6401Z4 ; VZC6401Z7 ; VZC6401Z8 ; VZC6401Z9 ; VZC6401Z10 ; VZC6401Z11 ; VZC6401Z12 ; VZC6401Z15 ; VZC6401Z16 ; VZC6401Z19 ; VZC6401Z20 ; GPP6012DT2 ; VT6401D1 ; VT6102D ; VH6401D1 ; VH6102D ; VFN6202DF ; VFN6202DR ; VFN6202D ; VFN6202DI ; VFN6202DP ; VRP6201D5 ; VAR6102DH ; VAR6102DT ; VFN6102DF ; VFN6102DR ; VFN6102D ; VFN6102DI ; VCT6102DP ; VRP6102D5 ; VCT6202DT ; VCT6102DT ; GTR6012F2 ; VTR6401 ; VTR6102 ; GTR6034F2 ; VHR6401 ; VHR6102 ; VTR6102 ; VHR6102 ; VTR6401 ; VHR6401 ; | Y |  |  |  | HVAC14 | HVAC
HVAC15DMA | MASTER ALARM PORTIQUE LOCAUX | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VRP6401D2 ; VRP6401D4 ; VRP6502D1 ; VRU6502D ; VRP6502D2 ; VRP6201D3 ; VRU6201D ; VRP6201D2 ; VRP6101D21 ; VRU6101D2 ; VRP6101D22 ; VRP6501D1 ; VRP6501D2 ; VRP6301D1 ; VRP6301D2 ; VRP6201D5 ; VRP6102D5 ; VRP6999D1 ; VFN6999D ; VFN6999DI ; VCT6999DP ; VRP6999D2 ; VRP6701D1 ; VZN6701D ; VFN6701D ; VFN6701DI ; VCT6701DP ; VRP6701D3 ; VRP6601D1 ; VZU6601D ; VRP6601D2 ; VFN6601D ; VFN6601DI ; VCT6601DP ; VRP6601D3; VRP6701D2; ZZN6014 | Y |  |  |  | HVAC15 | HVAC
HVAC16DMA | ALARMES NIVEAUX 1 ET 2 PORTIQUE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VRU6502D;VRU6201D;VRU6101D2;VZU6601D;VZN6701D; | Y |  |  |  | HVAC16 | HVAC
HVAC17DMA | MASTER ALARM PORTIQUE COMMANDE ET CONFIGURATION | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6401D ; VZC6126D ; VUM6401V ; VVU6401D | Y |  |  |  | HVAC17 | HVAC
HVAC18DMA | MASTER ALARM TEMPERATURE LOCAUX PORTIQUE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VVV6401DC1 ; VVV6401DC2 ;VVV6101DT1 ; VVV6102DT1 ; VVV6201DT1 ; VVV6202DT1 ; VVV6301DT1 ; VVV6301DT2 ; VVV6401DT1 ; VVV6501DT1 ; VVV6502DT1 ; VVV6801DT1; VTR6401 | Y |  |  |  | HVAC18 | HVAC
VZC6DMA | HVAC SYNTHESE DEFAUT | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6001DMA VZC7001DMA VZC8001DMA | Y |  |  |  | HVAC (Node) | HVAC
VZC6001DMA | HVAC BUNKER ET GANTRY SYNTHESE DEFAUT | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VZC6000DMA VZC6126DMA VZC6401DMA HVAC02DMA HVAC03DMA GGF6DMA HVAC04DMA HVAC05DMA HVAC06DMA HVAC07DMA HVAC08DMA HVAC09DMA HVAC10DMA HVAC11DMA HVAC12DMA HVAC13DMA HVAC14DMA HVAC15DMA HVAC16DMA HVAC17DMA HVAC18DMA ; | Y |  |  |  | HVAC Bunker et Gantry (group) | HVAC
VZC7001DMA | HVAC LAGRANGE SYNTHESE DEFAUT | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | HVAC19DMA HVAC20DMA HVAC21DMA HVAC23DMA | Y |  |  |  | HVAC Lagrange (group) | HVAC
HVAC19DMA | SYNTHESE DEFAUT HVAC LAGRANGE TEMPERATURE 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VTR7005A1 ; VTR7005A2 ; VCN7005DT1 ; VCN7005DT2 ; VVV7010DT1 ; VVV7010DT2 ; VVV7010DE1 ; VVV7010DE2 ; VVV7010DN1 ; VVV7010DN2 ; VTR7010V1 ; VTR7010V2 ; VVV7013D1 ; VVV7013D2 ; VTR7013V1 ; VTR7013V2; VCN7005M201; VCN7005M202; VVV7010M210; VVV7010M202; VVV7013M201; VVV7013M202; | Y |  |  |  | HVAC19 (HVAC Lagrange group) | HVAC
HVAC20DMA | SYNTHESE DEFAUT HVAC LAGRANGE TEMPERATURE 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VVV7008D1 ; VVV7008DT1 ; VVV7008DE1 ; VVV7008DN1 ; VTR7008V1 ; VVV7011D1 ; VVV7011DT1 ; ; VVV7011DE1 ; ; VVV7011DN1 ; VTR7011V1 ; VVV7012D1 ; VVV7012DT1 ; VVV7012DE1 ; ; VVV7012DN1 ;VTR7012V1 ; VVV7006D1 ; VVV7006DT1 ; VVV7006DE1 ; ; VVV7006DN1 ; VTR7006V1 | Y |  |  |  | HVAC20 (HVAC Lagrange group) | HVAC
HVAC21DMA | SYNTHESE DEFAUT HVAC LAGRANGE TEMPERATURE 3 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VTR7007V1 ; VTR7007V2 ; VTR7007V3 ; VTR7007V4 ; VTR7007V5 ; VTR7007V6 ; VTR7007V7 ; VTR7007V8 ; VVV7007DT1 ; VVV7007DT2 ; VVV7007DT3 ; VVV7007DT4 ; VVV7007DT5 ; VVV7007DT6 ; VVV7007DT7 ; VVV7007DT8 ; ; VVV7007DA7 ; VVV7007DA8 ; VVV7007DE1 ; VVV7007DE2 ; VVV7007DE3 ; VVV7007DE4 ; VVV7007DE5 ; VVV7007DE6 ; VVV7007DE7 ; VVV7007DE8 ; VVV7007DN1 ; VVV7007DN2 ; VVV7007DN3 ; VVV7007DN4 ; VVV7007DN5 ; VVV7007DN6 ; VVV7007DN7 ; VVV7007DN8 ; VVV7007DH7 ; VVV7007DH8 ; VVV7007DD7 ; VVV7007DD8 ; VVV7007DF7 ; VVV7007DF8 | Y |  |  |  | HVAC21 (HVAC Lagrange group) | HVAC
HVAC23DMA | SYNTHESE DEFAUT HVAC LAGRANGE CTA SALLE 20 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VSY7020W1 VSY7020W2 | Y |  |  |  | HVAC23 (HVAC Lagrange group) | HVAC
EZC6115DMA2 | TGBT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6115DMA1 ETH6100DMA ETH6101DMA EUL6100DMA EUL6101DMA EUL6200DMA | Y |  |  |  | Energie TGBT et UPS (Node) | Energie TGBT et UPS VEGA (E)
EZC6115DMA1 | DEFAUT API TGBT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6115D ; EZC6115K2 ; EZC6115K3 ; EZC6115K4 ; EZC6115K5 ; EZC6115K6 ; EZC6115K7 ; EZC6115K8 ; EZC6115K9 ; EZC6115K10 ; EZC6115K11 ; EZC6115K16 ; EZC6115K17 ; EZC6115K18 ; EZC6115K19 ; EZC6115;ZJG6107 | Y |  |  |  | E61, E62 E63 E64 E65 E60 | Energie TGBT et UPS VEGA (E)
ONX600DMA | CHATEAU D'EAU VEGA MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ONB6922 ONH6922; EZC6115K2 | Y |  |  |  | MG74 | Moyens Generaux VEGA (MG)
EUL6071DMA | UL7001 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL6071D1 ; EGB6071D1 ; EKM6071D1 ; EVC6071D1 ; EUL6071D2 ; EUL6071D3 ; EUL6071D4 ; EUL6071D5 ; EUL6071D6 ; ESY6071D1 ; EIR6071I1 ; EIR6071I2 ; EIR6071I3 ; EUR6071UB ; EFR6071 | Y |  |  |  | Infos Onduleur UL7001 (E63 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6072DMA | UL7002 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL6072D1 ; EGB6072D1 ; EKM6072D1 ; EVC6072D1 ; EUL6072D2 ; EUL6072D3 ; EUL6072D4 ; EUL6072D5 ; EUL6072D6 ; ESY6072D1 ; EIR6072I1 ; EIR6072I2 ; EIR6072I3 ; EUR6072UB ; EFR6072 | Y |  |  |  | Infos Onduleur UL7002 (E63 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6073DMA | UL7003 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL6073D1 ; EGB6073D1 ; EKM6073D1 ; EVC6073D1 ; EUL6073D2 ; EUL6073D3 ; EUL6073D4 ; EUL6073D5 ; EUL6073D6 ; ESY6073D1 ; EIR6073I1 ; EIR6073I2 ; EIR6073I3 ; EUR6073UB ; EFR6073 | Y |  |  |  | Infos Onduleur UL7003 (E63 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6074DMA | UL7004 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL6074D1 ; EGB6074D1 ; EKM6074D1 ; EVC6074D1 ; EUL6074D2 ; EUL6074D3 ; EUL6074D4 ; EUL6074D5 ; EUL6074D6 ; ESY6074D1 ; EIR6074I1 ; EIR6074I2 ; EIR6074I3 ; EUR6074UB ; EFR6074 | Y |  |  |  | Infos Onduleur UL7004 (E63 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6075DMA | UL7005 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EGB6075D1 ; EGB6075D2 ; EGB6075D3 ; EGB6075D4 ; EGB6075D5 ; EGB6075D6 ; EKM6075D1 ; EVC6075D1 ; EUL6075D2 ; EUL6075D3 ; EUL6075D4 ; EUL6075D5 ; EUL6075D6 ; ESY6075D1 ; EIR6075I1 ; EIR6075I2 ; EIR6075I3 ; EUR6075UB ; EFR6075 | Y |  |  |  | Infos UL7005 (E64 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6076DMA | UL7006 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6115K19 ; EGB6076D1 ; EGB6076D2 ; EGB6076D3 ; EGB6076D4 ; EGB6076D5 ; EGB6076D6 ; EKM6076D1 ; EVC6076D1 ; EUL6076D2 ; EUL6076D3 ; EUL6076D4 ; EUL6076D5 ; EUL6076D6 ; ESY6076D1 ; EIR6076I1 ; EIR6076I2 ; EIR6076I3 ; EUR6076UB ; EFR6076 | Y |  |  |  | Infos UL7006 (E64 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6077DMA | UL7007 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EVC6077D1 ; EUL6077D1 ; EUL6077D2 ; EUL6077D3 ; EUL6077D4 ; EUL6077D5 ; ESY6077D1 ; EIR6077I1 ; EIR6077I2 ; EIR6077I3 ; EUR6077UB ; EFR6077 | Y |  |  |  | E65; Convertisseur 60Hz (E65 popup) | CONTOUR CAT III B E63
EUL6001DMA | CAT IIIA UPS MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6091D; EWR6091PF; EIR6091I1; EIR6091I2; EIR6091I3; EUR6091V1; EUR6091V2; EUR6091V3; EUR609112; EUR609123; EUR609131; EFR6091; EWR6091S | Y |  |  |  | Mesures Arrivee TGBT CAT 3A (E63 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6002DMA | CAT IIIB UPS MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6092D; EWR6092PF; EIR6092I1; EIR6092I2; EIR6092I3; EUR6092V1; EUR6092V2; EUR6092V3; EUR609212; EUR609223; EUR609231; EFR6092; EWR6092S | Y |  |  |  | Mesures Arrivee TGBT CAT 3B (E63 popup) | Energie TGBT et UPS VEGA (E) - E63
EUL6100DMA | CLIENTS UPS MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6115K7 ESY6075D1 ESY6076D1 EUL6075DMA EUL6076DMA | Y |  |  |  | E64 | CONTOUR E62 TM7003
EUL6101DMA | CAT III UPS MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL6001DMA; EUL6002DMA; EUL6071DMA; EUL6072DMA; EUL6073DMA; EUL6074DMA; ESY6071D; ESY6072D; ESY6073D; ESY6074D; EZC6115K6; EQF6502D; EQF6702D | Y |  |  |  | E63
ETH6001DMA | TM 7001 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6083D ; EWR6083PF; EFR6083; EIR6083I1; EIR6083I2; EIR6083I3; EUR6083V1; EUR6083V2; EUR6083V3; EUR608312; EUR608323; EUR608331; | Y |  |  |  | E62; Infos Arrivee TM7001 (E62 popup) | Energie TGBT et UPS VEGA (E) - E62
ETH6002DMA | TM 7002 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6081D ; EWR6081PF ; EFR6081; EIR6081I1; EIR6081I2; EIR6081I3; EUR6081V1; EUR6081V2; EUR6081V3; EUR608112; EUR608123; EUR608131; | Y |  |  |  | E61; Infos Arrivee TM7002 (E61 popup) | Energie TGBT et UPS VEGA (E) - E61
ETH6003DMA | TM 7003 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6084D ; EWR6084PF ; EFR6084PF; EIR6084I1; EIR6084I2; EIR6084I3; EUR6084V1; EUR6084V2; EUR6084V3; EUR608412; EUR608423; EUR608431; | Y |  |  |  | E62; Infos Arrivee TM7003 (E62 popup) | Energie TGBT et UPS VEGA (E) - E62
ETH6004DMA | TM 7004 SYNTHESE DEFAUT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6082D ; EWR6082PF ; EFR6082; EIR6082I1; EIR6082I2; EIR6082I3; EUR6082V1; EUR6082V2; EUR6082V3; EUR608212; EUR608223; EUR608231; | Y |  |  |  | E61; Infos Arrivee TM7004 (E61 popup) | Energie TGBT et UPS VEGA (E) - E61
ETH6100DMA | TM TGBT MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ETH6002DMA; ETH6004DMA; EQF6000DMA; EZC6115K2 ; EZC6115K3 ; EUB6000AU ; EUB6002AU ; EUB6004AU ; ESO6002D ; ESA6001D ; EQF6003D ; EQF6003DE; ETH6002D1; ETH6002D2; ETH6002D3; ETH6004D1; ETH6004D2; ETH6004D3; EQF6001D; EQF6001DE; EQF6002D; EQF6002DE | Y |  |  |  | E61 | Energie TGBT et UPS VEGA (E)
ETH6101DMA | TM TGBT-C MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ETH6001DMA; ETH6003DMA; EZC6115K4; EUB6001AU; EUB6003AU; EUB6005AU; ESO6951D; ESA6951D; EQF6952D; EQF6952DE; ETH6001D1; ETH6001D2; ETH6001D3; ETH6003D1; ETH6003D3; ETH6003D3; EQF6950D; EQF6950DE; EQF6951D; EQF6951DE | Y |  |  |  | E62 | Energie TGBT et UPS VEGA (E)
EQF6000DMA | SYNTHESE DEFAUT MX DISJONCTEURS TGBT | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6115K2 ; EZC6115K3 ; EQF6001MO ; EQF6004MO ; EQF6006MO ; EQF6007MO ; EQF6008MO ; EQF6009MO ; EQF6010MO ; EQF6013MO ; EQF6016MO ; EQF6031MO ; EQF6032MO ; EQF6033MO | Y |  |  |  | Départ Supplementaires (E61 popup) | Energy TGBT et UPS VEGA (E)
EUL6200DMA | SYNTHESE DEFAUT CONVERTISSEUR 60Hz | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6115K6; ESY6077D1; EUL6077DMA | Y |  |  |  | E65 | Energy TGBT et UPS VEGA (E)
ESY6160DMA2 | MASTER ALARM DISTRIBUTION ET TGBT CLIM ZLV | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6003DMA ; ESY6001DMA ; ETH6005 ; ETV6005D ; EQL6005O ; ESY6000D ; ESY6001D; EQL6001O ; EQD6001O ; EQL6260O ; EQL6160O ; EQM6001O ; EQM6002O ; EQL6003O ; EQD6003O ; EZC6160K5; EZC6160K2 | Y |  |  |  | E69 | Energie 1D60 VEGA (E)
ESY6160DMA1 | MASTER ALARM DISTRIBUTION ET TGBT 1D60 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6142DMA ESY6242DMA ESY6002DMA ESY6004DMA ETH6005 ; ETV6005D ; EQL6005O ; ESY6000D ; EQL6260O ; EQL6160O ; EQM6001O ; EQM6002O ; EQL6142O ; EQD6142O ; EQL6242O ; EZC6160K5 ; EZC6160K2; EQD6242O ; EQL6002O ; EQD6002O ; EQL6004O ; EQD6004O | Y |  |  |  | E68 | Energie 1D60 VEGA (E)
EQF7320N | **TGBT 184-13-20 QF2001N MAIN SWITCH 1D21 OF STATUS | CR | O | FIL | 2 | E |  | E | [8 empty] | 0 | [15 empty] | MTCP | 500 |  | E74 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 0 | [7 empty] | BITVAL
EZC6160DMA | DEFAUT API 1D60 MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6160 ; EZC6160D ; EZC6160K2 ; EZC6160K3 ; EZC6160K5 ; EZC6160K6 ; EZC6160K7;ZJG6108 | Y |  |  |  | E72 | Energie 1D60 VEGA (E)
EQF7320R | **TGBT 184-13-20 QF2001R MAIN SWITCH REDUNDANT OF STATUS | CR | O | FIL | 2 | E |  | E | [8 empty] | 0 | [15 empty] | MTCP | 500 |  | E74 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 4 | [7 empty] | BITVAL
ESY6142DMA | SYNTHESE DEFAUT DEPART CAT. I 1D60 VERS 1D42 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6142D ; EIR6142I1 ; EIR6142I2 ; EIR6142I3 ; EUR6142V1 ; EUR6142V2 ; EUR6142V3 ; EUR614231 ; EUR614212 ; EUR614232 ; EWR6142 ; EFR6142 | Y |  |  |  | Départ Type 1 CAT 1 VERS 1D42 (E68 popup) | Energie 1D60 VEGA (E)
EQF7320C | **TGBT 184-13-20 CIRCUIT BREAKER CHAIN OF STATUS | CR | O | FIL | 2 | E |  | E | [8 empty] | 0 | [15 empty] | MTCP | 500 |  | E74 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 8 | [7 empty] | BITVAL
ESY6242DMA | SYNTHESE DEFAUT DEPART CAT. II 1D60 VERS 1D42 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6242D ; EIR6242I1 ; EIR6242I2 ; EIR6242I3 ; EUR6242V1 ; EUR6242V2 ; EUR6242V3 ; EUR624231 ; EUR624212 ; EUR624232 ; EWR6242 ; EFR6242 | Y |  |  |  | Départ Type 1 CAT 2 VERS 1D42 (E68 popup) | Energie 1D60 VEGA (E)
EQF7530 | **TD 184-05-30 OF STATUS | CR | N | FIL | 2 | E |  | E | [8 empty] | 0 | [15 empty] | MTCP | 500 |  | E73 | Energy TD (E) | LGRNG | 9 |  |  | 1027 | 12 | [7 empty] | BITVAL
ESY6002DMA | SYNTHESE DEFAUT DEPART CAT. II 1D60 VERS 1D61 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6002D ; EIR6002I1 ; EIR6002I2 ; EIR6002I3 ; EUR6002V1 ; EUR6002V2 ; EUR6002V3 ; EUR600231 ; EUR600212 ; EUR600232 ; EWR6002 ; EFR6002 | Y |  |  |  | Départ Type 2 CAT 1 VERS 1D61 (E68 popup) | Energie 1D60 VEGA (E)
EQF7531 | **TD 184-05-31 OF STATUS | CR | N | FIL | 2 | E |  | E | [8 empty] | 0 | [15 empty] | MTCP | 500 |  | E73 | Energy TD (E) | LGRNG | 9 |  |  | 1028 | 0 | [7 empty] | BITVAL
ESY6004DMA | SYNTHESE DEFAUT DEPART CAT. I 1D60 VERS 1D61 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6004D ; EIR6004I1 ; EIR6004I2 ; EIR6004I3 ; EUR6004V1 ; EUR6004V2 ; EUR6004V3 ; EUR600431 ; EUR600412 ; EUR600432 ; EWR6004 ; EFR6004 | Y |  |  |  | Départ Type 2 CAT 2 VERS 1D61 (E68 popup) | Energie 1D60 VEGA (E)
EQF7232 | **TD 184-13-32 OF STATUS | CR | N | FIL | 2 | E |  | E | [8 empty] | 0 | [15 empty] | MTCP | 500 |  | E73 | Energy TD (E) | LGRNG | 9 |  |  | 1028 | 4 | [7 empty] | BITVAL
ESY6001DMA | SYNTHESE DEFAUT DEPART CAT. II 1D60 VERS 1D61 CLIM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6001D ; EIR6001I1 ; EIR6001I2 ; EIR6001I3 ; EUR6001V1 ; EUR6001V2 ; EUR6001V3 ; EUR600131 ; EUR600112 ; EUR600132 ; EWR6001 ; EFR6001 | Y |  |  |  | Départ Type 2 CAT 1 VERS TGBT-C 1D61 (E69 popup) | Energie 1D60 VEGA (E)
ESY6003DMA | SYNTHESE DEFAUT DEPART CAT. I 1D60 VERS 1D61 CLIM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6003D ; EIR6003I1 ; EIR6003I2 ; EIR6003I3 ; EUR6003V1 ; EUR6003V2 ; EUR6003V3 ; EUR600331 ; EUR600312 ; EUR600332 ; EWR6003 ; EFR6003 | Y |  |  |  | Départ Type 2 CAT 2 VERS TGBT-C 1D61 (E69 popup) | Energie 1D60 VEGA (E)
ESY6160DMA3 | SYNTHESE DEFAUT ENERGY 1D60 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6160DMA1 ESY6160DMA2 EZC6160DMA | Y |  |  |  |  | Energie 1D60 VEGA (E)
EZC7000DMA | MASTER ALARM ENERGY LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL7000DMA EZC7325DMA;GE01DMA | Y |  |  |  | Energy Lagrange (Node) | Energy Lagrange (E)
EUL7000DMA | MASTER ALARM CATEGORIE 3 LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL7071DMA; EUL7072DMA; ESA7530; ESA7531; ESA7232; | Y |  |  |  | E73 | Energy Lagrange (E)
EUL7071DMA | SYNTHESE DEFAUT LAGRANGE UPS CAT A | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL7071D1 ; EGB7071D1 ; EKM7071D1 ; EVC7071D1 ; EUL7071D2 ; EUL7071D3 ; EUL7071D4 ; EUL7071D5 ; EKM7071F ; EFR7071 | Y |  |  |  | Lagrange UPS A (E73 popup) | Energy Lagrange (E)
EUL7072DMA | SYNTHESE DEFAUT LAGRANGE UPS CAT B | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EUL7072D1 ; EGB7072D1 ; EKM7072D1 ; EVC7072D1 ; EUL7072D2 ; EUL7072D3 ; EUL7072D4 ; EUL7072D5 ; EKM7072F ; EFR7072 | Y |  |  |  | Lagrange UPS B (E73 popup) | Energy Lagrange (E)
ZJP6103DMA | VMC FE BUNKER PLC MASTER ALARM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZJP6103 ZZZ6DMA0 ZZZ6DMA1 ZZZ6DMA2 ZZZ6DMA3 ZZZ6DMA4 ZZZ6DMA5 ZZZ6DMA6 ZZZ6DMA7 ZZZ6DMA8 ZZZ6DMA9 ZJE6103P1 ZJE6103P2 ZJA6103 ZJM6103 ZZZ6DMA10 | Y |  |  |  | VMC01 | CONTOUR VMC01 CHAIN 4
ZZZ6DMA0 | SYNTHESE MODULES VMC CHAINE 0 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6189M186 ZZZ6289M187 ZZZ6110EC0 | Y |  |  |  | Infos Chaine 0 (VMC01 button) | VMC(Z)
ZZZ6DMA1 | SYNTHESE MODULES EL1134 CHAINE 1 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC1 ZZZ6134M2 ZZZ6134M3 ZZZ6134M4 ZZZ6134M5 ZZZ6134M6 ZZZ6134M7 ZZZ6134M8 ZZZ6134M9 ZZZ6134M10 ZZZ6134M11 ZZZ6134M13 ZZZ6134M14 ZZZ6134M15 ZZZ6134M16 ZZZ6134M17 ZZZ6134M18 ZZZ6134M19 ZZZ6134M20 ZZZ6134M21 ZZZ6134M22 | Y |  |  |  | Infos Chaine 1 (VMC01 button) | VMC(Z)
ZZZ6DMA2 | SYNTHESE MODULES EL1134 CHAINE 2 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC2 ZZZ6134M24 ZZZ6134M25 ZZZ6134M26 ZZZ6134M27 ZZZ6134M28 ZZZ6134M29 ZZZ6134M30 ZZZ6134M31 ZZZ6134M32 ZZZ6134M33 ZZZ6134M35 ZZZ6134M36 ZZZ6134M37 ZZZ6134M38 ZZZ6134M39 ZZZ6134M40 ZZZ6134M41 ZZZ6134M42 ZZZ6134M43 ZZZ6134M44 | Y |  |  |  | Infos Chaine 2 (VMC01 button) | VMC(Z)
ZZZ6DMA3 | SYNTHESE MODULES EL1134 CHAINE 3 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZEC6100EC3 ZZZ6134M46 ZZZ6134M47 ZZZ6134M48 ZZZ6134M49 ZZZ6134M50 ZZZ6134M51 ZZZ6134M52 ZZZ6134M53 ZZZ6134M54 ZZZ6134M55 ZZZ6134M57 ZZZ6134M58 ZZZ6134M59 ZZZ6134M60 ZZZ6134M61 ZZZ6134M62 ZZZ6134M63 ZZZ6134M64 ZZZ6134M65 ZZZ6134M66 | Y |  |  |  | Infos Chaine 3 (VMC01 button) | VMC(Z)
ZZZ6DMA4 | SYNTHESE MODULES EL1134 CHAINE 4 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC4 ZZZ6134M68 ZZZ6134M69 ZZZ6134M70 ZZZ6134M71 ZZZ6134M72 ZZZ6134M73 ZZZ6134M74 ZZZ6134M75 ZZZ6134M76 ZZZ6134M77 ZZZ6134M79 ZZZ6134M80 ZZZ6134M81 ZZZ6134M82 ZZZ6134M83 ZZZ6134M84 ZZZ6134M85 ZZZ6134M86 ZZZ6134M87 ZZZ6134M88 | Y |  |  |  | Infos Chaine 4 (VMC01 button) | VMC(Z)
ZZZ6DMA5 | SYNTHESE MODULES EL1134 CHAINE 5 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC5 ZZZ6134M90 ZZZ6134M91 ZZZ6134M92 ZZZ6134M93 ZZZ6134M94 ZZZ6134M95 ZZZ6134M96 ZZZ6134M97 ZZZ6134M98 ZZZ6134M99 ZZZ6134M101 ZZZ6134M102 ZZZ6134M103 ZZZ6134M104 ZZZ6134M105 ZZZ6134M106 ZZZ6134M107 ZZZ6134M108 ZZZ6134M109 ZZZ6134M110 | Y |  |  |  | Infos Chaine 5 (VMC01 button) | VMC(Z)
ZZZ6DMA6 | SYNTHESE MODULES EL1134 CHAINE 6 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC6 ZZZ6134M112 ZZZ6134M113 ZZZ6134M114 ZZZ6134M115 ZZZ6134M116 ZZZ6134M117 ZZZ6134M118 ZZZ6134M119 ZZZ6134M120 ZZZ6134M121 ZZZ6134M123 ZZZ6134M124 ZZZ6134M125 ZZZ6134M126 ZZZ6134M127 ZZZ6134M128 ZZZ6134M129 ZZZ6134M130 ZZZ6134M131 ZZZ6134M132 | Y |  |  |  | Infos Chaine 6 (VMC01 button) | VMC(Z)
ZZZ6DMA7 | SYNTHESE MODULES EL1134 CHAINE 7 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC7 ZZZ6134M134 ZZZ6134M135 ZZZ6134M136 ZZZ6134M137 ZZZ6134M138 ZZZ6134M139 ZZZ6134M140 ZZZ6134M141 ZZZ6134M142 ZZZ6134M143 ZZZ6134M145 ZZZ6134M146 ZZZ6134M147 ZZZ6134M148 ZZZ6134M149 ZZZ6134M150 ZZZ6134M151 ZZZ6134M152 ZZZ6134M153 ZZZ6134M154 | Y |  |  |  | Infos Chaine 7 (VMC01 button) | VMC(Z)
ZZZ6DMA8 | SYNTHESE MODULES EL1134 CHAINE 8 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC8 ZZZ6134M156 ZZZ6134M157 ZZZ6134M158 ZZZ6134M159 | Y |  |  |  | Infos Chaine 8 (VMC01 button) | VMC(Z)
ZZZ6DMA9 | SYNTHESE MODULES CHAINE 9 | AL | N | CAL | 0 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC9 ZZZ6289M160 ZZZ6289M161 ZZZ6289M162 ZZZ6289M163 ZZZ6289M164 ZZZ6289M165 ZZZ6289M166 ZZZ6289M167 ZZZ6289M168 ZZZ6289M169 ZZZ6289M170 ZZZ6289M171 ZZZ6324M172 ZZZ6324M173 ZZZ6324M175 ZZZ6941M174 ZZZ6621M176 ZZZ6621M177 ZZZ6621M178 ZZZ6621M179 ZZZ6621M180 ZZZ6621M181 ZZZ6621M182 ZZZ6621M183 ZZZ6621M184 ZZZ6621M185 | Y |  |  |  | Infos Chaine 9 (VMC01 button) | VMC(Z)
ZCM6836DMA | SYNTHESE DEFAUT SWITCH BUNKER 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6836F1 ZCM6836F2 ZCM6836P1 ZCM6836P2 ZCM6836P3 ZCM6836P4 ZCM6836P5 ZCM6836P6 ZCM6836P7 ZCM6836P8 ZCM6836P9 ZCM6836P10 ZCM6836P11 ZCM6836P12 ZCM6836P13 ZCM6836P14 ZCM6836P15 ZCM6836P16 ZCM6836P17 ZCM6836P18 ZCM6836P19 ZCM6836P20 ZCM6836P21 ZCM6836P22 ZCM6836P23 ZCM6836P24 | Y |  |  |  | VMC02 | VMC(Z)
ZCM6837DMA | SYNTHESE DEFAUT SWITCH BUNKER 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6837F1 ZCM6837F2 ZCM6837P1 ZCM6837P2 ZCM6837P3 ZCM6837P4 ZCM6837P5 ZCM6837P6 ZCM6837P7 ZCM6837P8 ZCM6837P9 ZCM6837P10 ZCM6837P11 ZCM6837P12 ZCM6837P13 ZCM6837P14 ZCM6837P15 ZCM6837P16 ZCM6837P17 ZCM6837P18 ZCM6837P19 ZCM6837P20 ZCM6837P21 ZCM6837P22 ZCM6837P23 ZCM6837P24 | Y |  |  |  | VMC02 | VMC(Z)
ZCM6840DMA | SYNTHESE DEFAUT SWITCH PANDORA 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6840F1 ZCM6840F2 ZCM6840P1 ZCM6840P2 ZCM6840P3 ZCM6840P4 ZCM6840P5 ZCM6840P6 ZCM6840P7 ZCM6840P8 ZCM6840P9 ZCM6840P10 ZCM6840P11 ZCM6840P12 ZCM6840P13 ZCM6840P14 ZCM6840P15 ZCM6840P16 ZCM6840P17 ZCM6840P18 ZCM6840P19 ZCM6840P20 ZCM6840P21 ZCM6840P22 ZCM6840P23 ZCM6840P24 | Y |  |  |  | VMC02 | VMC(Z)
ZCM6841DMA | SYNTHESE DEFAUT SWITCH PANDORA 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6841F1 ZCM6841F2 ZCM6841P1 ZCM6841P2 ZCM6841P3 ZCM6841P4 ZCM6841P5 ZCM6841P6 ZCM6841P7 ZCM6841P8 ZCM6841P9 ZCM6841P10 ZCM6841P11 ZCM6841P12 ZCM6841P13 ZCM6841P14 ZCM6841P15 ZCM6841P16 ZCM6841P17 ZCM6841P18 ZCM6841P19 ZCM6841P20 ZCM6841P21 ZCM6841P22 ZCM6841P23 ZCM6841P24 | Y |  |  |  | VMC02 | VMC(Z)
ZCM6734DMA | SYNTHESE DEFAUT SWITCH LAGRANGE 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6734F1 ZCM6734F2 ZCM6734F3 ZCM6734F4 ZCM6734P1 ZCM6734P2 ZCM6734P3 ZCM6734P4 ZCM6734P5 ZCM6734P6 ZCM6734P7 ZCM6734P8 ZCM6734P9 ZCM6734P10 ZCM6734P11 ZCM6734P12 ZCM6734P13 ZCM6734P14 ZCM6734P15 ZCM6734P16 ZCM6734P17 ZCM6734P18 ZCM6734P19 ZCM6734P20 ZCM6734P21 ZCM6734P22 ZCM6734P23 ZCM6734P24 | Y |  |  |  | VMC02 | VMC(Z)
ZCM6735DMA | SYNTHESE DEFAUT SWITCH LAGRANGE 2 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6735F1 ZCM6735F2 ZCM6735F3 ZCM6735F4 ZCM6735P1 ZCM6735P2 ZCM6735P3 ZCM6735P4 ZCM6735P5 ZCM6735P6 ZCM6735P7 ZCM6735P8 ZCM6735P9 ZCM6735P10 ZCM6735P11 ZCM6735P12 ZCM6735P13 ZCM6735P14 ZCM6735P15 ZCM6735P16 ZCM6735P17 ZCM6735P18 ZCM6735P19 ZCM6735P20 ZCM6735P21 ZCM6735P22 ZCM6735P23 ZCM6735P24 | Y |  |  |  | VMC02 | VMC(Z)
ZCM683637DMA | SYNTHESE DEFAUT SWITCHES BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6836F1 ; ZCM6836F2 ; ZCM6836P1 ; ZCM6836P2 ; ZCM6836P3 ; ZCM6836P4 ; ZCM6836P5 ; ZCM6836P6 ; ZCM6836P7 ; ZCM6836P8 ; ZCM6836P9 ; ZCM6836P10 ; ZCM6836P11 ; ZCM6836P12 ; ZCM6836P13 ; ZCM6836P14 ; ZCM6836P15 ; ZCM6836P16 ; ZCM6836P17 ; ZCM6836P18 ; ZCM6836P19 ; ZCM6836P20 ; ZCM6836P21 ; ZCM6836P22 ; ZCM6836P23 ; ZCM6836P24 ; ZCM6837F1 ; ZCM6837F2 ; ZCM6837P1 ; ZCM6837P2 ; ZCM6837P3 ; ZCM6837P4 ; ZCM6837P5 ; ZCM6837P6 ; ZCM6837P7 ; ZCM6837P8 ; ZCM6837P9 ; ZCM6837P10 ; ZCM6837P11 ; ZCM6837P12 ; ZCM6837P13 ; ZCM6837P14 ; ZCM6837P15 ; ZCM6837P16 ; ZCM6837P17 ; ZCM6837P18 ; ZCM6837P19 ; ZCM6837P20 ; ZCM6837P21 ; ZCM6837P22 ; ZCM6837P23 ; ZCM6837P24 | Y |  |  |  | Etat switch Bunker (VMC02 popup) | VMC(Z)
ZCM684041DMA | SYNTHESE DEFAUT SWITCHES PANDORA | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6840F1 ; ZCM6840F2 ; ZCM6840P1 ; ZCM6840P2 ; ZCM6840P3 ; ZCM6840P4 ; ZCM6840P5 ; ZCM6840P6 ; ZCM6840P7 ; ZCM6840P8 ; ZCM6840P9 ; ZCM6840P10 ; ZCM6840P11 ; ZCM6840P12 ; ZCM6840P13 ; ZCM6840P14 ; ZCM6840P15 ; ZCM6840P16 ; ZCM6840P17 ; ZCM6840P18 ; ZCM6840P19 ; ZCM6840P20 ; ZCM6840P21 ; ZCM6840P22 ; ZCM6840P23 ; ZCM6840P24 ; ZCM6841F1 ; ZCM6841F2 ; ZCM6841P1 ; ZCM6841P2 ; ZCM6841P3 ; ZCM6841P4 ; ZCM6841P5 ; ZCM6841P6 ; ZCM6841P7 ; ZCM6841P8 ; ZCM6841P9 ; ZCM6841P10 ; ZCM6841P11 ; ZCM6841P12 ; ZCM6841P13 ; ZCM6841P14 ; ZCM6841P15 ; ZCM6841P16 ; ZCM6841P17 ; ZCM6841P18 ; ZCM6841P19 ; ZCM6841P20 ; ZCM6841P21 ; ZCM6841P22 ; ZCM6841P23 ; ZCM6841P24 | Y |  |  |  | Etat switch Pandora (VMC02 popup) | VMC(Z)
ZCM673435DMA | SYNTHESE DEFAUT SWITCHES LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6734F1 ; ZCM6734F2 ; ZCM6734F3 ; ZCM6734F4 ; ZCM6734P1 ; ZCM6734P2 ; ZCM6734P3 ; ZCM6734P4 ; ZCM6734P5 ; ZCM6734P6 ; ZCM6734P7 ; ZCM6734P8 ; ZCM6734P9 ; ZCM6734P10 ; ZCM6734P11 ; ZCM6734P12 ; ZCM6734P13 ; ZCM6734P14 ; ZCM6734P15 ; ZCM6734P16 ; ZCM6734P17 ; ZCM6734P18 ; ZCM6734P19 ; ZCM6734P20 ; ZCM6734P21 ; ZCM6734P22 ; ZCM6734P23 ; ZCM6734P24 ; ZCM6735F1 ; ZCM6735F2 ; ZCM6735F3 ; ZCM6735F4 ; ZCM6735P1 ; ZCM6735P2 ; ZCM6735P3 ; ZCM6735P4 ; ZCM6735P5 ; ZCM6735P6 ; ZCM6735P7 ; ZCM6735P8 ; ZCM6735P9 ; ZCM6735P10 ; ZCM6735P11 ; ZCM6735P12 ; ZCM6735P13 ; ZCM6735P14 ; ZCM6735P15 ; ZCM6735P16 ; ZCM6735P17 ; ZCM6735P18 ; ZCM6735P19 ; ZCM6735P20 ; ZCM6735P21 ; ZCM6735P22 ; ZCM6735P23 ; ZCM6735P24 | Y |  |  |  | Etat switch Lagrange (VMC02 popup) | VMC(Z)
ZCM6DMA | SYNTHESE DEFAUT SWITCH VMC | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZCM6836DMA ZCM6837DMA ZCM6838DMA ZCM6839DMA ZCM6840DMA ZCM6841DMA ZCM6734DMA ZCM6735DMA ZCM683637DMA ZCM683839DMA ZCM684041DMA ZCM673435DMA | Y |  |  |  | VMC02 | VMC(Z)
ZIF6DMA | DEFAUT CONNEXION IF VMC | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZSA6628SH1 ZSA6633SH1 ZNC6628NH1 ZNC6629NH1 ZNC6633NH1 ZNT6100 ZNT6632 ZNT6631 ZNT6632 | Y |  |  |  | VMC03 | VMC(Z)
ZVB6DMA | SYNTHESE DEFAUT VBRAIN | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZVB6951VH1 ZVB6951VH2 ZVB6952VH1 ZVB6952VH2 ZVB6953VH1 ZVB6953VH2 ZVB6954VH1 ZVB6954VH2 ZVB6950VH1 ZVB6950VH2 ZIS6955IH1 ZIS6955IH2 ZSQ6956QH1 ZSQ6956QH2 ZSQ6957QH1 ZSQ6957QH2 ZVB6958VH1 ZVB6958VH2 | Y |  |  |  | VMC04 | VMC(Z)
ZLG6DMA | SYNTHESE DEFAUT FE LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | LZS7100D ; LZS7101D ; LZS7102D ; LZS7200D ; LZS7201D ; LZS7202D ; LZS7300D ; LZS7301D ; LZS7302D ; LZS7400D ; LZS7401D ; LZS7402D ; LZE7000D ; LZE7100D ; LZR7003D2 ; LZR7004D2 ; LZR7005D2 ; LZR7006D2 LZR7003D3 ; LZR7004D3 ; LZR7005D3 ; LZR7006D3 ; LZR7007D3 ; LZM7000D1 ; LZM7000D2 ; LZM7000D3 ; LZL7000 ; LZA7000DA ; LZA7000DB ; LZL7000DS ; LZH7000D ; LZH7001D ; LZO7000D ; LZL7001D ; LZL7002D ; LZL7200D1 ; LZL7200D2; LZR7001D; LZR7002D; LZP7000D1; LZP7000D2; LZP7001D1; LZP7001D2; LZP7002D1; LZP7002D2; LZP7003D1; LZP7003D2; | Y |  |  |  | VMC05 | VMC(Z)
VMC6DMA | ERREUR GENERAL VMC | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZJP6103DMA ZCM6DMA ZIF6DMA ZVB6DMA ZJP8001DMA | Y |  |  |  | VMC (Node) | VMC(Z)
EZC6325DMA | SYNTHESE DEFAUT ENERGY TD GANTRY | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6970W ; ESY6980W ; EQF6632D ; EQF6832D ; EQF6642D ; EQF6842D ; ESA6672D ; EQF6872D ; EQF6657D ; EQF6857D ; ESA6121D ; ESA6122D ; ESA6132D ; ESA6133D ; EZC6115K8 ; EZC6325D121;EZC6325D120;EZC6325D130;EZC6325D131;EZC6325D230;EZC6325D231;EZC6325D530;EZC6325D531;EZC6325D630;EZC6325D631;EZC6325D41;EZC6325D43;EZC6325D132;EZC6325D133;EZC6325AD42;EZC6325BD42 | Y |  |  |  | E67 Energy TD Mobile Gantry | Energy TD
ESY6100DMA | SYNTHESE DEFAUT ENERGY TD BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6101D;ESY6102D;ESY6103D;ESY6104D;ESY6105D;ESY6106D;ESY6107D;ESY6108D;ESY6109D;ESY6110D;ESY6111D;ESY6112D;ESY6113D;ESY6114D;ESY6115D;ESY6116D;ESY6117D;ESY6118D;ESY6119D;ESY6120D;ESY6121D;EQF6162D;EQF6230D;EQF6232D;EQF6522D;EQF6537D;EQF6552D;EQF6567D;EQF6582D;EQF6597D;EQF6612D;EQF6627D;EQF6632D;EQF6642D;EQF6657D;EQF6667D;EQF6722D;EQF6737D;EQF6752D;EQF6782D;EQF6797;EQF6812D;EQF6832D;EQF6842D;EQF6872D;EQF6902D;EQF6917D;EQF6922D;ESA6012D;ESA6672D | Y |  |  |  | Energy TD Bunker | Energy TD
ESY6DMA | MASTER ALARM ENERGY TD | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | EZC6325DMA ESY6100DMA | Y |  |  |  | Energy TD (Node) | Energy TD
EZC7325DMA | SYNTHESE ALARME ENERGY LAGRANGE CATEGORIES I ET II | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESA7320N ; ESA7320R ; ESA7320C; | Y |  |  |  | E74 | Energy Lagrange
MG61DMA | MASTER ALARM RESEAU EAU PORTIQUE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZZE6006; ZZE6007; ZZE6010 |  |  |  |  | MG61 | Moyens Generaux
MG62DMA | SYNTHESE DEFAUT RINCAGE PORTIQUE MOBILE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | OVP6315O; ZZE6007; ZZE6008; ZZE6010 | Y |  |  |  | MG62 | Moyens Generaux
MG63DMA | SYNTHESE DEFAUT DELUGE LANCEUR ET LOCAL UDMH PORTIQUE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | OVP6303O OVP6304O OVP6305O; ZZE6007; ZZE6010 | Y |  |  |  | MG63 | Moyens Generaux
MG65DMA | SYNTHESE DEFAUT TRAITEMENT CARNEAUX VEGA | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | OOR6301 ONR6302 ONR6301 OVM6355O OVM6356O OPP6301D OPP6302D ONH6301 | Y |  |  |  | MG65 | Moyens Generaux
MG66DMA | SYNTHESE DEFAUT TRAITEMENT EFFLUENT GAZEAUX HYDRAZINE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | UNH6301 UNH6302; UMH6001; UCL6001D; UCL6001WD; UCL6002D; | Y |  |  |  | MG66 | Moyens Generaux
MG67DMA | SYNTHESE DEFAUT EFFLUENT GAZEAUX N2O4 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | NNH6301 NNH6302; NMH6001; NCL6001D; NCL6001WD; NCL6002D; | Y |  |  |  | MG67 | Moyens Generaux
MG68DMA | SYNTHESE DEFAUT MEASURES AZOTE ET AIR ZLV | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | RPR6305 HPR6310 RPD6301 RPR6301 RQR6301 HQR6301 AQR6301; ZZE6005; ZZE6010; ZZN6014 | Y |  |  |  | MG68 | Moyens Generaux
MG69DMA | SYNTHESE DEFAUT UNITE DE POMPAGE HYDRAZINE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | UVM6304O UPP6301D UNH6301 UNH6302 UPP6301D | Y |  |  |  | MG69 | Moyens Generaux
MG70DMA | SYNTHESE DEFAUT UNITE DE POMPAGE N204 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | NVM6304O NNH6301 NNH6302 | Y |  |  |  | MG70 | Moyens Generaux
MG71DMA | SYNTHESE DEFGAUT AE AR ET FEUX DE SIGNALISATION ZLV | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SCE6001D SCE6002D SSP6001D ; SFE6001M; SFE6002M; ZZP6001D; ZZP6002D; SCE6100D;SCE6101 | Y |  |  |  | MG71 | Moyens Generaux
MG72DMA | SYNTHESE ALARME AE ET AR LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZZP7001 ; ZZP7002 ; SCE7003 ; SCE7004 ; SCE7005 ; SCE7006 ; SCE7007 ; SCE7008 | Y |  |  |  | MG72 | Moyens Generaux
MG6DMA | SYNTHESE DEFAUT MOYENS GENERAUX VEGA | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | MG62DMA MG63DMA MG65DMA MG66DMA MG67DMA MG68DMA MG69DMA MG70DMA MG71DMA ONX600DMA | Y |  |  |  | Moyens Generaux (Node) | Moyens Generaux
VFN6DMA | MASTER ALARM SMOKE EXTRACTION | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VFN6000DMA; VFN7000DMA | Y |  |  |  | Smoke Extraction System (Node) | Smoke Extraction System (Node)
VFN7000DMA | SYNTHESE DEFAUT SMOKE EXTRACTION LAGRANGE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VCD7014D1; | Y |  |  |  | E75 Smoke Extraction Lagrange | Smoke Extraction System (Node)
VFN6000DMA | DEFAUT GENERAL SMOKE EXTRACTION SYSTEM | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VFN6002D1 VFN6004D1 VFN6007D1 VFN6008D1 VFN6009D1 VFN6010D1 VFN6012D1 VFN6013D1 VFN6014D1 VFN6101D1 VFN6109D1 VFN6111D1 VFN6112D1 VFN6113D1 VFN6117D1 VFN6002S2 VFN6004S2 VFN6007S2 VFN6008S2 VFN6009S2 VFN6010S2 VFN6012S2 VFN6013S2 VFN6014S2 VFN6101S2 VFN6109S2 VFN6113S2 VFN6117S2 | Y |  |  |  | E71 Smoke Extraction ZLV | HVAC
VG01DMA | SYNTHESE DEFAUT PROCESS FLUIDE PORTIQUE MOBILE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | JSY6002 HPR6310 RPR6305; ZZE6005; ZZE6006; ZZE6007; ZZE6008; ZZE6010; ZZN6014 | Y |  |  |  | VG01 | Process Fluide et Energie (VG)
VG02DMA | SYNTHESE DEFAUT VANNES PORTIQUE MOBILE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | OVP6303O OVP6304O OVP6305O | Y |  |  |  | VG02 | Process Fluide et Energie (VG)
VG03DMA | SYNTHESE DEFAUT PROCESS FLUIDE BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | AQR6301 HQR6301 RQR6301 RPR6301 RPD6301 JSY6001 SDC6001 | Y |  |  |  | VG03 | Process Fluide et Energie (VG)
VG04DMA | SYNTHESE DEFAUT PROCESS FLUIDE TRAITEMENT EFFLUENTS CARNEAUX | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ONR6301 ONR6302 OOR6301 OVM6355O OVM6356O OPP6301D OPP6302D ONH6301 | Y |  |  |  | VG04 | Process Fluide et Energie (VG)
VG05DMA | SYNTHESE DEFAUT PROCESS FLUIDE TRAITEMENT EFFLUENTS HYDRAZINE 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | UVM6304O UNH6301 UNH6302 UPP6301D | Y |  |  |  | VG05 | Process Fluide et Energie (VG)
VG06DMA | SYNTHESE DEFAUT PROCESS FLUIDE TRAITEMENT EFFLUENTS N2O4 1 | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | NVM6304O NNH6301 NNH6302 | Y |  |  |  | VG06 | Process Fluide et Energie (VG)
VG07DMA | SYNTHESE DEFAUT PROCESS ENERGIE FILAIRE MASSIF | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ESY6060D; ESY6031D; ESY6040D; ESY6041D; ESY6050D; ESY6051D; ESY6052D; ESY6053D; ESY6060D; ESY6061D; ESY6062D; ESY6063D; ESY6070D; ESY6080D; ESY6090D; ESY6100D | Y |  |  |  | VG07 | Process Fluide et Energie (VG)
VG08DMA | SYNTHESE DEFAUT PROCESS ENERGIE BUNKER | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | JSY6901 JSY6902 JSY6903 JSY6904 JSY6905 JSY6906 JSY6907 JSY6908 | Y |  |  |  | VG08 | Process Fluide et Energie (VG)
VG09DMA | SYNTHESE DEFAUT PROCESS ENERGIE GANTRY ET CLIM ZLV | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VSY6600W1 VSY6600W2; JSY6911 JSY6912 JSY6913 JSY6914 ESY6970W; ESY6980W; | Y |  |  |  | VG09 | Process Fluide et Energie (VG)
VG10DMA | SYNTHESE DEFAUT VEGA API FILAIRE | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | ZZZ6030K00 ; ZZS6002 ; ZZS6003 ; ZZE6004 ; ZZE6005 ; ZZE6006 ; ZZE6007 ; ZZE6008 ; ZZE6010 ; ZZT6010 ; ZZT6011 ; ZZT6012 ; ZZT6013 ; ZZN6014 ; ZZE6015; ZZC6009;ZJG6106 | Y |  |  |  | VG10; EI69DMA; MG61; MG62; MG63; MG64; MG68; VG01; DG64 | Moyens Generaux; Process Fluide et Energie (VG); Extinction Incendie (EI); Detection Vapeurs Toxiques (DVT)
VG6DMA | MASTER ALARM PROCESS FLUIDE ET ENERGIE VEGA | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | VG01DMA VG02DMA VG03DMA VG04DMA VG05DMA VG06DMA VG07DMA VG08DMA VG09DMA VG10DMA | Y |  |  |  | Process Fluide et Energie (Node) | Process Fluide et Energie (VG)
LZS7100D | LAGRANGE VMC FE SERIAL MODULE 1 ERROR | AL | N | RES | 2 | A |  | U | [10 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 0 | [7 empty] | BIT
LZS7101D | LAGRANGE VMC FE SERIAL MODULE 1 CHANNEL 0 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 1 | [7 empty] | BIT
LZS7102D | LAGRANGE VMC FE SERIAL MODULE 1 CHANNEL 1ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 2 | [7 empty] | BIT
LZS7200D | LAGRANGE VMC FE SERIAL MODULE 2 ERROR | AL | N | RES | 2 | A |  | U | [10 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 3 | [7 empty] | BIT
LZS7201D | LAGRANGE VMC FE SERIAL MODULE 2 CHANNEL 0 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 4 | [7 empty] | BIT
LZS7202D | LAGRANGE VMC FE SERIAL MODULE 2 CHANNEL 1ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 5 | [7 empty] | BIT
LZS7300D | LAGRANGE VMC FE SERIAL MODULE 3ERROR | AL | N | RES | 2 | A |  | U | [10 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 6 | [7 empty] | BIT
LZS7301D | LAGRANGE VMC FE SERIAL MODULE 3 CHANNEL 0 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 7 | [7 empty] | BIT
LZS7302D | LAGRANGE VMC FE SERIAL MODULE 3 CHANNEL 1ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 8 | [7 empty] | BIT
LZS7400D | LAGRANGE VMC FE SERIAL MODULE 4 ERROR | AL | N | RES | 2 | A |  | U | [10 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 9 | [7 empty] | BIT
LZS7401D | LAGRANGE VMC FE SERIAL MODULE 4 CHANNEL 0 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 10 | [7 empty] | BIT
LZS7402D | LAGRANGE VMC FE SERIAL MODULE 4 CHANNEL 1ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 11 | [7 empty] | BIT
LZE7000D | LAGRANGE VMC FE ETH BOARD NOC0301 MODULE 1 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 12 | [7 empty] | BIT
LZE7100D | LAGRANGE VMC FE ETH BOARD NOC0301 MODULE 2 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 13 | [7 empty] | BIT
LZR7003D2 | LAGRANGE VMC FE MODULE R2 SLOT 3 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 14 | [7 empty] | BIT
LZR7004D2 | LAGRANGE VMC FE MODULE R2 SLOT 4 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 901 | 15 | [7 empty] | BIT
LZR7005D2 | LAGRANGE VMC FE MODULE R2 SLOT 5 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 0 | [7 empty] | BIT
LZR7006D2 | LAGRANGE VMC FE MODULE R2 SLOT 6 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 1 | [7 empty] | BIT
LZR7003D3 | LAGRANGE VMC FE MODULE R3 SLOT 3 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 3 | [7 empty] | BIT
LZR7004D3 | LAGRANGE VMC FE MODULE R3 SLOT 4 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 4 | [7 empty] | BIT
LZR7005D3 | LAGRANGE VMC FE MODULE R3 SLOT 5 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 5 | [7 empty] | BIT
LZR7006D3 | LAGRANGE VMC FE MODULE R3 SLOT 6 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 6 | [7 empty] | BIT
LZR7007D3 | LAGRANGE VMC FE MODULE R3 SLOT 7 ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 7 | [7 empty] | BIT
LZM7000D1 | LAGRANGE VMC FE APP MISMATCH | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 8 | [7 empty] | BIT
LZM7000D2 | LAGRANGE VMC FE LOGIC MISMATCH | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 9 | [7 empty] | BIT
LZM7000D3 | LAGRANGE VMC FE FW MISMATCH | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 10 | [7 empty] | BIT
LZL7000 | LAGRANGE VMC FE DATA NOT UPDATED | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 11 | [7 empty] | BIT
LZA7000DA | LAGRANGE VMC FE PLCA ONLINE | AL | N | RES | 2 | A | [9 empty] | x==0 |  |  | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 12 | [7 empty] | BIT
LZA7000DB | LAGRANGE VMC FE PLCB ONLINE | AL | N | RES | 2 | A | [9 empty] | x==0 |  |  | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 13 | [7 empty] | BIT
LZL7000DS | LAGRANGE VMC FE MAST SYNCHRONIZED | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 14 | [7 empty] | BIT
LZH7000D | LAGRANGE VMC FE HSBY LINK ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 902 | 15 | [7 empty] | BIT
LZH7001D | LAGRANGE VMC FE HSBY SUPPLEMENTARY LINK ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 903 | 0 | [7 empty] | BIT
LZO7000D | LAGRANGE VMC FE EIO ERROR | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 903 | 5 | [7 empty] | BIT
LZL7001D | **LAGRANGE VMC FE LOCAL RACK STS | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 903 | 6 | [7 empty] | BIT
LZL7002D | LAGRANGE VMC FE MAST TASK STATE | AL | N | RES | 2 | A | [12 empty] | A | [13 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 903 | 8-9-10-11 | [7 empty] | BIT
LZL7200D1 | **DEFAUT LAGRANGE VMC FE ABL8RPM24200 1 | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 0 | [7 empty] | BIT
LZL7200D2 | **DEFAUT LAGRANGE VMC FE ABL8RPM24200 2 | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 2 | [7 empty] | BIT
LZR7001D | **REDUNDANCY MODULE 1 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 4 | [7 empty] | BIT
LZR7002D | **REDUNDANCY MODULE 2 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 6 | [7 empty] | BIT
LZP7000D1 | **PSU1 MODULE 1 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 8 | [7 empty] | BITVAL
LZP7000D2 | **PSU2 MODULE 1 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 10 | [7 empty] | BITVAL
LZP7001D1 | **PSU1 MODULE 2 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 12 | [7 empty] | BITVAL
LZP7001D2 | **PSU2 MODULE 2 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 907 | 14 | [7 empty] | BITVAL
LZP7002D1 | **PSU1 MODULE 3 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 908 | 0 | [7 empty] | BITVAL
LZP7002D2 | **PSU2 MODULE 3 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 908 | 2 | [7 empty] | BITVAL
LZP7003D1 | **PSU1 MODULE 4 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 908 | 4 | [7 empty] | BITVAL
LZP7003D2 | **PSU2 MODULE 4 FAULT | AL | N | RES | 2 | A | [9 empty] | x==1 |  |  | A | [9 empty] | NEQUAL |  |  |  | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 908 | 8 | [7 empty] | BITVAL
VVV7010DT1 | VC 1 SALLE 10 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 952 | 0 | [7 empty] | BITVAL
VVV7010DE1 | VC 1 SALLE 10 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 952 | 4 | [7 empty] | BITVAL
VVV7010DN1 | VC 1 SALLE 10 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 952 | 8 | [7 empty] | BITVAL
VVV7010DT2 | VC 2 SALLE 10 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 954 | 0 | [7 empty] | BITVAL
VVV7010DE2 | VC 2 SALLE 10 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 954 | 4 | [7 empty] | BITVAL
VVV7010DN2 | VC 2 SALLE 10 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 954 | 8 | [7 empty] | BITVAL
VVV7006DT1 | VC 1 SALLE 06 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 961 | 0 | [7 empty] | BITVAL
VVV7006DE1 | VC 1 SALLE 06 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 961 | 4 | [7 empty] | BITVAL
VVV7006DN1 | VC 1 SALLE 06 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 961 | 8 | [7 empty] | BITVAL
VVV7008DT1 | VC 1 SALLE 08 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 962 | 0 | [7 empty] | BITVAL
VVV7008DE1 | VC 1 SALLE 08 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 962 | 4 | [7 empty] | BITVAL
VVV7008DN1 | VC 1 SALLE 08 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 962 | 8 | [7 empty] | BITVAL
VVV7007DT1 | VC 1 SALLE 07 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 963 | 0 | [7 empty] | BITVAL
VVV7007DE1 | VC 1 SALLE 07 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 963 | 4 | [7 empty] | BITVAL
VVV7007DN1 | VC 1 SALLE 07 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 963 | 8 | [7 empty] | BITVAL
VVV7007DT2 | VC 2 SALLE 07 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 964 | 0 | [7 empty] | BITVAL
VVV7007DE2 | VC 2 SALLE 07 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 964 | 4 | [7 empty] | BITVAL
VVV7007DN2 | VC 2 SALLE 07 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 964 | 8 | [7 empty] | BITVAL
VVV7007DT3 | VC 3 SALLE 07 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 965 | 0 | [7 empty] | BITVAL
VVV7007DE3 | VC 3 SALLE 07 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 965 | 4 | [7 empty] | BITVAL
VVV7007DN3 | VC 3 SALLE 07 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 965 | 8 | [7 empty] | BITVAL
VVV7007DT4 | VC 4 SALLE 07 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 966 | 0 | [7 empty] | BITVAL
VVV7007DE4 | VC 4 SALLE 07 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 966 | 4 | [7 empty] | BITVAL
VVV7007DN4 | VC 4 SALLE 07 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 966 | 8 | [7 empty] | BITVAL
VVV7007DT5 | VC 5 SALLE 07 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 967 | 0 | [7 empty] | BITVAL
VVV7007DE5 | VC 5 SALLE 07 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 967 | 4 | [7 empty] | BITVAL
VVV7007DN5 | VC 5 SALLE 07 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 967 | 8 | [7 empty] | BITVAL
VVV7007DT6 | VC 6 SALLE 07 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 968 | 0 | [7 empty] | BITVAL
VVV7007DE6 | VC 6 SALLE 07 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 968 | 4 | [7 empty] | BITVAL
VVV7007DN6 | VC 6 SALLE 07 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 968 | 8 | [7 empty] | BITVAL
VVV7011DT1 | VC 1 SALLE 11 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 969 | 0 | [7 empty] | BITVAL
VVV7011DE1 | VC 1 SALLE 11 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 969 | 4 | [7 empty] | BITVAL
VVV7011DN1 | VC 1 SALLE 11 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 969 | 8 | [7 empty] | BITVAL
VVV7012DT1 | VC 1 SALLE 12 USER INTERFACE AND SONDE TEMPERATURE FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 970 | 0 | [7 empty] | BITVAL
VVV7012DE1 | VC 1 SALLE 12 WATER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 970 | 4 | [7 empty] | BITVAL
VVV7012DN1 | VC 1 SALLE 12 INVERTER FAULT | AL | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 970 | 8 | [7 empty] | BITVAL
VCD7014D1 | ACID BATTERY EVAC SALLE 14 LAGRANGE Fan Motor Circuit breaker FAULT | AL | O | FIL | 2 | E | [10 empty] | 0 |  | E | [13 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1012 | 10 | [7 empty] | BITVAL
VSY7020W1 | ALARME NIVEAU 1 CTA LAGRANGE SALLE 20 | AL | O | FIL | 2 | C |  | K | [8 empty] | 0 |  | C | [13 empty] | MTCP | 500 |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 1015 | 8 | [7 empty] | BITVAL
VSY7020W2 | ALARME NIVEAU 2 CTA LAGRANGE SALLE 20 | AL | O | FIL | 2 | C |  | K | [8 empty] | 0 |  | C | [13 empty] | MTCP | 500 |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 1015 | 10 | [7 empty] | BITVAL
EUL7071D1 | Lagrange UPS A DEFAUT GENERAL | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 0 | [7 empty] | BITVAL
EGB7071D1 | Lagrange UPS A MARCHE EN AUTONOMIE | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 2 | [7 empty] | BITVAL
EKM7071D1 | Lagrange UPS A Bypass switch status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 4 | [7 empty] | BITVAL
EVC7071D1 | Lagrange UPS A Battery alarm | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 6 | [7 empty] | BITVAL
EUL7071D2 | Lagrange UPS A Inverter major fault | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 8 | [7 empty] | BITVAL
EUL7071D3 | Lagrange UPS A Inverter overload status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 10 | [7 empty] | BITVAL
EUL7071D4 | Lagrange UPS A Inverter thermal overload status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 12 | [7 empty] | BITVAL
EUL7071D5 | Lagrange UPS A Inverter limitation status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1020 | 14 | [7 empty] | BITVAL
EUL7072D1 | Lagrange UPS B DEFAUT GENERAL | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 0 | [7 empty] | BITVAL
EGB7072D1 | Lagrange UPS B MARCHE EN AUTONOMIE | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 2 | [7 empty] | BITVAL
EKM7072D1 | Lagrange UPS B Bypass switch status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 4 | [7 empty] | BITVAL
EVC7072D1 | Lagrange UPS B Battery alarm | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 6 | [7 empty] | BITVAL
EUL7072D2 | Lagrange UPS B Inverter major fault | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 8 | [7 empty] | BITVAL
EUL7072D3 | Lagrange UPS B Inverter overload status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 10 | [7 empty] | BITVAL
EUL7072D4 | Lagrange UPS B Inverter thermal overload status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1022 | 12 | [7 empty] | BITVAL
EUL7072D5 | Lagrange UPS B Inverter limitation status | AL | N | RES | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1023 | 14 | [7 empty] | BITVAL
ESA7320N | TGBT 184-13-20 QF2001N MAIN SWITCH 1D21 SD FAULT | AL | O | FIL | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 500 |  | E74 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 2 | [7 empty] | BITVAL
ESA7320R | TGBT 184-13-20 QF2001R MAIN SWITCH REDUNDANT SD FAULT | AL | O | FIL | 2 | E |  | E | [10 empty] | E | [13 empty] | MTCP | 500 |  | E74 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 6 | [7 empty] | BITVAL
ESA7320C | **TGBT 184-13-20 CIRCUIT BREAKER CHAIN SD FAULT | AL | O | FIL | 2 | E |  | E | [8 empty] | 0 |  | E | [13 empty] | MTCP | 500 |  | E74 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 10 | [7 empty] | BITVAL
ESA7530 | TD 184-05-30 SD FAULT | AL | N | FIL | 2 | E |  | E | [8 empty] | 0 |  | E | [13 empty] | MTCP | 500 |  | E73 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1027 | 14 | [7 empty] | BITVAL
ESA7531 | TD 184-05-31 SD FAULT | AL | N | FIL | 2 | E |  | E | [8 empty] | 0 |  | E | [13 empty] | MTCP | 500 |  | E73 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1028 | 2 | [7 empty] | BITVAL
ESA7232 | **TD 184-13-32 SD FAULT | AL | N | FIL | 2 | E |  | E | [8 empty] | 0 |  | E | [13 empty] | MTCP | 500 |  | E73 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1028 | 6 | [7 empty] | BITVAL
SZI7000D | Defaut Lagrange Detection OFF/TEST | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 DI74 DI75 DI76 DI77 DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1031 | 0 | [7 empty] | BITVAL
SZI7000DE | Defaut Lagrange Emergency Power | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 DI74 DI75 DI76 DI77 DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1031 | 2 | [7 empty] | BITVAL
SCK7000DH | Defaut Lagrange Detection Hardware Fault | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 DI74 DI75 DI76 DI77 DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1031 | 6 | [7 empty] | BITVAL
SCK7000D | Defaut Lagrange Detection Fault | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 DI74 DI75 DI76 DI77 DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1031 | 8 | [7 empty] | BITVAL
SCK7001D | Defaut Lagrange Detection Alarm / Fault | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 DI74 DI75 DI76 DI77 DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1031 | 10 | [7 empty] | BITVAL
SZI7001W | Alarme Feu Lagrange Hall RDC 0000 ZAD01 - ZONE 1 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1032 | 2 | [7 empty] | BITVAL
SZI7002W | Alarme Feu Lagrange Aisle 0000 ZDA02 - ZONE 2 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1032 | 6 | [7 empty] | BITVAL
SZI7003W | Alarme Feu Lagrange Meeting room 0001 ZDA03 - ZONE 3 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1032 | 10 | [7 empty] | BITVAL
SZI7004W | Alarme Feu Lagrange Technical room 0005 ZDA04 Z1 - ZONE 4 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1032 | 14 | [7 empty] | BITVAL
WZC6001M | TOP (CCV) H0 - 120 S | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 98 | 7 | 12375 | 14 | 16416 | 173 | 6 | EL6021_M176 |  | BITVAL
WZC6000M | SEQUENCE OPTIQUE AUTOMATIQUE ACTIVEE | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 98 | 8 | 12376 | 0 | 16416 | 174 | 0 | EL6021_M176 |  | BITVAL
WEL6001M | CR MARCHE PROJECTEUR 1 SHELTER NORD | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 0 | 12377 | 0 | 16416 | 176 | 0 | EL6021_M176 |  | BITVAL
WEL6002M | CR MARCHE PROJECTEUR 2 SHELTER NORD | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 1 | 12377 | 2 | 16416 | 176 | 2 | EL6021_M176 |  | BITVAL
WEL6003M | MARCHE PROJECTEUR 3 SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 2 | 12377 | 4 | 16416 | 176 | 4 | EL6021_M176 |  | BITVAL
WEL6004M | MARCHE PROJECTEUR 4 SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 3 | 12377 | 6 | 16416 | 176 | 6 | EL6021_M176 |  | BITVAL
WBE6001U | SOUS TENSION SHELTER NORD VEGA | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 4 | 12377 | 8 | 16416 | 177 | 0 | EL6021_M176 |  | BITVAL
WBE6002U | SOUS TENSION SHELTER EST VEGA | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 5 | 12377 | 10 | 16416 | 177 | 2 | EL6021_M176 |  | BITVAL
WPO6001M | SYNTHESE MARCHE APV SHELTER NORD | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 6 | 12377 | 12 | 16416 | 177 | 4 | EL6021_M176 |  | BITVAL
WPO6003M | SYNTHESE MARCHE APV SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 7 | 12377 | 14 | 16416 | 177 | 6 | EL6021_M176 |  | BITVAL
WPO6002M | SYNTHESE MARCHE APV SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 8 | 12378 | 0 | 16416 | 178 | 0 | EL6021_M176 |  | BITVAL
WBE6003U | SOUS TENSION SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 10 | 12378 | 4 | 16416 | 178 | 4 | EL6021_M176 |  | BITVAL
WEL6005M | MARCHE PROJECTEUR 5 SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 11 | 12378 | 6 | 16416 | 178 | 6 | EL6021_M176 |  | BITVAL
WEL6006M | MARCHE PROJECTEUR 6 SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 99 | 12 | 12378 | 8 | 16416 | 179 | 0 | EL6021_M176 |  | BITVAL
WCO6001U | CAMERA CN1 ATT PRETE SHELTER NORD | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 0 | 12379 | 0 | 16416 | 180 | 0 | EL6021_M176 |  | BITVAL
WCO6002U | CAMERA CN2 ATT PRETE SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 2 | 12379 | 4 | 16416 | 180 | 4 | EL6021_M176 |  | BITVAL
WCO6003U | CAMERA CN3 POE PRETE SHELTER EST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 3 | 12379 | 6 | 16416 | 180 | 6 | EL6021_M176 |  | BITVAL
WCO6004U | CAMERA CN4 ATT PRETE SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 4 | 12379 | 8 | 16416 | 181 | 0 | EL6021_M176 |  | BITVAL
WCO6005U | CAMERA CN5 POE PRETE SHELTER OUEST | CR | N | RES | 1 | O | [26 empty] | NOT | 1000 |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 100 | 5 | 12379 | 10 | 16416 | 181 | 2 | EL6021_M176 |  | BITVAL
SPASCR1068 | SPARE SER CR 1068 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 305 | 10 | 12437 | 4 | 16416 | 296 | 4 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1068
SPASCR1069 | SPARE SER CR 1069 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 305 | 11 | 12437 | 6 | 16416 | 296 | 6 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1069
SPASCR1070 | SPARE SER CR 1070 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 305 | 12 | 12437 | 8 | 16416 | 297 | 0 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1070
SPASCR1071 | SPARE SER CR 1071 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 305 | 13 | 12437 | 10 | 16416 | 297 | 2 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1071
SPASCR1072 | SPARE SER CR 1072 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 2 | 12438 | 4 | 16416 | 298 | 4 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1072
SPASCR1073 | SPARE SER CR 1073 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 3 | 12438 | 6 | 16416 | 298 | 6 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1073
SPASCR1074 | SPARE SER CR 1074 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 4 | 12438 | 8 | 16416 | 299 | 0 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1074
SPASCR1075 | SPARE SER CR 1075 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 5 | 12438 | 10 | 16416 | 299 | 2 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1075
SPASCR1076 | SPARE SER CR 1076 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 10 | 12439 | 4 | 16416 | 300 | 4 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1076
SPASCR1077 | SPARE SER CR 1077 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 11 | 12439 | 6 | 16416 | 300 | 6 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1077
SPASCR1078 | SPARE SER CR 1078 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 12 | 12439 | 8 | 16416 | 301 | 0 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1078
SPASCR1079 | SPARE SER CR 1079 | CR | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 306 | 13 | 12439 | 10 | 16416 | 301 | 2 | EL6021_M176 |  | BITVAL |  | Eliminazione del segnale SDU6030D e aggiunta spare SPASCR1079
SPASCR0912 | SPARE SER 0912 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 1 |  |  | 400 | 13 | 12513 | 10 | 16416 | 449 | 2 | EL6021_M176 |  | BITVAL
SZI6001D | DEFAUT MASSIF ZLV LOCAL 001 PIED DE MAT | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63 | Detection Incendie (DI) | CCS | 1 |  |  | 408 | 0 | 12528 | 0 | 16416 | 478 | 0 | EL6021_M176 |  | BITVAL
SZI6002D | DEFAUT MASSIF ZLV LOCAL 002 A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63 | Detection Incendie (DI) | CCS | 1 |  |  | 408 | 1 | 12528 | 2 | 16416 | 478 | 2 | EL6021_M176 |  | BITVAL
SZI6003D | DEFAUT MASSIF ZLV LOCAL 003 GALERIE TECH | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63 | Detection Incendie (DI) | CCS | 1 |  |  | 408 | 2 | 12528 | 4 | 16416 | 478 | 4 | EL6021_M176 |  | BITVAL
SZI6004D | DEFAUT MASSIF ZLV LOCAL 006 TECHNIQUE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI72 | Detection Incendie (DI) | CCS | 1 |  |  | 408 | 3 | 12528 | 6 | 16416 | 478 | 6 | EL6021_M176 |  | BITVAL
SZI6005D | DEFAUT MASSIF ZLV LOCAL 012 MOY SECURITE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI72 | Detection Incendie (DI) | CCS | 1 |  |  | 408 | 4 | 12528 | 8 | 16416 | 479 | 0 | EL6021_M176 |  | BITVAL
SZI6006D | DEFAUT MASSIF ZLV LOCAL 004 COM A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 5 | 12528 | 10 | 16416 | 479 | 2 | EL6021_M176 |  | BITVAL
SZI6007D | DEFAUT MASSIF ZLV LOCAL 004 COM A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 6 | 12528 | 12 | 16416 | 479 | 4 | EL6021_M176 |  | BITVAL
SZI6008D | DEFAUT MASSIF ZLV LOCAL 007 CAT.III CU A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 7 | 12528 | 14 | 16416 | 479 | 6 | EL6021_M176 |  | BITVAL
SZI6009D | DEFAUT MASSIF ZLV LOCAL 007 CAT.III CU A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 8 | 12529 | 0 | 16416 | 480 | 0 | EL6021_M176 |  | BITVAL
SZI6010D | DEFAUT MASSIF ZLV LOCAL 008 BAT CUH A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 9 | 12529 | 2 | 16416 | 480 | 2 | EL6021_M176 |  | BITVAL
SZI6011D | DEFAUT MASSIF ZLV LOCAL 008 BAT CUH A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 10 | 12529 | 4 | 16416 | 480 | 4 | EL6021_M176 |  | BITVAL
SZI6012D | DEFAUT MASSIF ZLV LOCAL 009 BAT CUB A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 11 | 12529 | 6 | 16416 | 480 | 6 | EL6021_M176 |  | BITVAL
SZI6013D | DEFAUT MASSIF ZLV LOCAL 009 BAT CUB A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 12 | 12529 | 8 | 16416 | 481 | 0 | EL6021_M176 |  | BITVAL
SZI6014D | DEFAUT MASSIF ZLV LOCAL 013 VES A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 13 | 12529 | 10 | 16416 | 481 | 2 | EL6021_M176 |  | BITVAL
SZI6015D | DEFAUT MASSIF ZLV LOCAL 013 VES A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 14 | 12529 | 12 | 16416 | 481 | 4 | EL6021_M176 |  | BITVAL
SZI6016D | DEFAUT MASSIF ZLV LOCAL 013 VES FP1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 408 | 15 | 12529 | 14 | 16416 | 481 | 6 | EL6021_M176 |  | BITVAL
SZI6017D | DEFAUT MASSIF ZLV LOCAL 013 VES FP2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 409 | 0 | 12530 | 0 | 16416 | 482 | 0 | EL6021_M176 |  | BITVAL
SZI6022D | DEFAUT MASSIF ZLV LOCAL 100 CONNECTION | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 1 | 12530 | 2 | 16416 | 482 | 2 | EL6021_M176 |  | BITVAL
SZI6023D | DEFAUT MASSIF ZLV LOCAL 104 N2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 2 | 12530 | 4 | 16416 | 482 | 4 | EL6021_M176 |  | BITVAL
SZI6024D | DEFAUT MASSIF ZLV LOCAL 105 TECHNIQUE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 3 | 12530 | 6 | 16416 | 482 | 6 | EL6021_M176 |  | BITVAL
SZI6025D | DEFAUT MASSIF ZLV LOCAL 106 REPLI | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 4 | 12530 | 8 | 16416 | 483 | 0 | EL6021_M176 |  | BITVAL
SZI6026D | DEFAUT MASSIF ZLV LOCAL 107 N2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 5 | 12530 | 10 | 16416 | 483 | 2 | EL6021_M176 |  | BITVAL
SZI6027D | DEFAUT MASSIF ZLV LOCAL 108 FLUIDE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 6 | 12530 | 12 | 16416 | 483 | 4 | EL6021_M176 |  | BITVAL
SZI6028D | DEFAUT MASSIF ZLV LOCAL 117 DEGAGEMENT | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 7 | 12530 | 14 | 16416 | 483 | 6 | EL6021_M176 |  | BITVAL
SZI6029D | DEFAUT MASSIF ZLV LOCAL 118 CLIM | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 8 | 12531 | 0 | 16416 | 484 | 0 | EL6021_M176 |  | BITVAL
SZI6030D | DEFAUT MASSIF ZLV LOCAL 121 PLOMBERIE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 9 | 12531 | 2 | 16416 | 484 | 2 | EL6021_M176 |  | BITVAL
SZI6031D | DEFAUT MASSIF ZLV LOCAL 122 OUTILS MECA | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 10 | 12531 | 4 | 16416 | 484 | 4 | EL6021_M176 |  | BITVAL
SZI6032D | DEFAUT MASSIF ZLV LOCAL 127 LT CLIM | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62 | Detection Incendie (DI) | CCS | 1 |  |  | 409 | 11 | 12531 | 6 | 16416 | 484 | 6 | EL6021_M176 |  | BITVAL
SZI6038D | DEFAUT MASSIF ZLV LOCAL 101 BAIES CU A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 409 | 12 | 12531 | 8 | 16416 | 485 | 0 | EL6021_M176 |  | BITVAL
SZI6039D | DEFAUT MASSIF ZLV LOCAL 101 BAIES CU A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 409 | 13 | 12531 | 10 | 16416 | 485 | 2 | EL6021_M176 |  | BITVAL
SZI6040D | DEFAUT MASSIF ZLV LOCAL 101 BAIES CU FP1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 409 | 14 | 12531 | 12 | 16416 | 485 | 4 | EL6021_M176 |  | BITVAL
SZI6041D | DEFAUT MASSIF ZLV LOCAL 101 BAIES CU FP2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 409 | 15 | 12531 | 14 | 16416 | 485 | 6 | EL6021_M176 |  | BITVAL
SZI6042D | DEFAUT MASSIF ZLV LOCAL 103 BCV CCS A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 0 | 12532 | 0 | 16416 | 486 | 0 | EL6021_M176 |  | BITVAL
SZI6043D | DEFAUT MASSIF ZLV LOCAL 103 BCV CCS A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 1 | 12532 | 2 | 16416 | 486 | 2 | EL6021_M176 |  | BITVAL
SZI6044D | DEFAUT MASSIF ZLV LOCAL 103 BCV CCS FP1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 2 | 12532 | 4 | 16416 | 486 | 4 | EL6021_M176 |  | BITVAL
SZI6045D | DEFAUT MASSIF ZLV LOCAL 103 BCV CCS FP2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 3 | 12532 | 6 | 16416 | 486 | 6 | EL6021_M176 |  | BITVAL
SZI6046D | DEFAUT MASSIF ZLV LOCAL 111 CAT.III 2 A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 4 | 12532 | 8 | 16416 | 487 | 0 | EL6021_M176 |  | BITVAL
SZI6047D | DEFAUT MASSIF ZLV LOCAL 111 CAT.III 2 A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI66 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 5 | 12532 | 10 | 16416 | 487 | 2 | EL6021_M176 |  | BITVAL
SZI6048D | DEFAUT MASSIF ZLV LOCAL 112 CAT.III 1 A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 6 | 12532 | 12 | 16416 | 487 | 4 | EL6021_M176 |  | BITVAL
SZI6049D | DEFAUT MASSIF ZLV LOCAL 112 CAT.III 1 A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 7 | 12532 | 14 | 16416 | 487 | 6 | EL6021_M176 |  | BITVAL
SZI6050D | DEFAUT MASSIF ZLV LOCAL 113 CAT.III A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 8 | 12533 | 0 | 16416 | 488 | 0 | EL6021_M176 |  | BITVAL
SZI6051D | DEFAUT MASSIF ZLV LOCAL 113 CAT.III A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 9 | 12533 | 2 | 16416 | 488 | 2 | EL6021_M176 |  | BITVAL
SZI6052D | DEFAUT MASSIF ZLV LOCAL 115 TGBT A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 10 | 12533 | 4 | 16416 | 488 | 4 | EL6021_M176 |  | BITVAL
SZI6053D | DEFAUT MASSIF ZLV LOCAL 115 TGBT A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 11 | 12533 | 6 | 16416 | 488 | 6 | EL6021_M176 |  | BITVAL
SZI6054D | DEFAUT MASSIF ZLV LOCAL 116 HT A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 12 | 12533 | 8 | 16416 | 489 | 0 | EL6021_M176 |  | BITVAL
SZI6055D | DEFAUT MASSIF ZLV LOCAL 116 HT A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 13 | 12533 | 10 | 16416 | 489 | 2 | EL6021_M176 |  | BITVAL
SZI6056D | DEFAUT MASSIF ZLV LOCAL 126 SCC CLIM A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 14 | 12533 | 12 | 16416 | 489 | 4 | EL6021_M176 |  | BITVAL
SZI6057D | DEFAUT MASSIF ZLV LOCAL 126 SCC CLIM A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI62;EI67 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 410 | 15 | 12533 | 14 | 16416 | 489 | 6 | EL6021_M176 |  | BITVAL
SZI6058D | DEFAUT MAT ZLV NIV 18400 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 0 | 12534 | 0 | 16416 | 490 | 0 | EL6021_M176 |  | BITVAL
SZI6059D | DEFAUT MAT ZLV NIV 26600 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 1 | 12534 | 2 | 16416 | 490 | 2 | EL6021_M176 |  | BITVAL
SZI6060D | DEFAUT MAT ZLV NIV 34400 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 2 | 12534 | 4 | 16416 | 490 | 4 | EL6021_M176 |  | BITVAL
SZI6061D | DEFAUT MAT ZLV NIV 42200 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 3 | 12534 | 6 | 16416 | 490 | 6 | EL6021_M176 |  | BITVAL
SZI6064D | DEFAUT PORTIQUE ZLV NIV. 14200 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 4 | 12534 | 8 | 16416 | 491 | 0 | EL6021_M176 |  | BITVAL
SZI6065D | DEFAUT PORTIQUE ZLV NIV. 18400 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 5 | 12534 | 10 | 16416 | 491 | 2 | EL6021_M176 |  | BITVAL
SZI6066D | DEFAUT PORTIQUE ZLV LOCAL 101 A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 411 | 6 | 12534 | 12 | 16416 | 491 | 4 | EL6021_M176 |  | BITVAL
SZI6067D | DEFAUT PORTIQUE ZLV LOCAL 101 A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 411 | 7 | 12534 | 14 | 16416 | 491 | 6 | EL6021_M176 |  | BITVAL
SZI6068D | DEFAUT PORTIQUE ZLV LOCAL 102 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 8 | 12535 | 0 | 16416 | 492 | 0 | EL6021_M176 |  | BITVAL
SZI6069D | DEFAUT PORTIQUE ZLV NIV. 21200 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 9 | 12535 | 2 | 16416 | 492 | 2 | EL6021_M176 |  | BITVAL
SZI6070D | DEFAUT PORTIQUE ZLV LOCAL 201 A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 411 | 10 | 12535 | 4 | 16416 | 492 | 4 | EL6021_M176 |  | BITVAL
SZI6071D | DEFAUT PORTIQUE ZLV LOCAL 201 A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 411 | 11 | 12535 | 6 | 16416 | 492 | 6 | EL6021_M176 |  | BITVAL
SZI6072D | DEFAUT PORTIQUE ZLV LOCAL 202 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 12 | 12535 | 8 | 16416 | 493 | 0 | EL6021_M176 |  | BITVAL
SZI6073D | DEFAUT PORTIQUE ZLV NIV.24000 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 13 | 12535 | 10 | 16416 | 493 | 2 | EL6021_M176 |  | BITVAL
SZI6074D | DEFAUT PORTIQUE ZLV LOCAL 301 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 14 | 12535 | 12 | 16416 | 493 | 4 | EL6021_M176 |  | BITVAL
SZI6075D | DEFAUT PORTIQUE ZLV NIV. 26600 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 411 | 15 | 12535 | 14 | 16416 | 493 | 6 | EL6021_M176 |  | BITVAL
SZI6076D | DEFAUT PORTIQUE ZLV LOCAL 401 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 0 | 12536 | 0 | 16416 | 494 | 0 | EL6021_M176 |  | BITVAL
SZI6077D | DEFAUT PORTIQUE ZLV NIV. 29200 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 1 | 12536 | 2 | 16416 | 494 | 2 | EL6021_M176 |  | BITVAL
SZI6078D | DEFAUT PORTIQUE ZLV LOCAL 501 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 2 | 12536 | 4 | 16416 | 494 | 4 | EL6021_M176 |  | BITVAL
SZI6079D | DEFAUT PORTIQUE ZLV LOCAL 502 A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 412 | 3 | 12536 | 6 | 16416 | 494 | 6 | EL6021_M176 |  | BITVAL
SZI6080D | DEFAUT PORTIQUE ZLV LOCAL 502 A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI64;EI69 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 412 | 4 | 12536 | 8 | 16416 | 495 | 0 | EL6021_M176 |  | BITVAL
SZI6081D | DEFAUT PORTIQUE ZLV NIV. 31800 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 5 | 12536 | 10 | 16416 | 495 | 2 | EL6021_M176 |  | BITVAL
SZI6082D | DEFAUT PORTIQUE ZLV NIV. 34400 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 6 | 12536 | 12 | 16416 | 495 | 4 | EL6021_M176 |  | BITVAL
SZI6083D | DEFAUT PORTIQUE ZLV NIV. 37000 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 7 | 12536 | 14 | 16416 | 495 | 6 | EL6021_M176 |  | BITVAL
SZI6084D | DEFAUT PORTIQUE ZLV LOCAL 801 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 8 | 12537 | 0 | 16416 | 496 | 0 | EL6021_M176 |  | BITVAL
SZI6085D | DEFAUT PORTIQUE ZLV NIV. 39600 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 9 | 12537 | 2 | 16416 | 496 | 2 | EL6021_M176 |  | BITVAL
SZI6086D | DEFAUT PORTIQUE ZLV LOCAL 901 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 10 | 12537 | 4 | 16416 | 496 | 4 | EL6021_M176 |  | BITVAL
SZI6087D | DEFAUT PORTIQUE ZLV NIV. 42200 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 11 | 12537 | 6 | 16416 | 496 | 6 | EL6021_M176 |  | BITVAL
SZI6088D | DEFAUT PORTIQUE ZLV NIV. 44800 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 12 | 12537 | 8 | 16416 | 497 | 0 | EL6021_M176 |  | BITVAL
SZI6089D | DEFAUT PORTIQUE ZLV NIV. 47400 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 13 | 12537 | 10 | 16416 | 497 | 2 | EL6021_M176 |  | BITVAL
SZI6090D | DEFAUT PORTIQUE ZLV NIV. 50000 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 14 | 12537 | 12 | 16416 | 497 | 4 | EL6021_M176 |  | BITVAL
SZI6091D | DEFAUT PORTIQUE ZLV NIV. 53800 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 412 | 15 | 12537 | 14 | 16416 | 497 | 6 | EL6021_M176 |  | BITVAL
SZI6092D | DEFAUT PORTIQUE ZLV GAINE CLIM | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 0 | 12538 | 0 | 16416 | 498 | 0 | EL6021_M176 |  | BITVAL
SZI6098D | DEFAUT POSTE 1D60 ZLV | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 1 | 12538 | 2 | 16416 | 498 | 2 | EL6021_M176 |  | BITVAL
SZI6114D | Defaut Local 004 FX PL EST 1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 413 | 2 | 12538 | 4 | 16416 | 498 | 4 | EL6021_M176 |  | BITVAL
SZI6100D | DEFAUT SHELTER NORD ZLV | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 3 | 12538 | 6 | 16416 | 498 | 6 | EL6021_M176 |  | BITVAL
SZI6103D | DEFAUT SHELTER OUEST ZLV | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 4 | 12538 | 8 | 16416 | 499 | 0 | EL6021_M176 |  | BITVAL
SZI6102D | DEFAUT SHELTER EST ZLV | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 5 | 12538 | 10 | 16416 | 499 | 2 | EL6021_M176 |  | BITVAL
SZI6096D | DEFAUT PORTIQUE ZLV LOCAL 601 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 6 | 12538 | 12 | 16416 | 499 | 4 | EL6021_M176 |  | BITVAL
SZI6097D | DEFAUT PORTIQUE ZLV LOCAL 701 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 7 | 12538 | 14 | 16416 | 499 | 6 | EL6021_M176 |  | BITVAL
SZI6104D | DEFAUT DETECTEUR FLAMME CARBET N | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 8 | 12539 | 0 | 16416 | 500 | 0 | EL6021_M176 |  | BITVAL
SZI6105D | DEFAUT DETECTEUR FLAMME CARBET U | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI70 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 9 | 12539 | 2 | 16416 | 500 | 2 | EL6021_M176 |  | BITVAL
SZI6106D | DEFAUT DETECTEUR FLAMME 1 LOCAL 05 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI72 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 10 | 12539 | 4 | 16416 | 500 | 4 | EL6021_M176 |  | BITVAL
SZI6115D | Defaut Local 004 FX PL EST 2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 413 | 11 | 12539 | 6 | 16416 | 500 | 6 | EL6021_M176 |  | BITVAL
SZI6108D | DEFAUT DETECTEUR FLAMME LOCAL 102 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 12 | 12539 | 8 | 16416 | 501 | 0 | EL6021_M176 |  | BITVAL
SZI6109D | DEFAUT DETECTEUR FLAMME LOCAL 109 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI61 | Detection Incendie (DI) | CCS | 1 |  |  | 413 | 13 | 12539 | 10 | 16416 | 501 | 2 | EL6021_M176 |  | BITVAL
SZI6110D | DEFAUT MASSIF ZLV LOCAL 002 A2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;E71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 413 | 14 | 12539 | 12 | 16416 | 501 | 4 | EL6021_M176 |  | BITVAL
SZI6111D | DEFAUT MASSIF ZLV LOCAL 002 FF1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;E71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 413 | 15 | 12539 | 14 | 16416 | 501 | 6 | EL6021_M176 |  | BITVAL
SZI6112D | DEFAUT MASSIF ZLV LOCAL 002 FF2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;E71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 414 | 0 | 12540 | 0 | 16416 | 502 | 0 | EL6021_M176 |  | BITVAL
SZI6113D | DEFAUT LEVEL 47400 MAST A1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI65;EI71 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 414 | 1 | 12540 | 2 | 16416 | 502 | 2 | EL6021_M176 |  | BITVAL
SZI6116D | Defaut Local 004 FX PL OUEST 1 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 414 | 2 | 12540 | 4 | 16416 | 502 | 4 | EL6021_M176 |  | BITVAL
SZI6117D | Defaut Local 004 FX PL OUEST 2 | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 | SZR6002 | DI63;EI68 | Detection Incendie (DI);Extinction Incendie(EI) | CCS | 1 |  |  | 414 | 3 | 12540 | 6 | 16416 | 502 | 6 | EL6021_M176 |  | BITVAL
SPASCR0913 | SPARE SER 0913 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 1 | 12590 | 2 | 16416 | 602 | 2 | EL6021_M177 |  | BITVAL
SPASCR0914 | SPARE SER 0914 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 2 | 12590 | 4 | 16416 | 602 | 4 | EL6021_M177 |  | BITVAL
SPASCR0915 | SPARE SER 0915 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 3 | 12590 | 6 | 16416 | 602 | 6 | EL6021_M177 |  | BITVAL
SPASCR0916 | SPARE SER 0916 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 4 | 12590 | 8 | 16416 | 603 | 0 | EL6021_M177 |  | BITVAL
SPASCR0917 | SPARE SER 0917 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 5 | 12590 | 10 | 16416 | 603 | 2 | EL6021_M177 |  | BITVAL
SPASCR0918 | SPARE SER 0918 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 6 | 12590 | 12 | 16416 | 603 | 4 | EL6021_M177 |  | BITVAL
SPASCR0919 | SPARE SER 0919 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 7 | 12590 | 14 | 16416 | 603 | 6 | EL6021_M177 |  | BITVAL
SPASCR0920 | SPARE SER 0920 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 8 | 12591 | 0 | 16416 | 604 | 0 | EL6021_M177 |  | BITVAL
SPASCR0921 | SPARE SER 0921 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 9 | 12591 | 2 | 16416 | 604 | 2 | EL6021_M177 |  | BITVAL
SPASCR0922 | SPARE SER 0922 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 10 | 12591 | 4 | 16416 | 604 | 4 | EL6021_M177 |  | BITVAL
SPASCR0923 | SPARE SER 0923 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 11 | 12591 | 6 | 16416 | 604 | 6 | EL6021_M177 |  | BITVAL
SPASCR0924 | SPARE SER 0924 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 12 | 12591 | 8 | 16416 | 605 | 0 | EL6021_M177 |  | BITVAL
SPASCR0925 | SPARE SER 0925 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 13 | 12591 | 10 | 16416 | 605 | 2 | EL6021_M177 |  | BITVAL
SPASCR0926 | SPARE SER 0926 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 14 | 12591 | 12 | 16416 | 605 | 4 | EL6021_M177 |  | BITVAL
SPASCR0927 | SPARE SER 0927 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 90 | 15 | 12591 | 14 | 16416 | 605 | 6 | EL6021_M177 |  | BITVAL
SPASCR0939 | SPARE SER 0939 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 91 | 1 | 12592 | 2 | 16416 | 606 | 2 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6101D (CL8 Modification) | DEL
SPASCR0940 | SPARE SER 0940 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 91 | 3 | 12592 | 6 | 16416 | 606 | 6 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6103D (CL8 Modification) | DEL
SPASCR0943 | SPARE SER 0943 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 91 | 5 | 12592 | 10 | 16416 | 607 | 2 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6105D (CL8 Modification) | DEL
SPASCR0928 | SPARE SER 0928 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 9 | 12593 | 2 | 16416 | 608 | 2 | EL6021_M177 |  | BITVAL
SPASCR0929 | SPARE SER 0929 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 10 | 12593 | 4 | 16416 | 608 | 4 | EL6021_M177 |  | BITVAL
SPASCR0930 | SPARE SER 0930 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 11 | 12593 | 6 | 16416 | 608 | 6 | EL6021_M177 |  | BITVAL
SPASCR0931 | SPARE SER 0931 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 12 | 12593 | 8 | 16416 | 609 | 0 | EL6021_M177 |  | BITVAL
SPASCR0932 | SPARE SER 0932 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 13 | 12593 | 10 | 16416 | 609 | 2 | EL6021_M177 |  | BITVAL
SPASCR0933 | SPARE SER 0933 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 14 | 12593 | 12 | 16416 | 609 | 4 | EL6021_M177 |  | BITVAL
SPASCR0934 | SPARE SER 0934 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 91 | 15 | 12593 | 14 | 16416 | 609 | 6 | EL6021_M177 |  | BITVAL
SPASCR1066 | SPARE SER 1066 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 92 | 0 | 12594 | 0 | 16416 | 610 | 0 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6001W (CL8 Modification) | DEL
SPASCR1067 | SPARE SER 1067 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 92 | 1 | 12594 | 2 | 16416 | 610 | 2 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6002W (CL8 Modification) | DEL
SPASCR0935 | SPARE SER 0935 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 92 | 2 | 12594 | 4 | 16416 | 610 | 4 | EL6021_M177 |  | BITVAL
SPASCR0936 | SPARE SER 0936 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 92 | 3 | 12594 | 6 | 16416 | 610 | 6 | EL6021_M177 |  | BITVAL
SPASCR0937 | SPARE SER 0937 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 92 | 7 | 12594 | 14 | 16416 | 611 | 6 | EL6021_M177 |  | BITVAL
SPASCR0938 | SPARE SER 0938 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 92 | 10 | 12595 | 4 | 16416 | 612 | 4 | EL6021_M177 |  | BITVAL
SPASCR0941 | SPARE SER 0941 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 93 | 7 | 12596 | 14 | 16416 | 615 | 6 | EL6021_M177 |  | BITVAL
SPASCR0942 | SPARE SER 0942 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 93 | 10 | 12597 | 4 | 16416 | 616 | 4 | EL6021_M177 |  | BITVAL
SPASCR1044 | SPARE SER 0943 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 93 | 11 | 12597 | 6 | 16416 | 616 | 6 | EL6021_M177 |  | BITVAL
SPASCR0944 | SPARE SER 0944 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 94 | 4 | 12598 | 8 | 16416 | 619 | 0 | EL6021_M177 |  | BITVAL
SPASCR0945 | SPARE SER 0945 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 94 | 5 | 12598 | 10 | 16416 | 619 | 2 | EL6021_M177 |  | BITVAL
SPASCR0946 | SPARE SER 0946 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 94 | 14 | 12599 | 12 | 16416 | 621 | 4 | EL6021_M177 |  | BITVAL
SPASCR1045 | SPARE SER 0947 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 94 | 15 | 12599 | 14 | 16416 | 621 | 6 | EL6021_M177 |  | BITVAL
SPASCR0947 | SPARE SER 0947 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 95 | 2 | 12600 | 4 | 16416 | 622 | 4 | EL6021_M177 |  | BITVAL
SPASCR0948 | SPARE SER 0948 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 95 | 3 | 12600 | 6 | 16416 | 622 | 6 | EL6021_M177 |  | BITVAL
SPASCR0949 | SPARE SER 0949 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 95 | 4 | 12600 | 8 | 16416 | 623 | 0 | EL6021_M177 |  | BITVAL
SPASCR0950 | SPARE SER 0950 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 95 | 5 | 12600 | 10 | 16416 | 623 | 2 | EL6021_M177 |  | BITVAL
SPASCR0951 | SPARE SER 0951 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 6 | 12600 | 12 | 16416 | 623 | 4 | EL6021_M177 |  | BITVAL
SPASCR0952 | SPARE SER 0952 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 7 | 12600 | 14 | 16416 | 623 | 6 | EL6021_M177 |  | BITVAL
SPASCR0953 | SPARE SER 0953 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 8 | 12601 | 0 | 16416 | 624 | 0 | EL6021_M177 |  | BITVAL
SPASCR0954 | SPARE SER 0954 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 9 | 12601 | 2 | 16416 | 624 | 2 | EL6021_M177 |  | BITVAL
SPASCR0955 | SPARE SER 0955 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 10 | 12601 | 4 | 16416 | 624 | 4 | EL6021_M177 |  | BITVAL
SPASCR0956 | SPARE SER 0956 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 11 | 12601 | 6 | 16416 | 624 | 6 | EL6021_M177 |  | BITVAL
SPASCR0957 | SPARE SER 0957 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 12 | 12601 | 8 | 16416 | 625 | 0 | EL6021_M177 |  | BITVAL
SPASCR0958 | SPARE SER 0958 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 13 | 12601 | 10 | 16416 | 625 | 2 | EL6021_M177 |  | BITVAL
SPASCR0959 | SPARE SER 0959 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 14 | 12601 | 12 | 16416 | 625 | 4 | EL6021_M177 |  | BITVAL
SPASCR0960 | SPARE SER 0960 | CR | N | RES | [28 empty] | NOT | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 95 | 15 | 12601 | 14 | 16416 | 625 | 6 | EL6021_M177 |  | BITVAL
SPASCR0962 | SPARE SER 0962 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 96 | 15 | 12603 | 14 | 16416 | 629 | 6 | EL6021_M177 |  | BITVAL
SPASCR0963 | SPARE SER 0963 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 0 | 12604 | 0 | 16416 | 630 | 0 | EL6021_M177 |  | BITVAL
SPASCR0964 | SPARE SER 0964 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 1 | 12604 | 2 | 16416 | 630 | 2 | EL6021_M177 |  | BITVAL
SPASCR0965 | SPARE SER 0965 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 2 | 12604 | 4 | 16416 | 630 | 4 | EL6021_M177 |  | BITVAL
SPASCR0966 | SPARE SER 0966 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 3 | 12604 | 6 | 16416 | 630 | 6 | EL6021_M177 |  | BITVAL
SPASCR0967 | SPARE SER 0967 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 4 | 12604 | 8 | 16416 | 631 | 0 | EL6021_M177 |  | BITVAL
SPASCR0968 | SPARE SER 0968 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 5 | 12604 | 10 | 16416 | 631 | 2 | EL6021_M177 |  | BITVAL
SPASCR0969 | SPARE SER 0969 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 6 | 12604 | 12 | 16416 | 631 | 4 | EL6021_M177 |  | BITVAL
SPASCR0970 | SPARE SER 0970 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 7 | 12604 | 14 | 16416 | 631 | 6 | EL6021_M177 |  | BITVAL
SPASCR0971 | SPARE SER 0971 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 8 | 12605 | 0 | 16416 | 632 | 0 | EL6021_M177 |  | BITVAL
SPASCR0972 | SPARE SER 0972 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 9 | 12605 | 2 | 16416 | 632 | 2 | EL6021_M177 |  | BITVAL
SPASCR0973 | SPARE SER 0973 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 10 | 12605 | 4 | 16416 | 632 | 4 | EL6021_M177 |  | BITVAL
SPASCR0974 | SPARE SER 0974 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 11 | 12605 | 6 | 16416 | 632 | 6 | EL6021_M177 |  | BITVAL
SPASCR0975 | SPARE SER 0975 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 12 | 12605 | 8 | 16416 | 633 | 0 | EL6021_M177 |  | BITVAL
SPASCR0976 | SPARE SER 0976 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 13 | 12605 | 10 | 16416 | 633 | 2 | EL6021_M177 |  | BITVAL
SPASCR0977 | SPARE SER 0977 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 14 | 12605 | 12 | 16416 | 633 | 4 | EL6021_M177 |  | BITVAL
SPASCR0978 | SPARE SER 0978 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 97 | 15 | 12605 | 14 | 16416 | 633 | 6 | EL6021_M177 |  | BITVAL
SPASCR0979 | SPARE SER 0979 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 0 | 12606 | 0 | 16416 | 634 | 0 | EL6021_M177 |  | BITVAL
SPASCR0980 | SPARE SER 0980 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 1 | 12606 | 2 | 16416 | 634 | 2 | EL6021_M177 |  | BITVAL
SPASCR0981 | SPARE SER 0981 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 2 | 12606 | 4 | 16416 | 634 | 4 | EL6021_M177 |  | BITVAL
SPASCR0982 | SPARE SER 0982 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 3 | 12606 | 6 | 16416 | 634 | 6 | EL6021_M177 |  | BITVAL
SPASCR0983 | SPARE SER 0983 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 4 | 12606 | 8 | 16416 | 635 | 0 | EL6021_M177 |  | BITVAL
SPASCR0984 | SPARE SER 0984 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 5 | 12606 | 10 | 16416 | 635 | 2 | EL6021_M177 |  | BITVAL
SPASCR0985 | SPARE SER 0985 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 6 | 12606 | 12 | 16416 | 635 | 4 | EL6021_M177 |  | BITVAL
SPASCR0986 | SPARE SER 0986 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 7 | 12606 | 14 | 16416 | 635 | 6 | EL6021_M177 |  | BITVAL
SPASCR0987 | SPARE SER 0987 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 8 | 12607 | 0 | 16416 | 636 | 0 | EL6021_M177 |  | BITVAL
SPASCR0988 | SPARE SER 0988 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 9 | 12607 | 2 | 16416 | 636 | 2 | EL6021_M177 |  | BITVAL
SPASCR0989 | SPARE SER 0989 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 10 | 12607 | 4 | 16416 | 636 | 4 | EL6021_M177 |  | BITVAL
SPASCR0990 | SPARE SER 0990 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 11 | 12607 | 6 | 16416 | 636 | 6 | EL6021_M177 |  | BITVAL
SDC6002 | DEFAUT CAR PORTIQUE ZLV | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG68;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 98 | 12 | 12607 | 8 | 16416 | 637 | 0 | EL6021_M177 |  | BITVAL
SPASCR0991 | SPARE SER 0991 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 13 | 12607 | 10 | 16416 | 637 | 2 | EL6021_M177 |  | BITVAL
OSY6001 | SYNTHESE VANNE MANUELLE RESEAU EAU ZLV | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG61;MG62;MG63;MG64;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 98 | 14 | 12607 | 12 | 16416 | 637 | 4 | EL6021_M177 |  | BITVAL
SPASCR0992 | SPARE SER 0992 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 98 | 15 | 12607 | 14 | 16416 | 637 | 6 | EL6021_M177 |  | BITVAL
OVM6306F | VM OVM6306 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 0 | 12608 | 0 | 16416 | 638 | 0 | EL6021_M177 |  | BITVAL
OVM6310F | VM OVM6310 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 1 | 12608 | 2 | 16416 | 638 | 2 | EL6021_M177 |  | BITVAL
OVM6311F | VM OVM6311 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 2 | 12608 | 4 | 16416 | 638 | 4 | EL6021_M177 |  | BITVAL
OVM6314F | VANNE MANU RINCAGE PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 3 | 12608 | 6 | 16416 | 638 | 6 | EL6021_M177 |  | BITVAL
OVM6318F | VM OVM6318 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 4 | 12608 | 8 | 16416 | 639 | 0 | EL6021_M177 |  | BITVAL
OVM6307F | VM OVM6307 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 5 | 12608 | 10 | 16416 | 639 | 2 | EL6021_M177 |  | BITVAL
OVM6329F | VM OVM6329 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 6 | 12608 | 12 | 16416 | 639 | 4 | EL6021_M177 |  | BITVAL
OVM6341F | VM OVM6341 FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 7 | 12608 | 14 | 16416 | 639 | 6 | EL6021_M177 |  | BITVAL
OVM6306O | VM OVM6306 OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 8 | 12609 | 0 | 16416 | 640 | 0 | EL6021_M177 |  | BITVAL
OVM6310O | VM OVM6310 OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 9 | 12609 | 2 | 16416 | 640 | 2 | EL6021_M177 |  | BITVAL
OVM6311O | VM OVM6311 OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 10 | 12609 | 4 | 16416 | 640 | 4 | EL6021_M177 |  | BITVAL
OVM6314O | VANNE MANU RINCAGE PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 11 | 12609 | 6 | 16416 | 640 | 6 | EL6021_M177 |  | BITVAL
OVM6318O | VM OVM6318 OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG61;MG65;VG01;HVAC03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 99 | 12 | 12609 | 8 | 16416 | 641 | 0 | EL6021_M177 |  | BITVAL
SPASCR0993 | SPARE SER 0993 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 99 | 13 | 12609 | 10 | 16416 | 641 | 2 | EL6021_M177 |  | BITVAL
SPASCR0994 | SPARE SER 0994 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 99 | 14 | 12609 | 12 | 16416 | 641 | 4 | EL6021_M177 |  | BITVAL
SPASCR0995 | SPARE SER 0995 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 99 | 15 | 12609 | 14 | 16416 | 641 | 6 | EL6021_M177 |  | BITVAL
OVP6306F | VANNE RINCAGE FACADE O PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 0 | 12610 | 0 | 16416 | 642 | 0 | EL6021_M177 |  | BITVAL
OVP6307F | VANNE RINCAGE FACADE S PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 1 | 12610 | 2 | 16416 | 642 | 2 | EL6021_M177 |  | BITVAL
OVP6308F | VANNE RINCAGE FACADE E PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 2 | 12610 | 4 | 16416 | 642 | 4 | EL6021_M177 |  | BITVAL
OVP6309F | VANNE RINCAGE FACADE N PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62 | Moyens Generaux VEGA (MG) | CCS | 3 |  |  | 100 | 3 | 12610 | 6 | 16416 | 642 | 6 | EL6021_M177 |  | BITVAL
OVP6310F | VANNE RINCAGE TOITURE O PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 4 | 12610 | 8 | 16416 | 643 | 0 | EL6021_M177 |  | BITVAL
OVP6311F | VANNE RINCAGE TOITURE E PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 5 | 12610 | 10 | 16416 | 643 | 2 | EL6021_M177 |  | BITVAL
OVP6315F | VANNE RINCAGE PORTIQUE FERMEE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 6 | 12610 | 12 | 16416 | 643 | 4 | EL6021_M177 |  | BITVAL
SPASCR0996 | SPARE SER 0996 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 100 | 7 | 12610 | 14 | 16416 | 643 | 6 | EL6021_M177 |  | BITVAL
OVP6306O | VANNE RINCAGE FACADE O PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 8 | 12611 | 0 | 16416 | 644 | 0 | EL6021_M177 |  | BITVAL
OVP6307O | VANNE RINCAGE FACADE S PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 9 | 12611 | 2 | 16416 | 644 | 2 | EL6021_M177 |  | BITVAL
OVP6308O | VANNE RINCAGE FACADE E PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 10 | 12611 | 4 | 16416 | 644 | 4 | EL6021_M177 |  | BITVAL
OVP6309O | VANNE RINCAGE FACADE N PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 11 | 12611 | 6 | 16416 | 644 | 6 | EL6021_M177 |  | BITVAL
OVP6310O | VANNE RINCAGE TOITURE O PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 12 | 12611 | 8 | 16416 | 645 | 0 | EL6021_M177 |  | BITVAL
OVP6311O | VANNE RINCAGE TOITURE E PORTIQUE OUVERTE | CR | N | RES | 1 | F | [26 empty] | NOT | 1000 |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 100 | 13 | 12611 | 10 | 16416 | 645 | 2 | EL6021_M177 |  | BITVAL
SPASCR0997 | SPARE SER 0997 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 100 | 14 | 12611 | 12 | 16416 | 645 | 4 | EL6021_M177 |  | BITVAL
SPASCR0998 | SPARE SER 0998 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 100 | 15 | 12611 | 14 | 16416 | 645 | 6 | EL6021_M177 |  | BITVAL
SCX6021G | CENT.EI NIV 18.400 LOCAL 101 ENERGIE PRETE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 0 | 12612 | 0 | 16416 | 646 | 0 | EL6021_M177 |  | BITVAL
SCX6021U | CENT.EI NIV 18.400 LOCAL 101 ENERGIE PRES U | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 1 | 12612 | 2 | 16416 | 646 | 2 | EL6021_M177 |  | BITVAL
SCX6021D | CENT.EI NIV 18.400 LOC. 101 ENERGIE DEFAUT | CR | N | RES | 1 | S | [9 empty] | x==1 | [16 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 2 | 12612 | 4 | 16416 | 646 | 4 | EL6021_M177 |  | BITVAL
SPASCR0999 | SPARE SER 0999 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 101 | 3 | 12612 | 6 | 16416 | 646 | 6 | EL6021_M177 |  | BITVAL
SPB6021 | CR PRESSION BOUTEILLE N2 EI NIV 18.400 | CR | O | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 6 | 12612 | 12 | 16416 | 647 | 4 | EL6021_M177 |  | BITVAL
SPASCR1000 | SPARE SER 1000 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 101 | 7 | 12612 | 14 | 16416 | 647 | 6 | EL6021_M177 |  | BITVAL
SCX6022G | CENT.EI NIV 21.200 SAUVEGARDE CFS PRETE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 8 | 12613 | 0 | 16416 | 648 | 0 | EL6021_M177 |  | BITVAL
SCX6022U | CENT.EI NIV 21.200 SAUVEGARDE CFS PRES U | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 9 | 12613 | 2 | 16416 | 648 | 2 | EL6021_M177 |  | BITVAL
SCX6022D | CENT.EI NIV 21.200 SAUVEGARDE CFS DEFAUT | CR | N | RES | 1 | S | [9 empty] | x==1 | [16 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 10 | 12613 | 4 | 16416 | 648 | 4 | EL6021_M177 |  | BITVAL
SPASCR1001 | SPARE SER 1001 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 101 | 11 | 12613 | 6 | 16416 | 648 | 6 | EL6021_M177 |  | BITVAL
SPB6022 | CR PRESSION BOUTEILLE N2 NIV 21.200 | CR | O | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 101 | 14 | 12613 | 12 | 16416 | 649 | 4 | EL6021_M177 |  | BITVAL
SPASCR1002 | SPARE SER 1002 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 101 | 15 | 12613 | 14 | 16416 | 649 | 6 | EL6021_M177 |  | BITVAL
SCX6023G | CENT.EI NIV 29.200 BCV/INTF PRETE | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 102 | 0 | 12614 | 0 | 16416 | 650 | 0 | EL6021_M177 |  | BITVAL
SCX6023U | CENT.EI NIV 29.200 BCV/INTF PRES U | CR | N | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 102 | 1 | 12614 | 2 | 16416 | 650 | 2 | EL6021_M177 |  | BITVAL
SCX6023D | CENT.EI NIV 29.200 BCV/INTF DEFAUT | CR | N | RES | 1 | S | [9 empty] | x==1 | [16 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 102 | 2 | 12614 | 4 | 16416 | 650 | 4 | EL6021_M177 |  | BITVAL
SPASCR1003 | SPARE SER 1003 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 3 | 12614 | 6 | 16416 | 650 | 6 | EL6021_M177 |  | BITVAL
SPB6023 | CR PRESSION BOUTEILLE N2 EI NIV 29.200 | CR | O | RES | 1 | S | [26 empty] | NOT | 1000 |  | EI69 | Extinction Incendie (EI) | CCS | 3 |  |  | 102 | 6 | 12614 | 12 | 16416 | 651 | 4 | EL6021_M177 |  | BITVAL
SPASCR1004 | SPARE SER 1004 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 7 | 12614 | 14 | 16416 | 651 | 6 | EL6021_M177 |  | BITVAL
SPASCR1005 | SPARE SER 1005 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 8 | 12615 | 0 | 16416 | 652 | 0 | EL6021_M177 |  | BITVAL
SPASCR1006 | SPARE SER 1006 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 9 | 12615 | 2 | 16416 | 652 | 2 | EL6021_M177 |  | BITVAL
SPASCR1007 | SPARE SER 1007 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 10 | 12615 | 4 | 16416 | 652 | 4 | EL6021_M177 |  | BITVAL
SPASCR1008 | SPARE SER 1008 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 11 | 12615 | 6 | 16416 | 652 | 6 | EL6021_M177 |  | BITVAL
SPASCR1009 | SPARE SER 1009 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 12 | 12615 | 8 | 16416 | 653 | 0 | EL6021_M177 |  | BITVAL
SPASCR1010 | SPARE SER 1010 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 13 | 12615 | 10 | 16416 | 653 | 2 | EL6021_M177 |  | BITVAL
SPASCR1011 | SPARE SER 1011 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 14 | 12615 | 12 | 16416 | 653 | 4 | EL6021_M177 |  | BITVAL
SPASCR1012 | SPARE SER 1012 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 102 | 15 | 12615 | 14 | 16416 | 653 | 6 | EL6021_M177 |  | BITVAL
SPASCR1013 | SPARE SER 1013 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC(Z) |  | 3 |  |  | 103 | 2 | 12616 | 4 | 16416 | 654 | 4 | EL6021_M177 |  | BITVAL
SPASCR1014 | SPARE SER 1014 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC(Z) |  | 3 |  |  | 103 | 3 | 12616 | 6 | 16416 | 654 | 6 | EL6021_M177 |  | BITVAL
ESY6951D | **DEFAUT CONF. TD CAT III ZLV PORT CLIM 401 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 4 | 12616 | 8 | 16416 | 655 | 0 | EL6021_M177 |  | BITVAL
ESY6961D | **DEFAUT DEPART TD CAT III ZLV PORT CLIM 401 | CR | O | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 5 | 12616 | 10 | 16416 | 655 | 2 | EL6021_M177 |  | BITVAL
SPASCR1015 | SPARE SER 1015 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC(Z) |  | 3 |  |  | 103 | 6 | 12616 | 12 | 16416 | 655 | 4 | EL6021_M177 |  | BITVAL
SPASCR1016 | SPARE SER 1016 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC(Z) |  | 3 |  |  | 103 | 7 | 12616 | 14 | 16416 | 655 | 6 | EL6021_M177 |  | BITVAL
ESY6950D | **DEFAUT CONF. TD CAT III ZLV PORT 201/501/502 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 8 | 12617 | 0 | 16416 | 656 | 0 | EL6021_M177 |  | BITVAL
ESY6960D | **DEFAUT DEP. TD CAT III ZLV PORT 201/501/502 | CR | O | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 9 | 12617 | 2 | 16416 | 656 | 2 | EL6021_M177 |  | BITVAL
ESY6930D | **DEFAUT CONFIGURATION TDGA CAT.IIIA ZLV | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 10 | 12617 | 4 | 16416 | 656 | 4 | EL6021_M177 |  | BITVAL
ESY6940D | **DEFAUT DEPART TDGA CAT.IIIA ZLV | CR | O | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 11 | 12617 | 6 | 16416 | 656 | 6 | EL6021_M177 |  | BITVAL
ESY6931D | **DEFAUT CONFIGURATION TDGA CAT.IIIB ZLV | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 12 | 12617 | 8 | 16416 | 657 | 0 | EL6021_M177 |  | BITVAL
ESY6941D | **DEFAUT DEPART TDGA CAT.IIIB ZLV | CR | O | RES | 1 | E | [26 empty] | POL | 1000 |  | VG09 | Process Fluide et Energie General (VG) | CCS | 3 |  |  | 103 | 13 | 12617 | 10 | 16416 | 657 | 2 | EL6021_M177 |  | BITVAL
SPASCR1017 | SPARE SER 1017 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC(Z) |  | 3 |  |  | 103 | 14 | 12617 | 12 | 16416 | 657 | 4 | EL6021_M177 |  | BITVAL
SPASCR1018 | SPARE SER 1018 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC(Z) |  | 3 |  |  | 103 | 15 | 12617 | 14 | 16416 | 657 | 6 | EL6021_M177 |  | BITVAL
SPASCR0961 | SPARE SER 0961 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 104 | 0 | 12618 | 0 | 16416 | 658 | 0 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6101M (CL8 Modification) | DEL
SAV6102M | DETECTEUR CL8-1 EN MONITORING | CR | N | RES | 1 | S;F;D | [26 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 104 | 1 | 12618 | 2 | 16416 | 658 | 2 | EL6021_M177 |  | BITVAL |  |  | MOD
SPASCR1064 | SPARE SER 1064 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 104 | 2 | 12618 | 4 | 16416 | 658 | 4 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6103M (CL8 Modification) | DEL
SAV6104M | DETECTEUR CL8-2 EN MONITORING | CR | N | RES | 1 | S;F;D | [26 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 104 | 3 | 12618 | 6 | 16416 | 658 | 6 | EL6021_M177 |  | BITVAL |  |  | MOD
SPASCR1065 | SPARE SER 1065 | CR | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 104 | 4 | 12618 | 8 | 16416 | 659 | 0 | EL6021_M177 |  | BITVAL |  | Eliminazione del segnale SAV6105M (CL8 Modification) | DEL
SAV6106M | CL8-3 EN MONITORING | CR | N | RES | 1 | S;F;D | [26 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 104 | 5 | 12618 | 10 | 16416 | 659 | 2 | EL6021_M177 |  | BITVAL
SAV6108M | CL8-4 EN MONITORING | CR | N | RES | 1 | S;F;D | [26 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 104 | 7 | 12618 | 14 | 16416 | 659 | 6 | EL6021_M177 |  | BITVAL
SPASCR1019 | SPARE SER 1019 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 8 | 12619 | 0 | 16416 | 660 | 0 | EL6021_M177 |  | BITVAL
SPASCR1020 | SPARE SER 1020 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 9 | 12619 | 2 | 16416 | 660 | 2 | EL6021_M177 |  | BITVAL
SPASCR1021 | SPARE SER 1021 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 10 | 12619 | 4 | 16416 | 660 | 4 | EL6021_M177 |  | BITVAL
SPASCR1022 | SPARE SER 1022 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 11 | 12619 | 6 | 16416 | 660 | 6 | EL6021_M177 |  | BITVAL
SPASCR1023 | SPARE SER 1023 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 12 | 12619 | 8 | 16416 | 661 | 0 | EL6021_M177 |  | BITVAL
SPASCR1024 | SPARE SER 1024 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 13 | 12619 | 10 | 16416 | 661 | 2 | EL6021_M177 |  | BITVAL
SPASCR1025 | SPARE SER 1025 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 14 | 12619 | 12 | 16416 | 661 | 4 | EL6021_M177 |  | BITVAL
SPASCR1026 | SPARE SER 1026 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 104 | 15 | 12619 | 14 | 16416 | 661 | 6 | EL6021_M177 |  | BITVAL
SPASCR1027 | SPARE SER 1027 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 105 | 0 | 12620 | 0 | 16416 | 662 | 0 | EL6021_M177 |  | BITVAL
SPASCR1028 | SPARE SER 1028 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 105 | 1 | 12620 | 2 | 16416 | 662 | 2 | EL6021_M177 |  | BITVAL
SPASCR1029 | SPARE SER 1029 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 105 | 2 | 12620 | 4 | 16416 | 662 | 4 | EL6021_M177 |  | BITVAL
SPASCR1030 | SPARE SER 1030 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 105 | 3 | 12620 | 6 | 16416 | 662 | 6 | EL6021_M177 |  | BITVAL
SPASCR1031 | SPARE SER 1031 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 105 | 4 | 12620 | 8 | 16416 | 663 | 0 | EL6021_M177 |  | BITVAL
SPASCR1032 | SPARE SER 1032 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 105 | 5 | 12620 | 10 | 16416 | 663 | 2 | EL6021_M177 |  | BITVAL
EQF6132D | TD 1602-101-32 OF STATUS | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E67 | Energy TD (E) | ENE_MC | 3 |  |  | 105 | 6 | 12620 | 12 | 16416 | 663 | 4 | EL6021_M177 |  | BITVAL
EQF6133D | TD 1602-101-33 OF STATUS | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E67 | Energy TD (E) | ENE_MC | 3 |  |  | 105 | 7 | 12620 | 14 | 16416 | 663 | 6 | EL6021_M177 |  | BITVAL
SPASCR1033 | SPARE SER 1033 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 105 | 8 | 12621 | 0 | 16416 | 664 | 0 | EL6021_M177 |  | BITVAL
SPASCR1034 | SPARE SER 1034 | CR | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 3 |  |  | 105 | 11 | 12621 | 6 | 16416 | 664 | 6 | EL6021_M177 |  | BITVAL
SPASCR1035 | SPARE SER 1035 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 3 |  |  | 105 | 12 | 12621 | 8 | 16416 | 665 | 0 | EL6021_M177 |  | BITVAL
SPASCR1036 | SPARE SER 1036 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 3 |  |  | 105 | 13 | 12621 | 10 | 16416 | 665 | 2 | EL6021_M177 |  | BITVAL
SPASCR1037 | SPARE SER 1037 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 3 |  |  | 105 | 14 | 12621 | 12 | 16416 | 665 | 4 | EL6021_M177 |  | BITVAL
SPASCR1038 | SPARE SER 1038 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 3 |  |  | 105 | 15 | 12621 | 14 | 16416 | 665 | 6 | EL6021_M177 |  | BITVAL
SPASCR1049 | SPARE SER 1049 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 926 | 0 | 14536 | 0 | 16416 | 4494 | 0 | EL6021_M177 |  | BITVAL
SPASCR1050 | SPARE SER 1050 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 952 | 0 | 14562 | 0 | 16416 | 4546 | 0 | EL6021_M177 |  | BITVAL
SPASCR1051 | SPARE SER 1051 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 978 | 0 | 14588 | 0 | 16416 | 4598 | 0 | EL6021_M177 |  | BITVAL
SPASCR1052 | SPARE SER 1052 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1004 | 0 | 14614 | 0 | 16416 | 4650 | 0 | EL6021_M177 |  | BITVAL
SPASCR1053 | SPARE SER 1053 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1030 | 0 | 14640 | 0 | 16416 | 4702 | 0 | EL6021_M177 |  | BITVAL
SPASCR1054 | SPARE SER 1054 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1056 | 0 | 14666 | 0 | 16416 | 4754 | 0 | EL6021_M177 |  | BITVAL
SPASCR1055 | SPARE SER 1055 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1082 | 0 | 14692 | 0 | 16416 | 4806 | 0 | EL6021_M177 |  | BITVAL
SPASCR1056 | SPARE SER 1056 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1108 | 0 | 14718 | 0 | 16416 | 4858 | 0 | EL6021_M177 |  | BITVAL
SPASCR1057 | SPARE SER 1057 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1134 | 0 | 14744 | 0 | 16416 | 4910 | 0 | EL6021_M177 |  | BITVAL
SPASCR1058 | SPARE SER 1058 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1160 | 0 | 14770 | 0 | 16416 | 4962 | 0 | EL6021_M177 |  | BITVAL
SPASCR1059 | SPARE SER 1059 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1186 | 0 | 14796 | 0 | 16416 | 5014 | 0 | EL6021_M177 |  | BITVAL
SPASCR1060 | SPARE SER 1060 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1212 | 0 | 14822 | 0 | 16416 | 5066 | 0 | EL6021_M177 |  | BITVAL
SPASCR1061 | SPARE SER 1061 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1238 | 0 | 14848 | 0 | 16416 | 5118 | 0 | EL6021_M177 |  | BITVAL
SPASCR1062 | SPARE SER 1062 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1264 | 0 | 14874 | 0 | 16416 | 5170 | 0 | EL6021_M177 |  | BITVAL
SPASCR1063 | SPARE SER 1063 | CR | N | RES | 1 | [27 empty] | POL | 500 | [7 empty] | 1290 | 0 | 14900 | 0 | 16416 | 5222 | 0 | EL6021_M177 |  | BITVAL
SFE6101M | ACCES LIBRE TANGARA (VERT FIXE) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12862 | 14 | 16416 | 1147 | 6 | EL1134_M51 | 8 | BITVAL
SFE6102M | ACCES CONTROLE TANGARA (ORANGE FIXE) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12863 | 0 | 16416 | 1148 | 0 | EL1134_M52 | 1 | BITVAL
SFE6103M | ACCES LIMITE TANGARA (ROUGE FIXE) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12863 | 2 | 16416 | 1148 | 2 | EL1134_M52 | 5 | BITVAL
SFE6104M | ALERT EVAC TANGARA (ROUGE CLIGNOTANT) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12863 | 4 | 16416 | 1148 | 4 | EL1134_M52 | 4 | BITVAL
SFE6105M | ALERT REPLI TANGARA (ROUGE FIXE) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12863 | 6 | 16416 | 1148 | 6 | EL1134_M52 | 8 | BITVAL
SZI7005W | Alarme Feu Lagrange Technical room 0005 ZDA05 Z2 - ZONE 5 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1033 | 2 | [7 empty] | BITVAL
SZI7006W | Alarme Feu Lagrange COPV/PLANIF 0006 ZDA06 - ZONE 6 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1033 | 6 | [7 empty] | BITVAL
SZI7007W | Alarme Feu Lagrange Control room 0007 ZDA07 - ZONE 7 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1033 | 10 | [7 empty] | BITVAL
SZI7008W | Alarme Feu Lagrange DAS Room 0008 ZDA08 - ZONE 8 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1033 | 14 | [7 empty] | BITVAL
SZI7009W | Alarme Feu Lagrange Local Telecom 0009 ZDA09 - ZONE 9 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 2 | [7 empty] | BITVAL
SZI7010W | Alarme Feu Lagrange Launch range room 0010 ZDA10 Z1 - ZONE 10 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 6 | [7 empty] | BITVAL
SZI7011W | Alarme Feu Lagrange Launch range room 0010 ZDA10 Z2 - ZONE 11 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 10 | [7 empty] | BITVAL
SZI7012W | Alarme Feu Lagrange Office 0011 ZDA11 - ZONE 12 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 14 | [7 empty] | BITVAL
SZI7013W | Alarme Feu Lagrange Crisis room 0012 ZDA12 - ZONE 13 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1035 | 2 | [7 empty] | BITVAL
SZI7014W | Alarme Feu Lagrange UPS room 0013 ZDA13 Z1 - ZONE 14 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1035 | 6 | [7 empty] | BITVAL
SFE6010M | FEUX ROUGE PORTIQUE NIV 18.400 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 0 | 16416 | 1102 | 0 | EL1134_M2 | 1 | BITVAL
SFE6011M | FEUX ORANGE PORTIQUE NIV 18.400 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 2 | 16416 | 1102 | 2 | EL1134_M2 | 5 | BITVAL
SFE6010D | DEFAUT FEU BICOLORE PORTIQUE NIV 18.400 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 4 | 16416 | 1102 | 4 | EL1134_M2 | 4 | BITVAL
SFE6020M | FEUX ROUGE PORTIQUE NIV 21.200 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 6 | 16416 | 1102 | 6 | EL1134_M2 | 8 | BITVAL
SFE6021M | FEUX ORANGE PORTIQUE NIV 21.200 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 8 | 16416 | 1103 | 0 | EL1134_M3 | 1 | BITVAL
SFE6020D | DEFAUT FEU BICOLORE PORTIQUE NIV 21.200 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 10 | 16416 | 1103 | 2 | EL1134_M3 | 5 | BITVAL
SFE6030M | FEUX ROUGE PORTIQUE NIV 24.000 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 12 | 16416 | 1103 | 4 | EL1134_M3 | 4 | BITVAL
SFE6031M | FEUX ORANGE PORTIQUE NIV 24.000 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12840 | 14 | 16416 | 1103 | 6 | EL1134_M3 | 8 | BITVAL
SFE6030D | DEFAUT FEU BICOLORE PORTIQUE NIV 24.000 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 0 | 16416 | 1104 | 0 | EL1134_M4 | 1 | BITVAL
SFE6040M | FEUX ROUGE PORTIQUE PF ELEV 1 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 2 | 16416 | 1104 | 2 | EL1134_M4 | 5 | BITVAL
SFE6041M | FEUX ORANGE PORTIQUE PF ELEV 1 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 4 | 16416 | 1104 | 4 | EL1134_M4 | 4 | BITVAL
SFE6040D | DEFAUT FEU BICOLORE PORTIQUE PF ELEV 1 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 6 | 16416 | 1104 | 6 | EL1134_M4 | 8 | BITVAL
SFE6050M | FEUX ROUGE PORTIQUE PF ELEV 2 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 8 | 16416 | 1105 | 0 | EL1134_M5 | 1 | BITVAL
SFE6051M | FEUX ORANGE PORTIQUE PF ELEV 2 MARCHE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 10 | 16416 | 1105 | 2 | EL1134_M5 | 5 | BITVAL
SFE6050D | DEFAUT FEU BICOLORE PORTIQUE PF ELEV 2 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12841 | 12 | 16416 | 1105 | 4 | EL1134_M5 | 4 | BITVAL
SPAFCR0001 | SPARE FIL 0001 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12842 | 0 | 16416 | 1106 | 0 | EL1134_M6 | 1 | BITVAL
SPAFCR0002 | SPARE FIL 0002 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12842 | 2 | 16416 | 1106 | 2 | EL1134_M6 | 5 | BITVAL
SPAFCR0003 | SPARE FIL 0003 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12842 | 4 | 16416 | 1106 | 4 | EL1134_M6 | 4 | BITVAL
SFE6003M | PRESENCE LANCEUR ZLV (ORANGE FIXE) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12842 | 8 | 16416 | 1107 | 0 | EL1134_M7 | 1 | BITVAL
SFE6004M | ACCES LIBRE ZLV (VERT FIXE) | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12842 | 10 | 16416 | 1107 | 2 | EL1134_M7 | 5 | BITVAL
SFE6001D | DEFAUT FEU TRICOLORE ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12842 | 12 | 16416 | 1107 | 4 | EL1134_M7 | 4 | BITVAL
SST6001O | CR OUVERTURE BARRIERE ENTREE DE LA ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12843 | 2 | 16416 | 1108 | 2 | EL1134_M8 | 5 | BITVAL
SST6001D | CR DEFAUT BARRIERE ENTREE ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12843 | 6 | 16416 | 1108 | 6 | EL1134_M8 | 8 | BITVAL
SPAFCR0004 | SPARE FIL 0004 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12844 | 6 | 16416 | 1110 | 6 | EL1134_M10 | 8 | BITVAL
SPAFCR0005 | SPARE FIL 0005 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12844 | 8 | 16416 | 1111 | 0 | EL1134_M11 | 1 | BITVAL
SPAFCR0006 | SPARE FIL 0006 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12844 | 10 | 16416 | 1111 | 2 | EL1134_M11 | 5 | BITVAL
SPAFCR0007 | SPARE FIL 0007 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12844 | 12 | 16416 | 1111 | 4 | EL1134_M11 | 4 | BITVAL
SPAFCR0008 | SPARE FIL 0008 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12844 | 14 | 16416 | 1111 | 6 | EL1134_M11 | 8 | BITVAL
SDC6001 | **DEFAUT CAR MASSIF ZLV | CR | O | FIL | 1 | F | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG68;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12845 | 6 | 16416 | 1112 | 6 | EL1134_M13 | 8 | BITVAL
SCX6002G | CENT.EI LOCAL 004 COMMUNICATION PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12845 | 8 | 16416 | 1113 | 0 | EL1134_M14 | 1 | BITVAL
SCX6002U | CENT.EI LOCAL 004 COMMUNICATION PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12845 | 10 | 16416 | 1113 | 2 | EL1134_M14 | 5 | BITVAL
SCX6002D | **CENT.EI LOCAL 004 COMM. DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12845 | 12 | 16416 | 1113 | 4 | EL1134_M14 | 4 | BITVAL
SPB6002 | CR PRESSION BOUTEILLE N2 EI LOCAL 004 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 2 | 16416 | 1114 | 2 | EL1134_M15 | 5 | BITVAL
SCX6003G | CENT.EI LOCAL 007 CAT.III CU PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 6 | 16416 | 1114 | 6 | EL1134_M15 | 8 | BITVAL
SCX6003U | CENT.EI LOCAL 007 CAT.III CU PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 8 | 16416 | 1115 | 0 | EL1134_M16 | 1 | BITVAL
SCX6003D | **CENT.EI LOC. 007 CAT.III CU DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12846 | 10 | 16416 | 1115 | 2 | EL1134_M16 | 5 | BITVAL
SPAFCR0009 | SPARE FIL 0009 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12847 | 0 | 16416 | 1116 | 0 | EL1134_M17 | 1 | BITVAL
SPAFCR0010 | SPARE FIL 0010 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12847 | 2 | 16416 | 1116 | 2 | EL1134_M17 | 5 | BITVAL
SPAFCR0011 | SPARE FIL 0011 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12847 | 4 | 16416 | 1116 | 4 | EL1134_M17 | 4 | BITVAL
SPB6003 | CR PRESSION BOUTEILLE N2 EI LOCAL 007 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12847 | 6 | 16416 | 1116 | 6 | EL1134_M17 | 8 | BITVAL
SCX6004G | CENT.EI LOCAL 008 BATTERIES CUH PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12847 | 10 | 16416 | 1117 | 2 | EL1134_M18 | 5 | BITVAL
SCX6004U | CENT.EI LOCAL 008 BATTERIES CUH PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12847 | 12 | 16416 | 1117 | 4 | EL1134_M18 | 4 | BITVAL
SCX6004D | **CENT.EI LOCAL 008 BATT. CUH DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12847 | 14 | 16416 | 1117 | 6 | EL1134_M18 | 8 | BITVAL
SPB6004 | CR PRESSION BOUTEILLE N2 EI LOCAL 008 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 4 | 16416 | 1118 | 4 | EL1134_M19 | 4 | BITVAL
SCX6005G | CENT.EI LOCAL 009 BATTERIES CUB PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 8 | 16416 | 1119 | 0 | EL1134_M20 | 1 | BITVAL
SCX6005U | CENT.EI LOCAL 009 BATTERIES CUB PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 10 | 16416 | 1119 | 2 | EL1134_M20 | 5 | BITVAL
SCX6005D | **CENT.EI LOCAL 009 BATT. CUB DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12848 | 12 | 16416 | 1119 | 4 | EL1134_M20 | 4 | BITVAL
SPB6005 | CR PRESSION BOUTEILLE N2 EI LOCAL 009 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12849 | 2 | 16416 | 1120 | 2 | EL1134_M21 | 5 | BITVAL
SPAFCR0012 | SPARE FIL 0012 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12849 | 6 | 16416 | 1120 | 6 | EL1134_M21 | 8 | BITVAL
SPAFCR0013 | SPARE FIL 0013 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12849 | 8 | 16416 | 1121 | 0 | EL1134_M22 | 1 | BITVAL
SPAFCR0014 | SPARE FIL 0014 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12849 | 10 | 16416 | 1121 | 2 | EL1134_M22 | 5 | BITVAL
SPAFCR0015 | SPARE FIL 0015 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12849 | 12 | 16416 | 1121 | 4 | EL1134_M22 | 4 | BITVAL
SPAFCR0016 | SPARE FIL 0016 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12849 | 14 | 16416 | 1121 | 6 | EL1134_M22 | 8 | BITVAL
SCX6001G | CENTRALE EI LOCAL 013 ET 002 PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 0 | 16416 | 1122 | 0 | EL1134_M24 | 1 | BITVAL
SCX6001U | CENTRALE EI LOCAL 013 ET 002 PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 2 | 16416 | 1122 | 2 | EL1134_M24 | 5 | BITVAL
SCX6001D | **CENTRALE EI LOCAL 013 ET 002 DEFAUT GEN. | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 4 | 16416 | 1122 | 4 | EL1134_M24 | 4 | BITVAL
SPB6001 | CR PRESSION BOUTEILLE N2 EI LOCAL 013 ET 002 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 10 | 16416 | 1123 | 2 | EL1134_M25 | 5 | BITVAL
SCX6006G | CENT.EI LOCAL 101 BAIES CU PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12850 | 14 | 16416 | 1123 | 6 | EL1134_M25 | 8 | BITVAL
SCX6006U | CENT.EI LOCAL 101 BAIES CU PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12851 | 0 | 16416 | 1124 | 0 | EL1134_M26 | 1 | BITVAL
SCX6006D | **CENT.EI LOCAL 101 BAIES CU DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12851 | 2 | 16416 | 1124 | 2 | EL1134_M26 | 5 | BITVAL
EEL6001M | CR MARCHE ECLAIRAGE LANCEUR CONF.A | CR | O | FIL | 1 | E | [26 empty] | NOT | 1000 |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12851 | 6 | 16416 | 1124 | 6 | EL1134_M26 | 8 | BITVAL
SPAFCR0017 | SPARE FIL 0017 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12851 | 8 | 16416 | 1125 | 0 | EL1134_M27 | 1 | BITVAL
SPAFCR0018 | SPARE FIL 0018 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12851 | 10 | 16416 | 1125 | 2 | EL1134_M27 | 5 | BITVAL
SPAFCR0019 | SPARE FIL 0019 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12851 | 12 | 16416 | 1125 | 4 | EL1134_M27 | 4 | BITVAL
SPAFCR0020 | SPARE FIL 0020 | CR | N | FIL | [28 empty] | POL |  |  | VMC06 | VMC (Z) | [6 empty] | 12851 | 14 | 16416 | 1125 | 6 | EL1134_M27 | 8 | BITVAL
SPAFCR0021 | SPARE FIL 0021 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12852 | 0 | 16416 | 1126 | 0 | EL1134_M28 | 1 | BITVAL
SPAFCR0022 | SPARE FIL 0022 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12852 | 2 | 16416 | 1126 | 2 | EL1134_M28 | 5 | BITVAL
SPAFCR0023 | SPARE FIL 0023 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12852 | 4 | 16416 | 1126 | 4 | EL1134_M28 | 4 | BITVAL
EEL6002M | CR MARCHE ECLAIRAGE LANCEUR CONF.B | CR | O | FIL | 1 | E | [26 empty] | NOT | 1000 |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12852 | 12 | 16416 | 1127 | 4 | EL1134_M29 | 4 | BITVAL
EEL6003M | CR MARCHE ECLAIRAGE LANCEUR CONF.C | CR | O | FIL | 1 | E | [26 empty] | NOT | 1000 |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12852 | 14 | 16416 | 1127 | 6 | EL1134_M29 | 8 | BITVAL
EEL6004M | CR MARCHE ECLAIRAGE LANCEUR CONF.D | CR | O | FIL | 1 | E | [26 empty] | NOT | 1000 |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12853 | 0 | 16416 | 1128 | 0 | EL1134_M30 | 1 | BITVAL
SPAFCR0024 | SPARE FIL 0024 | CR | N | FIL | [28 empty] | NOT |  |  | VMC06 | VMC (Z) | [6 empty] | 12853 | 2 | 16416 | 1128 | 2 | EL1134_M30 | 5 | BITVAL
SPAFCR0025 | SPARE FIL 0025 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12853 | 4 | 16416 | 1128 | 4 | EL1134_M30 | 4 | BITVAL
SPAFCR0026 | SPARE FIL 0026 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12853 | 6 | 16416 | 1128 | 6 | EL1134_M30 | 8 | BITVAL
SPAFCR0027 | SPARE FIL 0027 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12853 | 8 | 16416 | 1129 | 0 | EL1134_M31 | 1 | BITVAL
SPAFCR0028 | SPARE FIL 0028 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12853 | 10 | 16416 | 1129 | 2 | EL1134_M31 | 5 | BITVAL
NVM6301F | VM NVM6301 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12854 | 4 | 16416 | 1130 | 4 | EL1134_M32 | 4 | BITVAL
SPAFCR0029 | SPARE FIL 0029 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12854 | 6 | 16416 | 1130 | 6 | EL1134_M32 | 8 | BITVAL
SPAFCR0030 | SPARE FIL 0030 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12854 | 8 | 16416 | 1131 | 0 | EL1134_M33 | 1 | BITVAL
SPAFCR0031 | SPARE FIL 0031 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12854 | 10 | 16416 | 1131 | 2 | EL1134_M33 | 5 | BITVAL
SPAFCR0032 | SPARE FIL 0032 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12854 | 12 | 16416 | 1131 | 4 | EL1134_M33 | 4 | BITVAL
SPAFCR0033 | SPARE FIL 0033 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12854 | 14 | 16416 | 1131 | 6 | EL1134_M33 | 8 | BITVAL
NVM6301O | VM NVM6301 (TRAITEMET N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 0 | 16416 | 1132 | 0 | EL1134_M35 | 1 | BITVAL
NVM6302F | VM NVM6302 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 2 | 16416 | 1132 | 2 | EL1134_M35 | 5 | BITVAL
NVM6302O | VM NVM6302 (TRAITEMET N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 4 | 16416 | 1132 | 4 | EL1134_M35 | 4 | BITVAL
UPP6301M | CR MARCHE POMPE UPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 6 | 16416 | 1132 | 6 | EL1134_M35 | 8 | BITVAL
UPP6301A | CR ARRET POMPE UPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 8 | 16416 | 1133 | 0 | EL1134_M36 | 1 | BITVAL
NPP6301M | CR MARCHE POMPE NPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 12 | 16416 | 1133 | 4 | EL1134_M36 | 4 | BITVAL
NPP6301A | CR ARRET POMPE NPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12855 | 14 | 16416 | 1133 | 6 | EL1134_M36 | 8 | BITVAL
NPP6301D | DEFAUT POMPE NPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12856 | 0 | 16416 | 1134 | 0 | EL1134_M37 | 1 | BITVAL
NVM6303F | VM NVM6303 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12856 | 10 | 16416 | 1135 | 2 | EL1134_M38 | 5 | BITVAL
NVM6303O | VM NVM6303 (TRAITEMET N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12856 | 12 | 16416 | 1135 | 4 | EL1134_M38 | 4 | BITVAL
NVM6304F | VM NVM6304 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12856 | 14 | 16416 | 1135 | 6 | EL1134_M38 | 8 | BITVAL
SPAFCR0034 | SPARE FIL 0034 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12857 | 0 | 16416 | 1136 | 0 | EL1134_M39 | 1 | BITVAL
SPAFCR0035 | SPARE FIL 0035 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12857 | 2 | 16416 | 1136 | 2 | EL1134_M39 | 5 | BITVAL
SPAFCR0036 | SPARE FIL 0036 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12857 | 4 | 16416 | 1136 | 4 | EL1134_M39 | 4 | BITVAL
SPAFCR0037 | SPARE FIL 0037 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12857 | 8 | 16416 | 1137 | 0 | EL1134_M40 | 1 | BITVAL
SPAFCR0038 | SPARE FIL 0038 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12857 | 10 | 16416 | 1137 | 2 | EL1134_M40 | 5 | BITVAL
SPAFCR0039 | SPARE FIL 0039 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12857 | 12 | 16416 | 1137 | 4 | EL1134_M40 | 4 | BITVAL
SPAFCR0040 | SPARE FIL 0040 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12857 | 14 | 16416 | 1137 | 6 | EL1134_M40 | 8 | BITVAL
SPAFCR0041 | SPARE FIL 0041 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12858 | 0 | 16416 | 1138 | 0 | EL1134_M41 | 1 | BITVAL
SPAFCR0042 | SPARE FIL 0042 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12858 | 2 | 16416 | 1138 | 2 | EL1134_M41 | 5 | BITVAL
SPAFCR0043 | SPARE FIL 0043 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12858 | 4 | 16416 | 1138 | 4 | EL1134_M41 | 4 | BITVAL
SPAFCR0044 | SPARE FIL 0044 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12858 | 6 | 16416 | 1138 | 6 | EL1134_M41 | 8 | BITVAL
SPAFCR0045 | SPARE FIL 0045 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12858 | 12 | 16416 | 1139 | 4 | EL1134_M42 | 4 | BITVAL
SPAFCR0046 | SPARE FIL 0046 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12858 | 14 | 16416 | 1139 | 6 | EL1134_M42 | 8 | BITVAL
SPAFCR0047 | SPARE FIL 0047 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12859 | 6 | 16416 | 1140 | 6 | EL1134_M43 | 8 | BITVAL
SPAFCR0048 | SPARE FIL 0048 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12859 | 8 | 16416 | 1141 | 0 | EL1134_M44 | 1 | BITVAL
SPAFCR0049 | SPARE FIL 0049 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12859 | 10 | 16416 | 1141 | 2 | EL1134_M44 | 5 | BITVAL
SPAFCR0050 | SPARE FIL 0050 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12859 | 12 | 16416 | 1141 | 4 | EL1134_M44 | 4 | BITVAL
SPAFCR0051 | SPARE FIL 0051 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12859 | 14 | 16416 | 1141 | 6 | EL1134_M44 | 8 | BITVAL
SPAFCR0052 | SPARE FIL 0052 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12860 | 2 | 16416 | 1142 | 2 | EL1134_M46 | 5 | BITVAL
SPAFCR0053 | SPARE FIL 0053 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12860 | 4 | 16416 | 1142 | 4 | EL1134_M46 | 4 | BITVAL
SCE6001S | MARCHE AE ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12860 | 10 | 16416 | 1143 | 2 | EL1134_M47 | 5 | BITVAL
SCE6001A | ARRET AE ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12860 | 12 | 16416 | 1143 | 4 | EL1134_M47 | 4 | BITVAL
SPAFCR0054 | SPARE FIL 0054 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12861 | 0 | 16416 | 1144 | 0 | EL1134_M48 | 1 | BITVAL
SSP6001QC | POSITION MARCHE ALERTE REPLI SIRENE ZLV | CR | O | FIL | 1 | S | [24 empty] | SSP6001QA |  | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12861 | 2 | 16416 | 1144 | 2 | EL1134_M48 | 5 | BITVAL
SSP6001QM | POSITION MARCHE ALERTE EVACUATION SIRENE ZLV | CR | O | FIL | 1 | S | [24 empty] | SSP6001QA |  | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12861 | 4 | 16416 | 1144 | 4 | EL1134_M48 | 4 | BITVAL
SZI7015W | Alarme Feu Lagrange UPS room 0013 ZDA13 Z2 - ZONE 15 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1035 | 10 | [7 empty] | BITVAL
SZI7016W | Alarme Feu Lagrange Battery room 0014 ZDA14 Z1 - ZONE 16 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1035 | 14 | [7 empty] | BITVAL
SPAFCR0055 | SPARE FIL 0055 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12861 | 8 | 16416 | 1145 | 0 | EL1134_M49 | 1 | BITVAL
SPAFCR0056 | SPARE FIL 0056 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12861 | 10 | 16416 | 1145 | 2 | EL1134_M49 | 5 | BITVAL
SCE6002S | MARCHE AR ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12861 | 12 | 16416 | 1145 | 4 | EL1134_M49 | 4 | BITVAL
SCE6002A | ARRET AR ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12861 | 14 | 16416 | 1145 | 6 | EL1134_M49 | 8 | BITVAL
SPAFCR0057 | SPARE FIL 0057 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12862 | 0 | 16416 | 1146 | 0 | EL1134_M50 | 1 | BITVAL
SPAFCR0058 | SPARE FIL 0058 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12862 | 2 | 16416 | 1146 | 2 | EL1134_M50 | 5 | BITVAL
SPAFCR0059 | SPARE FIL 0059 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12862 | 4 | 16416 | 1146 | 4 | EL1134_M50 | 4 | BITVAL
SST6002O | CR OUVERTURE BARRIERE SORTIE DE LA ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12862 | 8 | 16416 | 1147 | 0 | EL1134_M51 | 1 | BITVAL
SPAFCR0060 | SPARE FIL 0060 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12862 | 10 | 16416 | 1147 | 2 | EL1134_M51 | 5 | BITVAL
SST6002D | CR DEFAUT BARRIERE SORTIE ZLV | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12862 | 12 | 16416 | 1147 | 4 | EL1134_M51 | 4 | BITVAL
SPAFCR0068 | SPARE FIL 0068 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12863 | 12 | 16416 | 1149 | 4 | EL1134_M53 | 4 | BITVAL
SPAFCR0069 | SPARE FIL 0069 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12863 | 14 | 16416 | 1149 | 6 | EL1134_M53 | 8 | BITVAL
SPAFCR0070 | SPARE FIL 0070 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 0 | 16416 | 1150 | 0 | EL1134_M54 | 1 | BITVAL
SPAFCR0071 | SPARE FIL 0071 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 2 | 16416 | 1150 | 2 | EL1134_M54 | 5 | BITVAL
SPAFCR0072 | SPARE FIL 0072 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 4 | 16416 | 1150 | 4 | EL1134_M54 | 4 | BITVAL
SPAFCR0073 | SPARE FIL 0073 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 6 | 16416 | 1150 | 6 | EL1134_M54 | 8 | BITVAL
SPAFCR0074 | SPARE FIL 0074 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 8 | 16416 | 1151 | 0 | EL1134_M55 | 1 | BITVAL
SPAFCR0075 | SPARE FIL 0075 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 10 | 16416 | 1151 | 2 | EL1134_M55 | 5 | BITVAL
SPAFCR0076 | SPARE FIL 0076 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 12 | 16416 | 1151 | 4 | EL1134_M55 | 4 | BITVAL
SPAFCR0077 | SPARE FIL 0077 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12864 | 14 | 16416 | 1151 | 6 | EL1134_M55 | 8 | BITVAL
SPB6006 | CR PRESSION BOUTEILLE N2 EI LOCAL 101 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 2 | 16416 | 1152 | 2 | EL1134_M57 | 5 | BITVAL
SCX6007G | CENT.EI LOCAL 103 BCV/CCS PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 6 | 16416 | 1152 | 6 | EL1134_M57 | 8 | BITVAL
SCX6007U | CENT.EI LOCAL 103 BCV/CCS PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 8 | 16416 | 1153 | 0 | EL1134_M58 | 1 | BITVAL
SCX6007D | **CENT.EI LOCAL 103 BCV/CCS DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12865 | 10 | 16416 | 1153 | 2 | EL1134_M58 | 5 | BITVAL
SPB6007 | CR PRESSION BOUTEILLE N2 EI LOCAL 103 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 0 | 16416 | 1154 | 0 | EL1134_M59 | 1 | BITVAL
SCX6008G | CENT.EI LOCAL 111 BATT. CAT.III PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 4 | 16416 | 1154 | 4 | EL1134_M59 | 4 | BITVAL
SCX6008U | CENT.EI LOCAL 111 BATT. CAT.III PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 6 | 16416 | 1154 | 6 | EL1134_M59 | 8 | BITVAL
SCX6008D | **CENT.EI LOC 111 BA. CAT.III DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 8 | 16416 | 1155 | 0 | EL1134_M60 | 1 | BITVAL
SPB6008 | CR PRESSION BOUTEILLE N2 EI LOCAL 111 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12866 | 14 | 16416 | 1155 | 6 | EL1134_M60 | 8 | BITVAL
SPAFCR0078 | SPARE FIL 0078 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12867 | 0 | 16416 | 1156 | 0 | EL1134_M61 | 1 | BITVAL
SPAFCR0079 | SPARE FIL 0079 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12867 | 2 | 16416 | 1156 | 2 | EL1134_M61 | 5 | BITVAL
SPAFCR0080 | SPARE FIL 0080 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12867 | 4 | 16416 | 1156 | 4 | EL1134_M61 | 4 | BITVAL
SCX6009G | CENT.EI LOCAL 112 BATT. CAT.III PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12867 | 8 | 16416 | 1157 | 0 | EL1134_M62 | 1 | BITVAL
SCX6009U | CENT.EI LOCAL 112 BATT. CAT.III PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12867 | 10 | 16416 | 1157 | 2 | EL1134_M62 | 5 | BITVAL
SCX6009D | **CENT.EI LOC 112 BA. CAT.III DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12867 | 12 | 16416 | 1157 | 4 | EL1134_M62 | 4 | BITVAL
SPB6009 | CR PRESSION BOUTEILLE N2 EI LOCAL 112 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 2 | 16416 | 1158 | 2 | EL1134_M63 | 5 | BITVAL
SCX6010G | CENT.EI LOCAL 113 UPS PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 6 | 16416 | 1158 | 6 | EL1134_M63 | 8 | BITVAL
SCX6010U | CENT.EI LOCAL 113 UPS PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 8 | 16416 | 1159 | 0 | EL1134_M64 | 1 | BITVAL
SCX6010D | **CENT.EI LOCAL 113 UPS DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12868 | 10 | 16416 | 1159 | 2 | EL1134_M64 | 5 | BITVAL
SPB6010 | CR PRESSION BOUTEILLE N2 EI LOCAL 113 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12869 | 0 | 16416 | 1160 | 0 | EL1134_M65 | 1 | BITVAL
SCX6011G | CENT.EI LOCAL 115 TGBT PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12869 | 4 | 16416 | 1160 | 4 | EL1134_M65 | 4 | BITVAL
SPAFCR0081 | SPARE FIL 0081 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12869 | 6 | 16416 | 1160 | 6 | EL1134_M65 | 8 | BITVAL
SPAFCR0082 | SPARE FIL 0082 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12869 | 8 | 16416 | 1161 | 0 | EL1134_M66 | 1 | BITVAL
SPAFCR0083 | SPARE FIL 0083 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12869 | 10 | 16416 | 1161 | 2 | EL1134_M66 | 5 | BITVAL
SPAFCR0084 | SPARE FIL 0084 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12869 | 12 | 16416 | 1161 | 4 | EL1134_M66 | 4 | BITVAL
SPAFCR0085 | SPARE FIL 0085 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12869 | 14 | 16416 | 1161 | 6 | EL1134_M66 | 8 | BITVAL
SCX6011U | CENT.EI LOCAL 115 TGBT PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 0 | 16416 | 1162 | 0 | EL1134_M68 | 1 | BITVAL
SCX6011D | **CENT.EI LOCAL 115 TGBT DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 2 | 16416 | 1162 | 2 | EL1134_M68 | 5 | BITVAL
SPB6011 | CR PRESSION BOUTEILLE N2 EI LOCAL 115 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 8 | 16416 | 1163 | 0 | EL1134_M69 | 1 | BITVAL
SCX6012G | CENT.EI LOCAL 116 HT PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 12 | 16416 | 1163 | 4 | EL1134_M69 | 4 | BITVAL
SCX6012U | CENT.EI LOCAL 116 HT PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12870 | 14 | 16416 | 1163 | 6 | EL1134_M69 | 8 | BITVAL
SCX6012D | **CENT.EI LOCAL 116 HT DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 0 | 16416 | 1164 | 0 | EL1134_M70 | 1 | BITVAL
SPB6012 | CR PRESSION BOUTEILLE N2 EI LOCAL 116 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 6 | 16416 | 1164 | 6 | EL1134_M70 | 8 | BITVAL
SCX6013G | CENT.EI LOCAL 126 SCC CLIM PRETE | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 10 | 16416 | 1165 | 2 | EL1134_M71 | 5 | BITVAL
SCX6013U | CENT.EI LOCAL 126 SCC CLIM PRES.TENSION | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 12 | 16416 | 1165 | 4 | EL1134_M71 | 4 | BITVAL
SCX6013D | **CENT.EI LOCAL 126 SCC CLIM DEFAUT GENERAL | CR | O | FIL | 1 | S | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12871 | 14 | 16416 | 1165 | 6 | EL1134_M71 | 8 | BITVAL
SPAFCR0086 | SPARE FIL 0086 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12872 | 0 | 16416 | 1166 | 0 | EL1134_M72 | 1 | BITVAL
SPAFCR0087 | SPARE FIL 0087 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12872 | 2 | 16416 | 1166 | 2 | EL1134_M72 | 5 | BITVAL
SPAFCR0088 | SPARE FIL 0088 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12872 | 4 | 16416 | 1166 | 4 | EL1134_M72 | 4 | BITVAL
SPB6013 | CR PRESSION BOUTEILLE N2 EI LOCAL 126 | CR | O | FIL | 1 | S | [26 empty] | NOT | 1000 |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12872 | 10 | 16416 | 1167 | 2 | EL1134_M73 | 5 | BITVAL
ONB6301 | CAPTEUR NIVEAU BAS CUVE 175M3 ZLV VEGA | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 6 | 16416 | 1168 | 6 | EL1134_M74 | 8 | BITVAL
OPP6301M | CR MARCHE POMPE OPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 10 | 16416 | 1169 | 2 | EL1134_M75 | 5 | BITVAL
OPP6301A | CR ARRET POMPE OPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 12 | 16416 | 1169 | 4 | EL1134_M75 | 4 | BITVAL
OPP6301L | CR MODE LOCAL POMPE OPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12873 | 14 | 16416 | 1169 | 6 | EL1134_M75 | 8 | BITVAL
OPP6301R | CR MODE REMOTE POMPE OPP6301 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12874 | 0 | 16416 | 1170 | 0 | EL1134_M76 | 1 | BITVAL
OPP6302M | CR MARCHE POMPE OPP6302 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12874 | 4 | 16416 | 1170 | 4 | EL1134_M76 | 4 | BITVAL
SPAFCR0089 | SPARE FIL 0089 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12874 | 6 | 16416 | 1170 | 6 | EL1134_M76 | 8 | BITVAL
SPAFCR0090 | SPARE FIL 0090 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12874 | 8 | 16416 | 1171 | 0 | EL1134_M77 | 1 | BITVAL
SPAFCR0091 | SPARE FIL 0091 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12874 | 10 | 16416 | 1171 | 2 | EL1134_M77 | 5 | BITVAL
SPAFCR0092 | SPARE FIL 0092 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12874 | 12 | 16416 | 1171 | 4 | EL1134_M77 | 4 | BITVAL
SPAFCR0093 | SPARE FIL 0093 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12874 | 14 | 16416 | 1171 | 6 | EL1134_M77 | 8 | BITVAL
OPP6302A | CR ARRET POMPE OPP6302 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12875 | 0 | 16416 | 1172 | 0 | EL1134_M79 | 1 | BITVAL
OPP6302L | CR MODE LOCAL POMPE OPP6302 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12875 | 2 | 16416 | 1172 | 2 | EL1134_M79 | 5 | BITVAL
OPP6302R | CR MODE REMOTE POMPE OPP6302 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12875 | 4 | 16416 | 1172 | 4 | EL1134_M79 | 4 | BITVAL
OQB6301 | SEUIL BAS DEBIT POMPE 1 CUVE 175M3 ZLV VEGA | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12875 | 8 | 16416 | 1173 | 0 | EL1134_M80 | 1 | BITVAL
OQB6302 | SEUIL BAS DEBIT POMPE 2 CUVE 175M3 ZLV VEGA | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12875 | 10 | 16416 | 1173 | 2 | EL1134_M80 | 5 | BITVAL
SPAFCR0094 | SPARE FIL 0094 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12875 | 14 | 16416 | 1173 | 6 | EL1134_M80 | 8 | BITVAL
OVM6317O | VM PIED DE MAT RINCAGE ZLV OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 2 | 16416 | 1174 | 2 | EL1134_M81 | 5 | BITVAL
OVM6317F | VM PIED DE MAT RINCAGE ZLV FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 4 | 16416 | 1174 | 4 | EL1134_M81 | 4 | BITVAL
OVM6325O | VM PORTIQUE VEGA POSITION ARRIERE OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 6 | 16416 | 1174 | 6 | EL1134_M81 | 8 | BITVAL
OVM6325F | VM PORTIQUE VEGA POSITION ARRIERE FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 8 | 16416 | 1175 | 0 | EL1134_M82 | 1 | BITVAL
OVM6326F | VM PORTIQUE VEGA POSITION ARRIERE FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | VG03 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 10 | 16416 | 1175 | 2 | EL1134_M82 | 5 | BITVAL
OVM6330O | VM VIDANGE CARNEAU VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 12 | 16416 | 1175 | 4 | EL1134_M82 | 4 | BITVAL
OVM6330F | VM VIDANGE CARNEAU VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12876 | 14 | 16416 | 1175 | 6 | EL1134_M82 | 8 | BITVAL
SPAFCR0095 | SPARE FIL 0095 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12877 | 0 | 16416 | 1176 | 0 | EL1134_M83 | 1 | BITVAL
SPAFCR0096 | SPARE FIL 0096 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12877 | 2 | 16416 | 1176 | 2 | EL1134_M83 | 5 | BITVAL
SPAFCR0097 | SPARE FIL 0097 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12877 | 4 | 16416 | 1176 | 4 | EL1134_M83 | 4 | BITVAL
OVM6331O | VM VIDANGE CARNEAU VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12877 | 6 | 16416 | 1176 | 6 | EL1134_M83 | 8 | BITVAL
OVM6331F | VM VIDANGE CARNEAU VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | VG04 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12877 | 8 | 16416 | 1177 | 0 | EL1134_M84 | 1 | BITVAL
OVM6332O | VM OVM6332 (CUVE 175M3) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12877 | 10 | 16416 | 1177 | 2 | EL1134_M84 | 5 | BITVAL
OVM6332F | VM OVM6332 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12877 | 12 | 16416 | 1177 | 4 | EL1134_M84 | 4 | BITVAL
OVM6333O | VM OVM6333 (CUVE 175M3) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12877 | 14 | 16416 | 1177 | 6 | EL1134_M84 | 8 | BITVAL
OVM6333F | VM OVM6333 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12878 | 0 | 16416 | 1178 | 0 | EL1134_M85 | 1 | BITVAL
OVM6334O | VM OVM6334 (CUVE 175M3) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12878 | 2 | 16416 | 1178 | 2 | EL1134_M85 | 5 | BITVAL
OVM6334F | VM OVM6334 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12878 | 4 | 16416 | 1178 | 4 | EL1134_M85 | 4 | BITVAL
OVM6342F | VM OVM6342 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OVM6342O |  | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12879 | 4 | 16416 | 1180 | 4 | EL1134_M87 | 4 | BITVAL
SPAFCR0098 | SPARE FIL 0098 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12879 | 6 | 16416 | 1180 | 6 | EL1134_M87 | 8 | BITVAL
SPAFCR0099 | SPARE FIL 0099 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12879 | 8 | 16416 | 1181 | 0 | EL1134_M88 | 1 | BITVAL
SPAFCR0100 | SPARE FIL 0100 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12879 | 10 | 16416 | 1181 | 2 | EL1134_M88 | 5 | BITVAL
SPAFCR0101 | SPARE FIL 0101 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12879 | 12 | 16416 | 1181 | 4 | EL1134_M88 | 4 | BITVAL
SPAFCR0102 | SPARE FIL 0102 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12879 | 14 | 16416 | 1181 | 6 | EL1134_M88 | 8 | BITVAL
OVM6344O | VM OVM6344 (CUVE 175M3) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 0 | 16416 | 1182 | 0 | EL1134_M90 | 1 | BITVAL
OVM6344F | VM OVM6344 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 2 | 16416 | 1182 | 2 | EL1134_M90 | 5 | BITVAL
NVM6305F | VM NVM6305 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 4 | 16416 | 1182 | 4 | EL1134_M90 | 4 | BITVAL
NVM6305O | VM NVM6305 (TRAITEMET N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 6 | 16416 | 1182 | 6 | EL1134_M90 | 8 | BITVAL
NVM6306F | VM NVM6306 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 8 | 16416 | 1183 | 0 | EL1134_M91 | 1 | BITVAL
NVM6306O | VM NVM6306 (TRAITEMET N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 10 | 16416 | 1183 | 2 | EL1134_M91 | 5 | BITVAL
NVM6307F | VM NVM6307 (TRAITEMET N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 12 | 16416 | 1183 | 4 | EL1134_M91 | 4 | BITVAL
NVM6307O | VM NVM6307 (TRAITEMET N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12880 | 14 | 16416 | 1183 | 6 | EL1134_M91 | 8 | BITVAL
NPP6001A | ARRET POMPE H2O2 ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG) | CCS | [5 empty] | 12881 | 0 | 16416 | 1184 | 0 | EL1134_M92 | 1 | BITVAL
NPP6001M | MARCHE POMPE H2O2 ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG) | CCS | [5 empty] | 12881 | 2 | 16416 | 1184 | 2 | EL1134_M92 | 5 | BITVAL
OVM6355F | VM VIDANGE CUVE 175M3 VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12881 | 4 | 16416 | 1184 | 4 | EL1134_M92 | 4 | BITVAL
OVM6356F | VM OVM6356 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12881 | 8 | 16416 | 1185 | 0 | EL1134_M93 | 1 | BITVAL
OVM6357F | VM OVM6357 (CUVE 175M3) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OVM6357O |  | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12881 | 10 | 16416 | 1185 | 2 | EL1134_M93 | 5 | BITVAL
NPP6001D | DEFAUT POMPE H2O2 ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG) | CCS | [5 empty] | 12881 | 12 | 16416 | 1185 | 4 | EL1134_M93 | 4 | BITVAL
SPAFCR0103 | SPARE FIL 0103 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12881 | 14 | 16416 | 1185 | 6 | EL1134_M93 | 8 | BITVAL
SPAFCR0104 | SPARE FIL 0104 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12882 | 0 | 16416 | 1186 | 0 | EL1134_M94 | 1 | BITVAL
SPAFCR0105 | SPARE FIL 0105 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12882 | 2 | 16416 | 1186 | 2 | EL1134_M94 | 5 | BITVAL
SPAFCR0106 | SPARE FIL 0106 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12882 | 4 | 16416 | 1186 | 4 | EL1134_M94 | 4 | BITVAL
OVM6371F | VM OVM6371 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | VG06 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12882 | 6 | 16416 | 1186 | 6 | EL1134_M94 | 8 | BITVAL
OVM6372O | VM OVM6372 (COLONNE N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12882 | 8 | 16416 | 1187 | 0 | EL1134_M95 | 1 | BITVAL
OVM6372F | VM OVM6372 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12882 | 10 | 16416 | 1187 | 2 | EL1134_M95 | 5 | BITVAL
OVM6373F | VM OVM6373 (COLONNE N)FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6370 |  | NOT | 1000 |  | VG06 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12882 | 12 | 16416 | 1187 | 4 | EL1134_M95 | 4 | BITVAL
OVM6374F | VM OVM6374 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6370 |  | NOT | 1000 |  | VG06 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12882 | 14 | 16416 | 1187 | 6 | EL1134_M95 | 8 | BITVAL
OVM6375F | VM OVM6375 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6370 |  | NOT | 1000 |  | VG06 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 0 | 16416 | 1188 | 0 | EL1134_M96 | 1 | BITVAL
OVM6376O | VM OVM6376 (COLONNE N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 2 | 16416 | 1188 | 2 | EL1134_M96 | 5 | BITVAL
OVM6376F | VM OVM6376 (COLONNE N)FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 4 | 16416 | 1188 | 4 | EL1134_M96 | 4 | BITVAL
OVM6377O | VM OVM6377 (COLONNE N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 6 | 16416 | 1188 | 6 | EL1134_M96 | 8 | BITVAL
OVM6377F | VM OVM6377 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 8 | 16416 | 1189 | 0 | EL1134_M97 | 1 | BITVAL
OVM6378O | VM OVM6378 (COLONNE N) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 10 | 16416 | 1189 | 2 | EL1134_M97 | 5 | BITVAL
OVM6378F | VM OVM6378 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 12 | 16416 | 1189 | 4 | EL1134_M97 | 4 | BITVAL
OVM6379F | VM OVM6379 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6370 |  | NOT | 1000 |  | VG06 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12883 | 14 | 16416 | 1189 | 6 | EL1134_M97 | 8 | BITVAL
OVM6381F | VM OVM6381 (COLONNE N) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | VG05 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12884 | 0 | 16416 | 1190 | 0 | EL1134_M98 | 1 | BITVAL
OVM6382O | VM OVM6382 (COLONNE U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12884 | 2 | 16416 | 1190 | 2 | EL1134_M98 | 5 | BITVAL
OVM6382F | VM OVM6382 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12884 | 4 | 16416 | 1190 | 4 | EL1134_M98 | 4 | BITVAL
SPAFCR0107 | SPARE FIL 0107 | CR | N | FIL | [28 empty] | NOT | [10 empty] | 12884 | 6 | 16416 | 1190 | 6 | EL1134_M98 | 8 | BITVAL
SPAFCR0108 | SPARE FIL 0108 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12884 | 8 | 16416 | 1191 | 0 | EL1134_M99 | 1 | BITVAL
SPAFCR0109 | SPARE FIL 0109 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12884 | 10 | 16416 | 1191 | 2 | EL1134_M99 | 5 | BITVAL
SPAFCR0110 | SPARE FIL 0110 | CR | N | FIL | [28 empty] | POL | [10 empty] | 12884 | 12 | 16416 | 1191 | 4 | EL1134_M99 | 4 | BITVAL
SPAFCR0111 | SPARE FIL 0111 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12884 | 14 | 16416 | 1191 | 6 | EL1134_M99 | 8 | BITVAL
OVM6383F | VM OVM6383 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6380 |  | NOT | 1000 |  | VG05 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 0 | 16416 | 1192 | 0 | EL1134_M101 | 1 | BITVAL
OVM6384F | VM OVM6384 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6380 |  | NOT | 1000 |  | VG05 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 2 | 16416 | 1192 | 2 | EL1134_M101 | 5 | BITVAL
OVM6385F | VM OVM6385 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6380 |  | NOT | 1000 |  | VG05 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 4 | 16416 | 1192 | 4 | EL1134_M101 | 4 | BITVAL
OVM6386O | VM OVM6386 (COLONNE U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 6 | 16416 | 1192 | 6 | EL1134_M101 | 8 | BITVAL
OVM6386F | VM OVM6386 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 8 | 16416 | 1193 | 0 | EL1134_M102 | 1 | BITVAL
OVM6387O | VM OVM6387 (COLONNE U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 10 | 16416 | 1193 | 2 | EL1134_M102 | 5 | BITVAL
OVM6387F | VM OVM6387 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 12 | 16416 | 1193 | 4 | EL1134_M102 | 4 | BITVAL
OVM6388O | VM OVM6388 (COLONNE U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12885 | 14 | 16416 | 1193 | 6 | EL1134_M102 | 8 | BITVAL
OVM6388F | VM OVM6388 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 0 | 16416 | 1194 | 0 | EL1134_M103 | 1 | BITVAL
OVM6389F | VM OVM6389 (COLONNE U) FERMEE | CR | N | FIL | 1 | F | [24 empty] | OSY6380 |  | NOT | 1000 |  | VG05 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 2 | 16416 | 1194 | 2 | EL1134_M103 | 5 | BITVAL
OVP6312O | CRO VANNE PILOTEE PIED DE MAT RINCAGE ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 4 | 16416 | 1194 | 4 | EL1134_M103 | 4 | BITVAL
OVP6312F | CRF VANNE PILOTEE PIED DE MAT RINCAGE ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 6 | 16416 | 1194 | 6 | EL1134_M103 | 8 | BITVAL
OVP6313O | CRO VANNE PILOTEE RINCAGE TABLE PALETTE ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 8 | 16416 | 1195 | 0 | EL1134_M104 | 1 | BITVAL
OVP6313F | CRF VANNE PILOTEE RINCAGE TABLE PALETTE ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 10 | 16416 | 1195 | 2 | EL1134_M104 | 5 | BITVAL
OVP6314O | CRO VANNE PILOTEE RINCAGE MAT ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 12 | 16416 | 1195 | 4 | EL1134_M104 | 4 | BITVAL
OVP6314F | CRF VANNE PILOTEE RINCAGE MAT ZLV | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12886 | 14 | 16416 | 1195 | 6 | EL1134_M104 | 8 | BITVAL
SPAFCR0112 | SPARE FIL 0112 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12887 | 0 | 16416 | 1196 | 0 | EL1134_M105 | 1 | BITVAL
SPAFCR0113 | SPARE FIL 0113 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12887 | 2 | 16416 | 1196 | 2 | EL1134_M105 | 5 | BITVAL
SPAFCR0114 | SPARE FIL 0114 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12887 | 4 | 16416 | 1196 | 4 | EL1134_M105 | 4 | BITVAL
NCL6001M | COLONNE LAVAGE N2O4 MARCHE | CR | O | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG | CCS | [5 empty] | 12887 | 12 | 16416 | 1197 | 4 | EL1134_M106 | 4 | BITVAL
NCL6001A | **COLONNE LAVAGE N2O4 ARRETEE | CR | O | FIL | 1 | F | [10 empty] | 0 | [15 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG) | CCS | [5 empty] | 12887 | 14 | 16416 | 1197 | 6 | EL1134_M106 | 8 | BITVAL
NVS6001F | COLONNE LAVAGE N2O4 VANNE SECURITE FERMEE | CR | O | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG | CCS | [5 empty] | 12888 | 0 | 16416 | 1198 | 0 | EL1134_M107 | 1 | BITVAL
NCL6001P | COLONNE LAVAGE N2O4 PRETE A DEMARRER (SYNTH) | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG67 | Moyens Generaux (MG | CCS | [5 empty] | 12888 | 2 | 16416 | 1198 | 2 | EL1134_M107 | 5 | BITVAL
NCL6003D | **COLONNE LAVAGE N2O4 PERTE REDONDANCE POMPE | CR | O | FIL | 1 | F | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG67 | Moyens Generaux (MG | CCS | [5 empty] | 12888 | 4 | 16416 | 1198 | 4 | EL1134_M107 | 4 | BITVAL
NCL6004D | **COLONNE LAVAGE N2O4 PERTE CAPTEUR REDONDE | CR | O | FIL | 1 | F | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG67 | Moyens Generaux (MG | CCS | [5 empty] | 12888 | 6 | 16416 | 1198 | 6 | EL1134_M107 | 8 | BITVAL
UCL6001M | COLONNE LAVAGE UDMH MARCHE | CR | O | FIL | 1 | S;F;D | [26 empty] | NOT | 1000 |  | MG66 | Moyens Generaux (MG | CCS | [5 empty] | 12888 | 12 | 16416 | 1199 | 4 | EL1134_M108 | 4 | BITVAL
UCL6001A | **COLONNE LAVAGE UDMH ARRETEE | CR | O | FIL | 1 | S;F;D | [10 empty] | 0 | [15 empty] | NOT | 1000 |  | MG66 | Moyens Generaux (MG) | CCS | [5 empty] | 12888 | 14 | 16416 | 1199 | 6 | EL1134_M108 | 8 | BITVAL
UVS6001F | COLONNE LAVAGE UDMH VANNE SECURITE FERMEE | CR | O | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66; | Moyens Generaux (MG | CCS | [5 empty] | 12889 | 0 | 16416 | 1200 | 0 | EL1134_M109 | 1 | BITVAL
UCL6001P | COLONNE LAVAGE UDMH PRETE A DEMARRER (SYNTH) | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG66 | Moyens Generaux (MG | CCS | [5 empty] | 12889 | 2 | 16416 | 1200 | 2 | EL1134_M109 | 5 | BITVAL
UCL6003D | **COLONNE LAVAGE UDMH PERTE REDONDANCE POMPE | CR | O | FIL | 1 | F | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG66 | Moyens Generaux (MG | CCS | [5 empty] | 12889 | 4 | 16416 | 1200 | 4 | EL1134_M109 | 4 | BITVAL
SPAFCR0115 | SPARE FIL 0115 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12889 | 6 | 16416 | 1200 | 6 | EL1134_M109 | 8 | BITVAL
SPAFCR0116 | SPARE FIL 0116 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12889 | 8 | 16416 | 1201 | 0 | EL1134_M110 | 1 | BITVAL
SPAFCR0117 | SPARE FIL 0117 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12889 | 10 | 16416 | 1201 | 2 | EL1134_M110 | 5 | BITVAL
SPAFCR0118 | SPARE FIL 0118 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12889 | 12 | 16416 | 1201 | 4 | EL1134_M110 | 4 | BITVAL
SPAFCR0119 | SPARE FIL 0119 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12889 | 14 | 16416 | 1201 | 6 | EL1134_M110 | 8 | BITVAL
UCL6004D | **COLONNE LAVAGE UDMH PERTE CAPTEUR REDONDE | CR | O | FIL | 1 | F | [10 empty] | 0 | [11 empty] | NEQUAL |  |  |  | NOT | 1000 |  | MG66 | Moyens Generaux (MG | CCS | [5 empty] | 12890 | 0 | 16416 | 1202 | 0 | EL1134_M112 | 1 | BITVAL
OVM6343F | VM OVM6343 (PIED DE MAT ZLV) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | VG03 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12890 | 14 | 16416 | 1203 | 6 | EL1134_M113 | 8 | BITVAL
OVM6301O | VM PORTIQUE VEGA POSITION AVANT OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12891 | 0 | 16416 | 1204 | 0 | EL1134_M114 | 1 | BITVAL
OVM6302F | VM PORTIQUE VEGA POSITION AVANT FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | VG03 | Process Fluide et Energie General (VG) | CCS | [5 empty] | 12891 | 2 | 16416 | 1204 | 2 | EL1134_M114 | 5 | BITVAL
OVM6301F | VM PORTIQUE VEGA POSITION AVANT FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12891 | 6 | 16416 | 1204 | 6 | EL1134_M114 | 8 | BITVAL
SPAFCR0120 | SPARE FIL 0120 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12891 | 8 | 16416 | 1205 | 0 | EL1134_M115 | 1 | BITVAL
SPAFCR0121 | SPARE FIL 0121 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12891 | 10 | 16416 | 1205 | 2 | EL1134_M115 | 5 | BITVAL
SPAFCR0122 | SPARE FIL 0122 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12891 | 12 | 16416 | 1205 | 4 | EL1134_M115 | 4 | BITVAL
SPAFCR0123 | SPARE FIL 0123 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12891 | 14 | 16416 | 1205 | 6 | EL1134_M115 | 8 | BITVAL
SPAFCR0124 | SPARE FIL 0124 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 0 | 16416 | 1206 | 0 | EL1134_M116 | 1 | BITVAL
SPAFCR0125 | SPARE FIL 0125 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 2 | 16416 | 1206 | 2 | EL1134_M116 | 5 | BITVAL
SPAFCR0126 | SPARE FIL 0126 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 4 | 16416 | 1206 | 4 | EL1134_M116 | 4 | BITVAL
SPAFCR0127 | SPARE FIL 0127 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 6 | 16416 | 1206 | 6 | EL1134_M116 | 8 | BITVAL
SPAFCR0128 | SPARE FIL 0128 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 8 | 16416 | 1207 | 0 | EL1134_M117 | 1 | BITVAL
SPAFCR0129 | SPARE FIL 0129 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 10 | 16416 | 1207 | 2 | EL1134_M117 | 5 | BITVAL
SPAFCR0130 | SPARE FIL 0130 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 12 | 16416 | 1207 | 4 | EL1134_M117 | 4 | BITVAL
SPAFCR0131 | SPARE FIL 0131 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12892 | 14 | 16416 | 1207 | 6 | EL1134_M117 | 8 | BITVAL
SPAFCR0132 | SPARE FIL 0132 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 0 | 16416 | 1208 | 0 | EL1134_M118 | 1 | BITVAL
SPAFCR0133 | SPARE FIL 0133 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 2 | 16416 | 1208 | 2 | EL1134_M118 | 5 | BITVAL
SPAFCR0134 | SPARE FIL 0134 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 4 | 16416 | 1208 | 4 | EL1134_M118 | 4 | BITVAL
SPAFCR0135 | SPARE FIL 0135 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 6 | 16416 | 1208 | 6 | EL1134_M118 | 8 | BITVAL
SPAFCR0136 | SPARE FIL 0136 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 8 | 16416 | 1209 | 0 | EL1134_M119 | 1 | BITVAL
SPAFCR0137 | SPARE FIL 0137 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 10 | 16416 | 1209 | 2 | EL1134_M119 | 5 | BITVAL
SPAFCR0138 | SPARE FIL 0138 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 12 | 16416 | 1209 | 4 | EL1134_M119 | 4 | BITVAL
SPAFCR0139 | SPARE FIL 0139 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12893 | 14 | 16416 | 1209 | 6 | EL1134_M119 | 8 | BITVAL
SPAFCR0140 | SPARE FIL 0140 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 0 | 16416 | 1210 | 0 | EL1134_M120 | 1 | BITVAL
SPAFCR0141 | SPARE FIL 0141 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 2 | 16416 | 1210 | 2 | EL1134_M120 | 5 | BITVAL
SPAFCR0142 | SPARE FIL 0142 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 4 | 16416 | 1210 | 4 | EL1134_M120 | 4 | BITVAL
SPAFCR0143 | SPARE FIL 0143 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 6 | 16416 | 1210 | 6 | EL1134_M120 | 8 | BITVAL
SPAFCR0144 | SPARE FIL 0144 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 8 | 16416 | 1211 | 0 | EL1134_M121 | 1 | BITVAL
SPAFCR0145 | SPARE FIL 0145 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 10 | 16416 | 1211 | 2 | EL1134_M121 | 5 | BITVAL
SPAFCR0146 | SPARE FIL 0146 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 12 | 16416 | 1211 | 4 | EL1134_M121 | 4 | BITVAL
SPAFCR0147 | SPARE FIL 0147 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12894 | 14 | 16416 | 1211 | 6 | EL1134_M121 | 8 | BITVAL
OVM6308F | VM RINCAGE LOCAL UDMH PORTIQUE VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 0 | 16416 | 1212 | 0 | EL1134_M123 | 1 | BITVAL
OVM6308O | VM RINCAGE LOCAL UDMH PORTIQUE VEGA OUVERT | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 2 | 16416 | 1212 | 2 | EL1134_M123 | 5 | BITVAL
OVM6309F | VM RINCAGE LOCAL UDMH PORTIQUE VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 4 | 16416 | 1212 | 4 | EL1134_M123 | 4 | BITVAL
OVM6309O | VM RINCAGE LOCAL UDMH PORTIQUE VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 6 | 16416 | 1212 | 6 | EL1134_M123 | 8 | BITVAL
OVM6312F | VM DELUGE LANCEUR VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 8 | 16416 | 1213 | 0 | EL1134_M124 | 1 | BITVAL
OVM6312O | VM DELUGE LANCEUR VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 10 | 16416 | 1213 | 2 | EL1134_M124 | 5 | BITVAL
OVM6313F | VM DELUGE LANCEUR VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 12 | 16416 | 1213 | 4 | EL1134_M124 | 4 | BITVAL
OVM6313O | VM DELUGE LANCEUR VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12895 | 14 | 16416 | 1213 | 6 | EL1134_M124 | 8 | BITVAL
OVM6323F | CR FERMETURE OVM6323 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 0 | 16416 | 1214 | 0 | EL1134_M125 | 1 | BITVAL
OVM6323O | CR OUVERTURE OVM6323 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 2 | 16416 | 1214 | 2 | EL1134_M125 | 5 | BITVAL
OVM6324F | CR FERMETURE OVM6324 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 4 | 16416 | 1214 | 4 | EL1134_M125 | 4 | BITVAL
OVM6324O | CR OUVERTURE OVM6324 | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 6 | 16416 | 1214 | 6 | EL1134_M125 | 8 | BITVAL
OVP6301F | VP RINCAGE LOCAL UDMH PORTIQUE VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 8 | 16416 | 1215 | 0 | EL1134_M126 | 1 | BITVAL
OVP6301O | VP RINCAGE LOCAL UDMH PORTIQUE VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 10 | 16416 | 1215 | 2 | EL1134_M126 | 5 | BITVAL
OVP6302F | VP RINCAGE LOCAL UDMH PORTIQUE VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 12 | 16416 | 1215 | 4 | EL1134_M126 | 4 | BITVAL
OVP6302O | VP RINCAGE LOCAL UDMH PORTIQUE VEGA OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12896 | 14 | 16416 | 1215 | 6 | EL1134_M126 | 8 | BITVAL
OVM6390F | VM DELUGE LANCEUR VEGA-C FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63 | Moyens Gerneraux (MG) | CCS | [5 empty] | 12897 | 0 | 16416 | 1216 | 0 | EL1134_M127 | 1 | BITVAL
OVM6390O | VM DELUGE LANCEUR VEGA-C OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63 | Moyens Gerneraux (MG) | CCS | [5 empty] | 12897 | 2 | 16416 | 1216 | 2 | EL1134_M127 | 5 | BITVAL
SPAFCR0148 | SPARE FIL 0148 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12897 | 4 | 16416 | 1216 | 4 | EL1134_M127 | 4 | BITVAL
OVP6303F | VP DELUGE LANCEUR VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12897 | 6 | 16416 | 1216 | 6 | EL1134_M127 | 8 | BITVAL
OVP6304F | VP DELUGE LANCEUR VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12897 | 10 | 16416 | 1217 | 2 | EL1134_M128 | 5 | BITVAL
OVP6305F | VP DELUGE LANCEUR VEGA FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12897 | 14 | 16416 | 1217 | 6 | EL1134_M128 | 8 | BITVAL
SPAFCR0149 | SPARE FIL 0149 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12898 | 6 | 16416 | 1218 | 6 | EL1134_M129 | 8 | BITVAL
SPAFCR0150 | SPARE FIL 0150 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12898 | 8 | 16416 | 1219 | 0 | EL1134_M130 | 1 | BITVAL
SPAFCR0151 | SPARE FIL 0151 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12898 | 10 | 16416 | 1219 | 2 | EL1134_M130 | 5 | BITVAL
SPAFCR0152 | SPARE FIL 0152 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12898 | 12 | 16416 | 1219 | 4 | EL1134_M130 | 4 | BITVAL
SPAFCR0153 | SPARE FIL 0153 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12898 | 14 | 16416 | 1219 | 6 | EL1134_M130 | 8 | BITVAL
SPAFCR0154 | SPARE FIL 0154 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 0 | 16416 | 1220 | 0 | EL1134_M131 | 1 | BITVAL
SPAFCR0155 | SPARE FIL 0155 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 2 | 16416 | 1220 | 2 | EL1134_M131 | 5 | BITVAL
SPAFCR0156 | SPARE FIL 0156 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 4 | 16416 | 1220 | 4 | EL1134_M131 | 4 | BITVAL
SPAFCR0157 | SPARE FIL 0157 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 6 | 16416 | 1220 | 6 | EL1134_M131 | 8 | BITVAL
SPAFCR0158 | SPARE FIL 0158 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 8 | 16416 | 1221 | 0 | EL1134_M132 | 1 | BITVAL
SPAFCR0159 | SPARE FIL 0159 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 10 | 16416 | 1221 | 2 | EL1134_M132 | 5 | BITVAL
SPAFCR0160 | SPARE FIL 0160 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 12 | 16416 | 1221 | 4 | EL1134_M132 | 4 | BITVAL
SPAFCR0161 | SPARE FIL 0161 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12899 | 14 | 16416 | 1221 | 6 | EL1134_M132 | 8 | BITVAL
UVM6301F | VM UVM6301 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 0 | 16416 | 1222 | 0 | EL1134_M134 | 1 | BITVAL
UVM6301O | VM UVM6301 (TRAITEMET U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 2 | 16416 | 1222 | 2 | EL1134_M134 | 5 | BITVAL
UVM6302F | VM UVM6302 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 4 | 16416 | 1222 | 4 | EL1134_M134 | 4 | BITVAL
UVM6302O | VM UVM6302 (TRAITEMET U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 6 | 16416 | 1222 | 6 | EL1134_M134 | 8 | BITVAL
UVM6303F | VM UVM6303 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 8 | 16416 | 1223 | 0 | EL1134_M135 | 1 | BITVAL
UVM6303O | VM UVM6303 (TRAITEMET U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 10 | 16416 | 1223 | 2 | EL1134_M135 | 5 | BITVAL
UVM6304F | VM UVM6304 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12900 | 12 | 16416 | 1223 | 4 | EL1134_M135 | 4 | BITVAL
UVM6305F | VM UVM6305 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12901 | 0 | 16416 | 1224 | 0 | EL1134_M136 | 1 | BITVAL
UVM6305O | VM UVM6305 (TRAITEMET U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12901 | 2 | 16416 | 1224 | 2 | EL1134_M136 | 5 | BITVAL
UVM6306F | VM UVM6306 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12901 | 4 | 16416 | 1224 | 4 | EL1134_M136 | 4 | BITVAL
UVM6306O | VM UVM6306 (TRAITEMET U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12901 | 6 | 16416 | 1224 | 6 | EL1134_M136 | 8 | BITVAL
UVM6307F | VM UVM6307 (TRAITEMET U) FERMEE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12901 | 8 | 16416 | 1225 | 0 | EL1134_M137 | 1 | BITVAL
UVM6307O | VM UVM6307 (TRAITEMET U) OUVERTE | CR | N | FIL | 1 | F | [26 empty] | NOT | 1000 |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG) | CCS | [5 empty] | 12901 | 10 | 16416 | 1225 | 2 | EL1134_M137 | 5 | BITVAL
SPAFCR0162 | SPARE FIL 0162 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12901 | 12 | 16416 | 1225 | 4 | EL1134_M137 | 4 | BITVAL
SPAFCR0163 | SPARE FIL 0163 | CR | N | FIL | [28 empty] | NOT | 10000 | [9 empty] | 12901 | 14 | 16416 | 1225 | 6 | EL1134_M137 | 8 | BITVAL
SPAFCR0164 | SPARE FIL 0164 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 0 | 16416 | 1226 | 0 | EL1134_M138 | 1 | BITVAL
SPAFCR0165 | SPARE FIL 0165 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 2 | 16416 | 1226 | 2 | EL1134_M138 | 5 | BITVAL
SPAFCR0166 | SPARE FIL 0166 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 4 | 16416 | 1226 | 4 | EL1134_M138 | 4 | BITVAL
SPAFCR0167 | SPARE FIL 0167 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 6 | 16416 | 1226 | 6 | EL1134_M138 | 8 | BITVAL
SPAFCR0168 | SPARE FIL 0168 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 8 | 16416 | 1227 | 0 | EL1134_M139 | 1 | BITVAL
SPAFCR0169 | SPARE FIL 0169 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 10 | 16416 | 1227 | 2 | EL1134_M139 | 5 | BITVAL
SPAFCR0170 | SPARE FIL 0170 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 12 | 16416 | 1227 | 4 | EL1134_M139 | 4 | BITVAL
SPAFCR0171 | SPARE FIL 0171 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12902 | 14 | 16416 | 1227 | 6 | EL1134_M139 | 8 | BITVAL
SPAFCR0172 | SPARE FIL 0172 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 0 | 16416 | 1228 | 0 | EL1134_M140 | 1 | BITVAL
SPAFCR0173 | SPARE FIL 0173 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 2 | 16416 | 1228 | 2 | EL1134_M140 | 5 | BITVAL
SPAFCR0174 | SPARE FIL 0174 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 4 | 16416 | 1228 | 4 | EL1134_M140 | 4 | BITVAL
SPAFCR0175 | SPARE FIL 0175 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 6 | 16416 | 1228 | 6 | EL1134_M140 | 8 | BITVAL
SPAFCR0176 | SPARE FIL 0176 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 8 | 16416 | 1229 | 0 | EL1134_M141 | 1 | BITVAL
SPAFCR0177 | SPARE FIL 0177 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 10 | 16416 | 1229 | 2 | EL1134_M141 | 5 | BITVAL
SPAFCR0178 | SPARE FIL 0178 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 12 | 16416 | 1229 | 4 | EL1134_M141 | 4 | BITVAL
SPAFCR0179 | SPARE FIL 0179 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12903 | 14 | 16416 | 1229 | 6 | EL1134_M141 | 8 | BITVAL
SPAFCR0180 | SPARE FIL 0180 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 0 | 16416 | 1230 | 0 | EL1134_M142 | 1 | BITVAL
SPAFCR0181 | SPARE FIL 0181 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 2 | 16416 | 1230 | 2 | EL1134_M142 | 5 | BITVAL
SPAFCR0182 | SPARE FIL 0182 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 4 | 16416 | 1230 | 4 | EL1134_M142 | 4 | BITVAL
SPAFCR0183 | SPARE FIL 0183 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 6 | 16416 | 1230 | 6 | EL1134_M142 | 8 | BITVAL
SPAFCR0184 | SPARE FIL 0184 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 8 | 16416 | 1231 | 0 | EL1134_M143 | 1 | BITVAL
SPAFCR0185 | SPARE FIL 0185 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 10 | 16416 | 1231 | 2 | EL1134_M143 | 5 | BITVAL
SPAFCR0186 | SPARE FIL 0186 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 12 | 16416 | 1231 | 4 | EL1134_M143 | 4 | BITVAL
SPAFCR0187 | SPARE FIL 0187 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12904 | 14 | 16416 | 1231 | 6 | EL1134_M143 | 8 | BITVAL
SPAFCR0188 | SPARE FIL 0188 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 0 | 16416 | 1232 | 0 | EL1134_M145 | 1 | BITVAL
SPAFCR0189 | SPARE FIL 0189 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 2 | 16416 | 1232 | 2 | EL1134_M145 | 5 | BITVAL
SPAFCR0190 | SPARE FIL 0190 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 4 | 16416 | 1232 | 4 | EL1134_M145 | 4 | BITVAL
SPAFCR0191 | SPARE FIL 0191 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 6 | 16416 | 1232 | 6 | EL1134_M145 | 8 | BITVAL
SPAFCR0192 | SPARE FIL 0192 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 8 | 16416 | 1233 | 0 | EL1134_M146 | 1 | BITVAL
SPAFCR0193 | SPARE FIL 0193 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 10 | 16416 | 1233 | 2 | EL1134_M146 | 5 | BITVAL
SPAFCR0194 | SPARE FIL 0194 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 12 | 16416 | 1233 | 4 | EL1134_M146 | 4 | BITVAL
SPAFCR0195 | SPARE FIL 0195 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12905 | 14 | 16416 | 1233 | 6 | EL1134_M146 | 8 | BITVAL
SPAFCR0196 | SPARE FIL 0196 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 0 | 16416 | 1234 | 0 | EL1134_M147 | 1 | BITVAL
SPAFCR0197 | SPARE FIL 0197 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 2 | 16416 | 1234 | 2 | EL1134_M147 | 5 | BITVAL
SPAFCR0198 | SPARE FIL 0198 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 4 | 16416 | 1234 | 4 | EL1134_M147 | 4 | BITVAL
SPAFCR0199 | SPARE FIL 0199 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 6 | 16416 | 1234 | 6 | EL1134_M147 | 8 | BITVAL
SPAFCR0200 | SPARE FIL 0200 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 8 | 16416 | 1235 | 0 | EL1134_M148 | 1 | BITVAL
SPAFCR0201 | SPARE FIL 0201 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 10 | 16416 | 1235 | 2 | EL1134_M148 | 5 | BITVAL
SPAFCR0202 | SPARE FIL 0202 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 12 | 16416 | 1235 | 4 | EL1134_M148 | 4 | BITVAL
SPAFCR0203 | SPARE FIL 0203 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12906 | 14 | 16416 | 1235 | 6 | EL1134_M148 | 8 | BITVAL
SPAFCR0204 | SPARE FIL 0204 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 0 | 16416 | 1236 | 0 | EL1134_M149 | 1 | BITVAL
SPAFCR0205 | SPARE FIL 0205 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 2 | 16416 | 1236 | 2 | EL1134_M149 | 5 | BITVAL
SPAFCR0206 | SPARE FIL 0206 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 4 | 16416 | 1236 | 4 | EL1134_M149 | 4 | BITVAL
SPAFCR0207 | SPARE FIL 0207 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 6 | 16416 | 1236 | 6 | EL1134_M149 | 8 | BITVAL
SPAFCR0208 | SPARE FIL 0208 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 8 | 16416 | 1237 | 0 | EL1134_M150 | 1 | BITVAL
SPAFCR0209 | SPARE FIL 0209 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 10 | 16416 | 1237 | 2 | EL1134_M150 | 5 | BITVAL
SPAFCR0210 | SPARE FIL 0210 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 12 | 16416 | 1237 | 4 | EL1134_M150 | 4 | BITVAL
SPAFCR0211 | SPARE FIL 0211 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12907 | 14 | 16416 | 1237 | 6 | EL1134_M150 | 8 | BITVAL
SPAFCR0212 | SPARE FIL 0212 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 0 | 16416 | 1238 | 0 | EL1134_M151 | 1 | BITVAL
SPAFCR0213 | SPARE FIL 0213 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 2 | 16416 | 1238 | 2 | EL1134_M151 | 5 | BITVAL
SPAFCR0214 | SPARE FIL 0214 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 4 | 16416 | 1238 | 4 | EL1134_M151 | 4 | BITVAL
SPAFCR0215 | SPARE FIL 0215 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 6 | 16416 | 1238 | 6 | EL1134_M151 | 8 | BITVAL
SPAFCR0216 | SPARE FIL 0216 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 8 | 16416 | 1239 | 0 | EL1134_M152 | 1 | BITVAL
SPAFCR0217 | SPARE FIL 0217 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 10 | 16416 | 1239 | 2 | EL1134_M152 | 5 | BITVAL
SPAFCR0218 | SPARE FIL 0218 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 12 | 16416 | 1239 | 4 | EL1134_M152 | 4 | BITVAL
SPAFCR0219 | SPARE FIL 0219 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12908 | 14 | 16416 | 1239 | 6 | EL1134_M152 | 8 | BITVAL
SPAFCR0220 | SPARE FIL 0220 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 0 | 16416 | 1240 | 0 | EL1134_M153 | 1 | BITVAL
SPAFCR0221 | SPARE FIL 0221 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 2 | 16416 | 1240 | 2 | EL1134_M153 | 5 | BITVAL
SPASCR0001 | SPARE SER 0001 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3000 | 12 | 13036 | 8 | 16416 | 1495 | 0 | EL6021_M178 |  | BITVAL
SPASCR0002 | SPARE SER 0002 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3000 | 13 | 13036 | 10 | 16416 | 1495 | 2 | EL6021_M178 |  | BITVAL
SPASCR0003 | SPARE SER 0003 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3000 | 14 | 13036 | 12 | 16416 | 1495 | 4 | EL6021_M178 |  | BITVAL
SPASCR0004 | SPARE SER 0004 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3000 | 15 | 13036 | 14 | 16416 | 1495 | 6 | EL6021_M178 |  | BITVAL
SPASCR0005 | SPARE SER 0005 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 4 | 13037 | 8 | 16416 | 1497 | 0 | EL6021_M178 |  | BITVAL
SPASCR0006 | SPARE SER 0006 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 5 | 13037 | 10 | 16416 | 1497 | 2 | EL6021_M178 |  | BITVAL
SPASCR0007 | SPARE SER 0007 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 6 | 13037 | 12 | 16416 | 1497 | 4 | EL6021_M178 |  | BITVAL
SPASCR0008 | SPARE SER 0008 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 7 | 13037 | 14 | 16416 | 1497 | 6 | EL6021_M178 |  | BITVAL
SPASCR0009 | SPARE SER 0009 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 8 | 13038 | 0 | 16416 | 1498 | 0 | EL6021_M178 |  | BITVAL
SPASCR0010 | SPARE SER 0010 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 9 | 13038 | 2 | 16416 | 1498 | 2 | EL6021_M178 |  | BITVAL
SPASCR0011 | SPARE SER 0011 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 10 | 13038 | 4 | 16416 | 1498 | 4 | EL6021_M178 |  | BITVAL
SPASCR0012 | SPARE SER 0012 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 11 | 13038 | 6 | 16416 | 1498 | 6 | EL6021_M178 |  | BITVAL
SPASCR0013 | SPARE SER 0013 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 12 | 13038 | 8 | 16416 | 1499 | 0 | EL6021_M178 |  | BITVAL
SPASCR0014 | SPARE SER 0014 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 13 | 13038 | 10 | 16416 | 1499 | 2 | EL6021_M178 |  | BITVAL
SPASCR0015 | SPARE SER 0015 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 14 | 13038 | 12 | 16416 | 1499 | 4 | EL6021_M178 |  | BITVAL
SPASCR0016 | SPARE SER 0016 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3001 | 15 | 13038 | 14 | 16416 | 1499 | 6 | EL6021_M178 |  | BITVAL
SPASCR0017 | SPARE SER 0017 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3002 | 6 | 13039 | 12 | 16416 | 1501 | 4 | EL6021_M178 |  | BITVAL
SPASCR0018 | SPARE SER 0018 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3002 | 7 | 13039 | 14 | 16416 | 1501 | 6 | EL6021_M178 |  | BITVAL
SPASCR0019 | SPARE SER 0019 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3002 | 10 | 13040 | 4 | 16416 | 1502 | 4 | EL6021_M178 |  | BITVAL
SPASCR0020 | SPARE SER 0020 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3002 | 11 | 13040 | 6 | 16416 | 1502 | 6 | EL6021_M178 |  | BITVAL
SPASCR0021 | SPARE SER 0021 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3002 | 14 | 13040 | 12 | 16416 | 1503 | 4 | EL6021_M178 |  | BITVAL
SPASCR0022 | SPARE SER 0022 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3002 | 15 | 13040 | 14 | 16416 | 1503 | 6 | EL6021_M178 |  | BITVAL
SPASCR0023 | SPARE SER 0023 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3003 | 12 | 13042 | 8 | 16416 | 1507 | 0 | EL6021_M178 |  | BITVAL
SPASCR0024 | SPARE SER 0024 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3003 | 13 | 13042 | 10 | 16416 | 1507 | 2 | EL6021_M178 |  | BITVAL
SPASCR0025 | SPARE SER 0025 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3003 | 14 | 13042 | 12 | 16416 | 1507 | 4 | EL6021_M178 |  | BITVAL
SPASCR0026 | SPARE SER 0026 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3003 | 15 | 13042 | 14 | 16416 | 1507 | 6 | EL6021_M178 |  | BITVAL
SPASCR0145 | SPARE SER 0145 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3004 | 0 | 13043 | 0 | 16416 | 1508 | 0 | EL6021_M178 |  | BITVAL
SPASCR0146 | SPARE SER 0146 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3004 | 1 | 13043 | 2 | 16416 | 1508 | 2 | EL6021_M178 |  | BITVAL
SPASCR0147 | SPARE SER 0147 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3004 | 6 | 13043 | 12 | 16416 | 1509 | 4 | EL6021_M178 |  | BITVAL
SPASCR0148 | SPARE SER 0148 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3004 | 7 | 13043 | 14 | 16416 | 1509 | 6 | EL6021_M178 |  | BITVAL
SPASCR0027 | SPARE SER 0027 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3004 | 12 | 13044 | 8 | 16416 | 1511 | 0 | EL6021_M178 |  | BITVAL
SPASCR0028 | SPARE SER 0028 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3004 | 13 | 13044 | 10 | 16416 | 1511 | 2 | EL6021_M178 |  | BITVAL
SPASCR0029 | SPARE SER 0029 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3004 | 14 | 13044 | 12 | 16416 | 1511 | 4 | EL6021_M178 |  | BITVAL
SPASCR0030 | SPARE SER 0030 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3004 | 15 | 13044 | 14 | 16416 | 1511 | 6 | EL6021_M178 |  | BITVAL
SPASCR0149 | SPARE SER 0149 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3005 | 0 | 13045 | 0 | 16416 | 1512 | 0 | EL6021_M178 |  | BITVAL
SPASCR0150 | SPARE SER 0150 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3005 | 1 | 13045 | 2 | 16416 | 1512 | 2 | EL6021_M178 |  | BITVAL
SPASCR0031 | SPARE SER 0031 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3005 | 6 | 13045 | 12 | 16416 | 1513 | 4 | EL6021_M178 |  | BITVAL
SPASCR0032 | SPARE SER 0032 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3005 | 7 | 13045 | 14 | 16416 | 1513 | 6 | EL6021_M178 |  | BITVAL
SPASCR0033 | SPARE SER 0033 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 8 | 13046 | 0 | 16416 | 1514 | 0 | EL6021_M178 |  | BITVAL
SPASCR0034 | SPARE SER 0034 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 9 | 13046 | 2 | 16416 | 1514 | 2 | EL6021_M178 |  | BITVAL
SPASCR0035 | SPARE SER 0035 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 10 | 13046 | 4 | 16416 | 1514 | 4 | EL6021_M178 |  | BITVAL
SPASCR0036 | SPARE SER 0036 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 11 | 13046 | 6 | 16416 | 1514 | 6 | EL6021_M178 |  | BITVAL
SPASCR0037 | SPARE SER 0037 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 12 | 13046 | 8 | 16416 | 1515 | 0 | EL6021_M178 |  | BITVAL
SPASCR0038 | SPARE SER 0038 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 13 | 13046 | 10 | 16416 | 1515 | 2 | EL6021_M178 |  | BITVAL
SPASCR0039 | SPARE SER 0039 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 14 | 13046 | 12 | 16416 | 1515 | 4 | EL6021_M178 |  | BITVAL
SPASCR0040 | SPARE SER 0040 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3005 | 15 | 13046 | 14 | 16416 | 1515 | 6 | EL6021_M178 |  | BITVAL
SPASCR0041 | SPARE SER 0041 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3006 | 12 | 13048 | 8 | 16416 | 1519 | 0 | EL6021_M178 |  | BITVAL
SPASCR0042 | SPARE SER 0042 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3006 | 13 | 13048 | 10 | 16416 | 1519 | 2 | EL6021_M178 |  | BITVAL
SPASCR0043 | SPARE SER 0043 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3006 | 14 | 13048 | 12 | 16416 | 1519 | 4 | EL6021_M178 |  | BITVAL
SPASCR0044 | SPARE SER 0044 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3006 | 15 | 13048 | 14 | 16416 | 1519 | 6 | EL6021_M178 |  | BITVAL
SPASCR0045 | SPARE SER 0045 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3007 | 2 | 13049 | 4 | 16416 | 1520 | 4 | EL6021_M178 |  | BITVAL
SPASCR0046 | SPARE SER 0046 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3007 | 3 | 13049 | 6 | 16416 | 1520 | 6 | EL6021_M178 |  | BITVAL
SPASCR0047 | SPARE SER 0047 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 4 | 13049 | 8 | 16416 | 1521 | 0 | EL6021_M178 |  | BITVAL
SPASCR0048 | SPARE SER 0048 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 5 | 13049 | 10 | 16416 | 1521 | 2 | EL6021_M178 |  | BITVAL
SPASCR0049 | SPARE SER 0049 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 6 | 13049 | 12 | 16416 | 1521 | 4 | EL6021_M178 |  | BITVAL
SPASCR0050 | SPARE SER 0050 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 7 | 13049 | 14 | 16416 | 1521 | 6 | EL6021_M178 |  | BITVAL
SPASCR0051 | SPARE SER 0051 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 8 | 13050 | 0 | 16416 | 1522 | 0 | EL6021_M178 |  | BITVAL
SPASCR0052 | SPARE SER 0052 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 9 | 13050 | 2 | 16416 | 1522 | 2 | EL6021_M178 |  | BITVAL
SPASCR0053 | SPARE SER 0053 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 10 | 13050 | 4 | 16416 | 1522 | 4 | EL6021_M178 |  | BITVAL
SPASCR0054 | SPARE SER 0054 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 11 | 13050 | 6 | 16416 | 1522 | 6 | EL6021_M178 |  | BITVAL
SPASCR0055 | SPARE SER 0055 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 12 | 13050 | 8 | 16416 | 1523 | 0 | EL6021_M178 |  | BITVAL
SPASCR0056 | SPARE SER 0056 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 13 | 13050 | 10 | 16416 | 1523 | 2 | EL6021_M178 |  | BITVAL
SPASCR0057 | SPARE SER 0057 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 14 | 13050 | 12 | 16416 | 1523 | 4 | EL6021_M178 |  | BITVAL
SPASCR0058 | SPARE SER 0058 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3007 | 15 | 13050 | 14 | 16416 | 1523 | 6 | EL6021_M178 |  | BITVAL
SPASCR0059 | SPARE SER 0059 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 7 | 13055 | 14 | 16416 | 1533 | 6 | EL6021_M178 |  | BITVAL
SPASCR0060 | SPARE SER 0060 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 8 | 13056 | 0 | 16416 | 1534 | 0 | EL6021_M178 |  | BITVAL
SPASCR0061 | SPARE SER 0061 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 9 | 13056 | 2 | 16416 | 1534 | 2 | EL6021_M178 |  | BITVAL
SPASCR0062 | SPARE SER 0062 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 10 | 13056 | 4 | 16416 | 1534 | 4 | EL6021_M178 |  | BITVAL
SPASCR0063 | SPARE SER 0063 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 11 | 13056 | 6 | 16416 | 1534 | 6 | EL6021_M178 |  | BITVAL
SPASCR0064 | SPARE SER 0064 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 12 | 13056 | 8 | 16416 | 1535 | 0 | EL6021_M178 |  | BITVAL
SPASCR0065 | SPARE SER 0065 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 13 | 13056 | 10 | 16416 | 1535 | 2 | EL6021_M178 |  | BITVAL
SPASCR0066 | SPARE SER 0066 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 14 | 13056 | 12 | 16416 | 1535 | 4 | EL6021_M178 |  | BITVAL
SPASCR0067 | SPARE SER 0067 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3010 | 15 | 13056 | 14 | 16416 | 1535 | 6 | EL6021_M178 |  | BITVAL
SPASCR0068 | SPARE SER 0068 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 4 | 13057 | 8 | 16416 | 1537 | 0 | EL6021_M178 |  | BITVAL
SPASCR0069 | SPARE SER 0069 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 5 | 13057 | 10 | 16416 | 1537 | 2 | EL6021_M178 |  | BITVAL
SPASCR0070 | SPARE SER 0070 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 6 | 13057 | 12 | 16416 | 1537 | 4 | EL6021_M178 |  | BITVAL
SPASCR0071 | SPARE SER 0071 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 7 | 13057 | 14 | 16416 | 1537 | 6 | EL6021_M178 |  | BITVAL
SPASCR0072 | SPARE SER 0072 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 8 | 13058 | 0 | 16416 | 1538 | 0 | EL6021_M178 |  | BITVAL
SPASCR0073 | SPARE SER 0073 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 9 | 13058 | 2 | 16416 | 1538 | 2 | EL6021_M178 |  | BITVAL
SPASCR0074 | SPARE SER 0074 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 10 | 13058 | 4 | 16416 | 1538 | 4 | EL6021_M178 |  | BITVAL
SPASCR0075 | SPARE SER 0075 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 11 | 13058 | 6 | 16416 | 1538 | 6 | EL6021_M178 |  | BITVAL
SPASCR0076 | SPARE SER 0076 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 12 | 13058 | 8 | 16416 | 1539 | 0 | EL6021_M178 |  | BITVAL
SPASCR0077 | SPARE SER 0077 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 13 | 13058 | 10 | 16416 | 1539 | 2 | EL6021_M178 |  | BITVAL
SPASCR0078 | SPARE SER 0078 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 14 | 13058 | 12 | 16416 | 1539 | 4 | EL6021_M178 |  | BITVAL
SPASCR0079 | SPARE SER 0079 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3011 | 15 | 13058 | 14 | 16416 | 1539 | 6 | EL6021_M178 |  | BITVAL
SPASCR0080 | SPARE SER 0080 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3012 | 2 | 13059 | 4 | 16416 | 1540 | 4 | EL6021_M178 |  | BITVAL
SPASCR0081 | SPARE SER 0081 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3012 | 3 | 13059 | 6 | 16416 | 1540 | 6 | EL6021_M178 |  | BITVAL
SPASCR0082 | SPARE SER 0082 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 4 | 13059 | 8 | 16416 | 1541 | 0 | EL6021_M178 |  | BITVAL
SPASCR0083 | SPARE SER 0083 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 5 | 13059 | 10 | 16416 | 1541 | 2 | EL6021_M178 |  | BITVAL
SPASCR0084 | SPARE SER 0084 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 6 | 13059 | 12 | 16416 | 1541 | 4 | EL6021_M178 |  | BITVAL
SPASCR0085 | SPARE SER 0085 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 7 | 13059 | 14 | 16416 | 1541 | 6 | EL6021_M178 |  | BITVAL
SPASCR0086 | SPARE SER 0086 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 8 | 13060 | 0 | 16416 | 1542 | 0 | EL6021_M178 |  | BITVAL
SPASCR0087 | SPARE SER 0087 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 9 | 13060 | 2 | 16416 | 1542 | 2 | EL6021_M178 |  | BITVAL
SPASCR0088 | SPARE SER 0088 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 10 | 13060 | 4 | 16416 | 1542 | 4 | EL6021_M178 |  | BITVAL
SPASCR0089 | SPARE SER 0089 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 11 | 13060 | 6 | 16416 | 1542 | 6 | EL6021_M178 |  | BITVAL
SPASCR0090 | SPARE SER 0090 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 12 | 13060 | 8 | 16416 | 1543 | 0 | EL6021_M178 |  | BITVAL
SPASCR0091 | SPARE SER 0091 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 13 | 13060 | 10 | 16416 | 1543 | 2 | EL6021_M178 |  | BITVAL
SPASCR0092 | SPARE SER 0092 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 14 | 13060 | 12 | 16416 | 1543 | 4 | EL6021_M178 |  | BITVAL
SPASCR0093 | SPARE SER 0093 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3012 | 15 | 13060 | 14 | 16416 | 1543 | 6 | EL6021_M178 |  | BITVAL
SPASCR0094 | SPARE SER 0094 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3013 | 9 | 13062 | 2 | 16416 | 1546 | 2 | EL6021_M178 |  | BITVAL
SPASCR0095 | SPARE SER 0095 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3013 | 10 | 13062 | 4 | 16416 | 1546 | 4 | EL6021_M178 |  | BITVAL
SPASCR0096 | SPARE SER 0096 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3013 | 12 | 13062 | 8 | 16416 | 1547 | 0 | EL6021_M178 |  | BITVAL
SPASCR0097 | SPARE SER 0097 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3013 | 13 | 13062 | 10 | 16416 | 1547 | 2 | EL6021_M178 |  | BITVAL
SPASCR0098 | SPARE SER 0098 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3013 | 14 | 13062 | 12 | 16416 | 1547 | 4 | EL6021_M178 |  | BITVAL
SPASCR0099 | SPARE SER 0099 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3013 | 15 | 13062 | 14 | 16416 | 1547 | 6 | EL6021_M178 |  | BITVAL
SPASCR0100 | SPARE SER 0100 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3014 | 9 | 13064 | 2 | 16416 | 1550 | 2 | EL6021_M178 |  | BITVAL
SPASCR0101 | SPARE SER 0101 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3014 | 10 | 13064 | 4 | 16416 | 1550 | 4 | EL6021_M178 |  | BITVAL
SPASCR0102 | SPARE SER 0102 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3014 | 12 | 13064 | 8 | 16416 | 1551 | 0 | EL6021_M178 |  | BITVAL
SPASCR0103 | SPARE SER 0103 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3014 | 13 | 13064 | 10 | 16416 | 1551 | 2 | EL6021_M178 |  | BITVAL
SPASCR0104 | SPARE SER 0104 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3014 | 14 | 13064 | 12 | 16416 | 1551 | 4 | EL6021_M178 |  | BITVAL
SPASCR0105 | SPARE SER 0105 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3014 | 15 | 13064 | 14 | 16416 | 1551 | 6 | EL6021_M178 |  | BITVAL
SPASCR0106 | SPARE SER 0106 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3015 | 9 | 13066 | 2 | 16416 | 1554 | 2 | EL6021_M178 |  | BITVAL
SPASCR0107 | SPARE SER 0107 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3015 | 10 | 13066 | 4 | 16416 | 1554 | 4 | EL6021_M178 |  | BITVAL
SPASCR0108 | SPARE SER 0108 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3015 | 12 | 13066 | 8 | 16416 | 1555 | 0 | EL6021_M178 |  | BITVAL
SPASCR0109 | SPARE SER 0109 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3015 | 13 | 13066 | 10 | 16416 | 1555 | 2 | EL6021_M178 |  | BITVAL
SPASCR0110 | SPARE SER 0110 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3015 | 14 | 13066 | 12 | 16416 | 1555 | 4 | EL6021_M178 |  | BITVAL
SPASCR0111 | SPARE SER 0111 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3015 | 15 | 13066 | 14 | 16416 | 1555 | 6 | EL6021_M178 |  | BITVAL
SPASCR0112 | SPARE SER 0112 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3016 | 9 | 13068 | 2 | 16416 | 1558 | 2 | EL6021_M178 |  | BITVAL
SPASCR0113 | SPARE SER 0113 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3016 | 10 | 13068 | 4 | 16416 | 1558 | 4 | EL6021_M178 |  | BITVAL
SPASCR0114 | SPARE SER 0114 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3016 | 12 | 13068 | 8 | 16416 | 1559 | 0 | EL6021_M178 |  | BITVAL
SPASCR0115 | SPARE SER 0115 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3016 | 13 | 13068 | 10 | 16416 | 1559 | 2 | EL6021_M178 |  | BITVAL
SPASCR0116 | SPARE SER 0116 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3016 | 14 | 13068 | 12 | 16416 | 1559 | 4 | EL6021_M178 |  | BITVAL
SPASCR0117 | SPARE SER 0117 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3016 | 15 | 13068 | 14 | 16416 | 1559 | 6 | EL6021_M178 |  | BITVAL
SPASCR0118 | SPARE SER 0118 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3017 | 13 | 13070 | 10 | 16416 | 1563 | 2 | EL6021_M178 |  | BITVAL
SPASCR0119 | SPARE SER 0119 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3017 | 15 | 13070 | 14 | 16416 | 1563 | 6 | EL6021_M178 |  | BITVAL
SPASCR0120 | SPARE SER 0120 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3018 | 13 | 13072 | 10 | 16416 | 1567 | 2 | EL6021_M178 |  | BITVAL
SPASCR0121 | SPARE SER 0121 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3018 | 15 | 13072 | 14 | 16416 | 1567 | 6 | EL6021_M178 |  | BITVAL
SPASCR0122 | SPARE SER 0122 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3019 | 6 | 13073 | 12 | 16416 | 1569 | 4 | EL6021_M178 |  | BITVAL
SPASCR0123 | SPARE SER 0123 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3019 | 7 | 13073 | 14 | 16416 | 1569 | 6 | EL6021_M178 |  | BITVAL
SPASCR0124 | SPARE SER 0124 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3019 | 9 | 13074 | 2 | 16416 | 1570 | 2 | EL6021_M178 |  | BITVAL
SPASCR0125 | SPARE SER 0125 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3019 | 10 | 13074 | 4 | 16416 | 1570 | 4 | EL6021_M178 |  | BITVAL
SPASCR0126 | SPARE SER 0126 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3019 | 11 | 13074 | 6 | 16416 | 1570 | 6 | EL6021_M178 |  | BITVAL
SPASCR0127 | SPARE SER 0127 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3019 | 12 | 13074 | 8 | 16416 | 1571 | 0 | EL6021_M178 |  | BITVAL
SPASCR0128 | SPARE SER 0128 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3019 | 13 | 13074 | 10 | 16416 | 1571 | 2 | EL6021_M178 |  | BITVAL
SPASCR0129 | SPARE SER 0129 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3019 | 14 | 13074 | 12 | 16416 | 1571 | 4 | EL6021_M178 |  | BITVAL
SPASCR0130 | SPARE SER 0130 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3019 | 15 | 13074 | 14 | 16416 | 1571 | 6 | EL6021_M178 |  | BITVAL
SPASCR0131 | SPARE SER 0131 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 5 | 13077 | 10 | 16416 | 1577 | 2 |  |  | BITVAL
SPASCR0132 | SPARE SER 0132 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 6 | 13077 | 12 | 16416 | 1577 | 4 |  |  | BITVAL
SPASCR0133 | SPARE SER 0133 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 7 | 13077 | 14 | 16416 | 1577 | 6 |  |  | BITVAL
SPASCR0134 | SPARE SER 0134 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 8 | 13078 | 0 | 16416 | 1578 | 0 |  |  | BITVAL
SPASCR0135 | SPARE SER 0135 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 9 | 13078 | 2 | 16416 | 1578 | 2 |  |  | BITVAL
SPASCR0136 | SPARE SER 0136 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 10 | 13078 | 4 | 16416 | 1578 | 4 |  |  | BITVAL
SPASCR0137 | SPARE SER 0137 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 11 | 13078 | 6 | 16416 | 1578 | 6 |  |  | BITVAL
SPASCR0138 | SPARE SER 0138 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 12 | 13078 | 8 | 16416 | 1579 | 0 |  |  | BITVAL
SPASCR0139 | SPARE SER 0139 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 13 | 13078 | 10 | 16416 | 1579 | 2 |  |  | BITVAL
SPASCR0140 | SPARE SER 0140 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 14 | 13078 | 12 | 16416 | 1579 | 4 |  |  | BITVAL
SPASCR0141 | SPARE SER 0141 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3021 | 15 | 13078 | 14 | 16416 | 1579 | 6 |  |  | BITVAL
SPASCR0142 | SPARE SER 0142 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3022 | 15 | 13080 | 14 | 16416 | 1583 | 6 |  |  | BITVAL
EUB6000U | TGBT ZLV PRESENCE TENSION JDB | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 0 | 13090 | 0 | 16416 | 1602 | 0 | EL6021_M178 |  | BITVAL
EUB6001U | TGBT-C ZLV PRESENCE TENSION CAT.II | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 1 | 13090 | 2 | 16416 | 1602 | 2 | EL6021_M178 |  | BITVAL
EUB6002U | TGBT ZLV PRESENCE TENSION CAT.II | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 2 | 13090 | 4 | 16416 | 1602 | 4 | EL6021_M178 |  | BITVAL
EUB6003U | TGBT-C ZLV PRESENCE TENSION CAT.I | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 3 | 13090 | 6 | 16416 | 1602 | 6 | EL6021_M178 |  | BITVAL
EUB6004U | TGBT ZLV PRESENCE TENSION CAT.I | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 4 | 13090 | 8 | 16416 | 1603 | 0 | EL6021_M178 |  | BITVAL
EUB6005U | TGBT-C ZLV PRESENCE TENSION JDB | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 5 | 13090 | 10 | 16416 | 1603 | 2 | EL6021_M178 |  | BITVAL
EQF6950F | TGBT-C ZLV ARRIVEE TM 7001 CAT.II OF DISJ. QF7950 CLOSE | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 6 | 13090 | 12 | 16416 | 1603 | 4 | EL6021_M178 |  | BITVAL
EQF6001F | TGBT ZLV ARRIVEE TM 7002 CAT.II OF DISJ. QF7001 CLOSE | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 7 | 13090 | 14 | 16416 | 1603 | 6 | EL6021_M178 |  | BITVAL
EQF6951F | TGBT-C ZLV ARRIVEE TM 7003 CAT.I OF DISJ. QF7951 CLOSE | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 8 | 13091 | 0 | 16416 | 1604 | 0 | EL6021_M178 |  | BITVAL
EQF6002F | TGBT ZLV ARRIVEE TM 7004 CAT.I OF DISJ. QF7002 CLOSE | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 9 | 13091 | 2 | 16416 | 1604 | 2 | EL6021_M178 |  | BITVAL
EQF6002M | TGBT ZLV MARCHE EN SECOURS INVERSE | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 10 | 13091 | 4 | 16416 | 1604 | 4 | EL6021_M178 |  | BITVAL
EQF6951M | TGBT-C ZLV MARCHE EN SECOURS INVERSE | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 11 | 13091 | 6 | 16416 | 1604 | 6 | EL6021_M178 |  | BITVAL
EQF6003F | TGBT ZLV ARRIVEE GEN SET XS-7001 OF DISJ. QF7003 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 12 | 13091 | 8 | 16416 | 1605 | 0 | EL6021_M178 |  | BITVAL
EQF6952F | TGBT-C ZLV ARRIVEE GEN SET XS-7002 OF DISJ. QF7952 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3035 | 13 | 13091 | 10 | 16416 | 1605 | 2 | EL6021_M178 |  | BITVAL
SPASCR0143 | SPARE SER 0143 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3035 | 14 | 13091 | 12 | 16416 | 1605 | 4 | EL6021_M178 |  | BITVAL
SPASCR1046 | SPARE SER 0144 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3035 | 15 | 13091 | 14 | 16416 | 1605 | 6 | EL6021_M178 |  | BITVAL
EQF6004F | TGBT ZLV DEPART TD LOCAL 012 MOYENS DE SECURITE OF DISJ. QF7004 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 0 | 13092 | 0 | 16416 | 1606 | 0 | EL6021_M178 |  | BITVAL
EQF6004D | TGBT ZLV DEPART TD LOCAL 012 MOYENS DE SECURITE SD DISJ. QF7004 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 1 | 13092 | 2 | 16416 | 1606 | 2 | EL6021_M178 |  | BITVAL
EQF6005F | TGBT ZLV DEPART TDGA NIV 18.400 OF DISJ. QF7005 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 2 | 13092 | 4 | 16416 | 1606 | 4 | EL6021_M178 |  | BITVAL
EQF6005D | TGBT ZLV DEPART TDGA NIV 18.400 SD DISJ. QF7005 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 3 | 13092 | 6 | 16416 | 1606 | 6 | EL6021_M178 |  | BITVAL
EQF6006F | TGBT ZLV DEPART TD LOCAL 103 BCV/VMC OF DISJ. QF7006 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 4 | 13092 | 8 | 16416 | 1607 | 0 | EL6021_M178 |  | BITVAL
EQF6006D | TGBT ZLV DEPART TD LOCAL 103 BCV/VMC SD DISJ. QF7006 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 5 | 13092 | 10 | 16416 | 1607 | 2 | EL6021_M178 |  | BITVAL
EQF6007F | TGBT ZLV DEPART TD LOCAL 102 SAS OF DISJ. QF7007 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 6 | 13092 | 12 | 16416 | 1607 | 4 | EL6021_M178 |  | BITVAL
EQF6007D | TGBT ZLV DEPART TD LOCAL 102 SAS SD DISJ. QF7007 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 7 | 13092 | 14 | 16416 | 1607 | 6 | EL6021_M178 |  | BITVAL
EQF6008F | TGBT ZLV DEPART TD LOCAL 108 FLUIDE OF DISJ. QF7008 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 8 | 13093 | 0 | 16416 | 1608 | 0 | EL6021_M178 |  | BITVAL
EQF6008D | TGBT ZLV DEPART TD LOCAL 108 FLUIDE SD DISJ. QF7008 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 9 | 13093 | 2 | 16416 | 1608 | 2 | EL6021_M178 |  | BITVAL
EQF6009F | TGBT ZLV DEPART TD LOCAL 117 ECLAIRAGE LANCEUR OF DISJ. QF7009 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 10 | 13093 | 4 | 16416 | 1608 | 4 | EL6021_M178 |  | BITVAL
EQF6009D | TGBT ZLV DEPART TD LOCAL 117 ECLAIRAGE LANCEUR SD DISJ. QF7009 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 11 | 13093 | 6 | 16416 | 1608 | 6 | EL6021_M178 |  | BITVAL
EQF6010F | TGBT ZLV DEPART TD LOCAL 115 TGBT OF DISJ. QF7010 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 12 | 13093 | 8 | 16416 | 1609 | 0 | EL6021_M178 |  | BITVAL
EQF6010D | TGBT ZLV DEPART TD LOCAL 115 TGBT SD DISJ. QF7010 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 13 | 13093 | 10 | 16416 | 1609 | 2 | EL6021_M178 |  | BITVAL
EQF6011F | TGBT ZLV DEPART TD LOCAL 117 TD1R OF DISJ. QF7011 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 14 | 13093 | 12 | 16416 | 1609 | 4 | EL6021_M178 |  | BITVAL
EQF6011D | TGBT ZLV DEPART TD LOCAL 117 TD1R SD DISJ. QF7011 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3036 | 15 | 13093 | 14 | 16416 | 1609 | 6 | EL6021_M178 |  | BITVAL
EQF6012F | TGBT ZLV DEPART TD LOCAL 117 TD2R OF DISJ. QF7012 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 0 | 13094 | 0 | 16416 | 1610 | 0 | EL6021_M178 |  | BITVAL
EQF6012D | TGBT ZLV DEPART TD LOCAL 117 TD2R SD DISJ. QF7012 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 1 | 13094 | 2 | 16416 | 1610 | 2 | EL6021_M178 |  | BITVAL
EQF6013F | TGBT ZLV DEPART TD LOCAL 121 PLOMBERIE OF DISJ. QF7013 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 2 | 13094 | 4 | 16416 | 1610 | 4 | EL6021_M178 |  | BITVAL
EQF6013D | TGBT ZLV DEPART TD LOCAL 121 PLOMBERIE SD DISJ. QF7013 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 3 | 13094 | 6 | 16416 | 1610 | 6 | EL6021_M178 |  | BITVAL
EQF6014F | TGBT ZLV DEPART TD LOCAL 102/117 PRISE CAT III MOBILE OF DISJ. QF7014 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 4 | 13094 | 8 | 16416 | 1611 | 0 | EL6021_M178 |  | BITVAL
EQF6014D | TGBT ZLV DEPART TD LOCAL 102/117 PRISE CAT III MOBILE SD DISJ. QF7014 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 5 | 13094 | 10 | 16416 | 1611 | 2 | EL6021_M178 |  | BITVAL
EQF6015F | TGBT ZLV DEPART TD LOCAL 102/117 PRISE CAT III MOBILE OF DISJ. QF7015 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 6 | 13094 | 12 | 16416 | 1611 | 4 | EL6021_M178 |  | BITVAL
EQF6015D | TGBT ZLV DEPART TD LOCAL 102/117 PRISE CAT III MOBILE SD DISJ. QF7015 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 7 | 13094 | 14 | 16416 | 1611 | 6 | EL6021_M178 |  | BITVAL
EQF6016F | TGBT ZLV DEPART HPB2 OF DISJ. QF7016 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 8 | 13095 | 0 | 16416 | 1612 | 0 | EL6021_M178 |  | BITVAL
EQF6016D | TGBT ZLV DEPART HPB2 SD DISJ. QF7016 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 9 | 13095 | 2 | 16416 | 1612 | 2 | EL6021_M178 |  | BITVAL
EQF6017F | TGBT ZLV DEPART ONDULEUR UL7001 CAT.IIIA-1 OF DISJ. QF7017 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61);E61;E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 10 | 13095 | 4 | 16416 | 1612 | 4 | EL6021_M178 |  | BITVAL
EQF6017D | TGBT ZLV DEPART ONDULEUR UL7001 CAT.IIIA-1 SD DISJ. QF7017 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 11 | 13095 | 6 | 16416 | 1612 | 6 | EL6021_M178 |  | BITVAL
EQF6018F | TGBT ZLV DEPART BYPASS UL7001/7002 CAT.IIIA OF DISJ. QF7018 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 12 | 13095 | 8 | 16416 | 1613 | 0 | EL6021_M178 |  | BITVAL
EQF6018D | TGBT ZLV DEPART BYPASS UL7001/7002 CAT.IIIA SD DISJ. QF7018 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 13 | 13095 | 10 | 16416 | 1613 | 2 | EL6021_M178 |  | BITVAL
EQF6019F | TGBT ZLV DEPART ONDULEUR UL7002 CAT.IIIA-2 OF DISJ. QF7019 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 14 | 13095 | 12 | 16416 | 1613 | 4 | EL6021_M178 |  | BITVAL
EQF6019D | TGBT ZLV DEPART ONDULEUR UL7002 CAT.IIIA-2 SD DISJ. QF7019 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3037 | 15 | 13095 | 14 | 16416 | 1613 | 6 | EL6021_M178 |  | BITVAL
EQF6020F | TGBT ZLV DEPART ONDULEUR UL7003 CAT.IIIB-1 OF DISJ. QF7020 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 0 | 13096 | 0 | 16416 | 1614 | 0 | EL6021_M178 |  | BITVAL
EQF6020D | TGBT ZLV DEPART ONDULEUR UL7003 CAT.IIIB-1 SD DISJ. QF7020 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 1 | 13096 | 2 | 16416 | 1614 | 2 | EL6021_M178 |  | BITVAL
EQF6021F | TGBT ZLV DEPART BYPASS UL7003/7004 CAT.IIIB OF DISJ. QF7021 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 2 | 13096 | 4 | 16416 | 1614 | 4 | EL6021_M178 |  | BITVAL
EQF6021D | TGBT ZLV DEPART BYPASS UL7003/7004 CAT.IIIB SD DISJ. QF7021 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 3 | 13096 | 6 | 16416 | 1614 | 6 | EL6021_M178 |  | BITVAL
EQF6022F | TGBT ZLV DEPART ONDULEUR UL7004 CAT.IIIB-2 OF DISJ. QF7022 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 4 | 13096 | 8 | 16416 | 1615 | 0 | EL6021_M178 |  | BITVAL
EQF6022D | TGBT ZLV DEPART ONDULEUR UL7004 CAT.IIIB-2 SD DISJ. QF7022 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 5 | 13096 | 10 | 16416 | 1615 | 2 | EL6021_M178 |  | BITVAL
EQF6023F | TGBT ZLV DEPART ONDULEUR UL7005 CAT.III CUB OF DISJ. QF7023 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 6 | 13096 | 12 | 16416 | 1615 | 4 | EL6021_M178 |  | BITVAL
EQF6023D | TGBT ZLV DEPART ONDULEUR UL7005 CAT.III CUB SD DISJ. QF7023 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 7 | 13096 | 14 | 16416 | 1615 | 6 | EL6021_M178 |  | BITVAL
EQF6024F | TGBT ZLV DEPART BYPASS 50HZ/60HZ CAT.III CUB OF DISJ. QF7024 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 8 | 13097 | 0 | 16416 | 1616 | 0 | EL6021_M178 |  | BITVAL
EQF6024D | TGBT ZLV DEPART BYPASS 50HZ/60HZ CAT.III CUB SD DISJ. QF7024 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 9 | 13097 | 2 | 16416 | 1616 | 2 | EL6021_M178 |  | BITVAL
EQF6025F | TGBT ZLV DEPART CONVERTISSEUR 60HZ CLIENT OF DISJ. QF7025 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 10 | 13097 | 4 | 16416 | 1616 | 4 | EL6021_M178 |  | BITVAL
EQF6025D | TGBT ZLV DEPART CONVERTISSEUR 60HZ CLIENT SD DISJ. QF7025 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 11 | 13097 | 6 | 16416 | 1616 | 6 | EL6021_M178 |  | BITVAL
EQF6026F | TGBT ZLV DEPART ONDULEUR UL7006 CAT.III CUH OF DISJ. QF7026 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 12 | 13097 | 8 | 16416 | 1617 | 0 | EL6021_M178 |  | BITVAL
EQF6026D | TGBT ZLV DEPART ONDULEUR UL7006 CAT.III CUH SD DISJ. QF7026 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 13 | 13097 | 10 | 16416 | 1617 | 2 | EL6021_M178 |  | BITVAL
EQF6027F | TGBT ZLV DEPART BYPASS 50HZ/60HZ CAT.III CUH OF DISJ. QF7027 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 14 | 13097 | 12 | 16416 | 1617 | 4 | EL6021_M178 |  | BITVAL
EQF6027D | TGBT ZLV DEPART BYPASS 50HZ/60HZ CAT.III CUH SD DISJ. QF7027 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3038 | 15 | 13097 | 14 | 16416 | 1617 | 6 | EL6021_M178 |  | BITVAL
EQF6030F | TGBT ZLV DEPART CAPA. CO7001 OF DISJ. QF7030 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 0 | 13098 | 0 | 16416 | 1618 | 0 | EL6021_M178 |  | BITVAL
EQF6030D | TGBT ZLV DEPART CAPA. CO7001 SD DISJ. QF7030 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 1 | 13098 | 2 | 16416 | 1618 | 2 | EL6021_M178 |  | BITVAL
EQF6031F | TGBT ZLV DEPART TD CUVE 175 M3 OF DISJ. QF7031 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 2 | 13098 | 4 | 16416 | 1618 | 4 | EL6021_M178 |  | BITVAL
EQF6031D | TGBT ZLV DEPART TD CUVE 175 M3 SD DISJ. QF7031 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 3 | 13098 | 6 | 16416 | 1618 | 6 | EL6021_M178 |  | BITVAL
EQF6032F | TGBT ZLV DEPART CUVE UDMH OF DISJ. QF7032 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 4 | 13098 | 8 | 16416 | 1619 | 0 | EL6021_M178 |  | BITVAL
EQF6032D | TGBT ZLV DEPART CUVE UDMH SD DISJ. QF7032 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 5 | 13098 | 10 | 16416 | 1619 | 2 | EL6021_M178 |  | BITVAL
EQF6033F | TGBT ZLV DEPART CUVE N2O4 OF DISJ. QF7033 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 6 | 13098 | 12 | 16416 | 1619 | 4 | EL6021_M178 |  | BITVAL
EQF6033D | TGBT ZLV DEPART CUVE N2O4 SD DISJ. QF7033 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3039 | 7 | 13098 | 14 | 16416 | 1619 | 6 | EL6021_M178 |  | BITVAL
SPASCR0144 | SPARE SER 0144 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3039 | 8 | 13099 | 0 | 16416 | 1620 | 0 | EL6021_M178 |  | BITVAL
EQF6001O | TGBT ZLV ARRIVEE TM 7002 CAT.II OF DISJ. QF7001 OPEN | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energy TGBT et UPS (E) |  | 4 |  |  | 3039 | 9 | 13099 | 2 | 16416 | 1620 | 2 | EL6021_M178 |  | BITVAL
EQF6002O | TGBT ZLV ARRIVEE TM 7004 CAT.I OF DISJ. QF7002 OPEN | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energy TGBT et UPS (E) |  | 4 |  |  | 3039 | 10 | 13099 | 4 | 16416 | 1620 | 4 | EL6021_M178 |  | BITVAL
EQF6950O | TGBT-C ZLV ARRIVEE TM 7001 CAT.II SD DISJ. QF7950 OPEN | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energy TGBT et UPS (E) |  | 4 |  |  | 3039 | 11 | 13099 | 6 | 16416 | 1620 | 6 | EL6021_M178 |  | BITVAL
EQF6951O | TGBT-C ZLV ARRIVEE TM 7003 CAT.I SD DISJ. QF7951 OPEN | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energy TGBT et UPS (E) |  | 4 |  |  | 3039 | 12 | 13099 | 8 | 16416 | 1621 | 0 | EL6021_M178 |  | BITVAL
EQF6003O | TGBT ZLV ARRIVEE GEN SET XS-7001 OF DISJ. QF7003 OPEN | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energy TGBT et UPS (E) |  | 4 |  |  | 3039 | 13 | 13099 | 10 | 16416 | 1621 | 2 | EL6021_M178 |  | BITVAL
EQF6952O | TGBT-C ZLV ARRIVEE GEN SET XS-7002 OF DISJ. QF7952 OPEN | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energy TGBT et UPS (E) |  | 4 |  |  | 3039 | 14 | 13099 | 12 | 16416 | 1621 | 4 | EL6021_M178 |  | BITVAL
SPASCR0151 | SPARE SER 0151 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3039 | 15 | 13099 | 14 | 16416 | 1621 | 6 | EL6021_M178 |  | BITVAL
EQF6954F | TGBT-C ZLV DEPART GENERATEUR FROID NO 3 OF DISJ. QF7954 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 0 | 13100 | 0 | 16416 | 1622 | 0 | EL6021_M178 |  | BITVAL
EQF6954D | TGBT-C ZLV DEPART GENERATEUR FROID NO 3 SD DISJ. QF7954 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 1 | 13100 | 2 | 16416 | 1622 | 2 | EL6021_M178 |  | BITVAL
EQF6955F | TGBT-C ZLV DEPART GENERATEUR FROID NO 2 OF DISJ. QF7955 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 2 | 13100 | 4 | 16416 | 1622 | 4 | EL6021_M178 |  | BITVAL
EQF6955D | TGBT-C ZLV DEPART GENERATEUR FROID NO 2 SD DISJ. QF7955 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 3 | 13100 | 6 | 16416 | 1622 | 6 | EL6021_M178 |  | BITVAL
EQF6956F | TGBT-C ZLV DEPART GENERATEUR FROID NO 1 OF DISJ. QF7956 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 4 | 13100 | 8 | 16416 | 1623 | 0 | EL6021_M178 |  | BITVAL
EQF6956D | TGBT-C ZLV DEPART GENERATEUR FROID NO 1 SD DISJ. QF7956 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 5 | 13100 | 10 | 16416 | 1623 | 2 | EL6021_M178 |  | BITVAL
EQF6957F | TGBT-C ZLV DEPART PREHEATING GENERATOR SET SYSTEM OF DISJ. QF7957 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 6 | 13100 | 12 | 16416 | 1623 | 4 | EL6021_M178 |  | BITVAL
EQF6957D | TGBT-C ZLV DEPART PREHEATING GENERATOR SET SYSTEM SD DISJ. QF7957 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 7 | 13100 | 14 | 16416 | 1623 | 6 | EL6021_M178 |  | BITVAL
EQF6958F | TGBT-C ZLV DEPART CAPA. CO7002 OF DISJ. QF7958 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 8 | 13101 | 0 | 16416 | 1624 | 0 | EL6021_M178 |  | BITVAL
EQF6958D | TGBT-C ZLV DEPART CAPA. CO7002 SD DISJ. QF7958 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 9 | 13101 | 2 | 16416 | 1624 | 2 | EL6021_M178 |  | BITVAL
EQF6963F | TGBT-C ZLV DEPART TD AUX CLIM LOCAL 126 SECT.1 OF DISJ. QF7963 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 10 | 13101 | 4 | 16416 | 1624 | 4 | EL6021_M178 |  | BITVAL
EQF6963D | TGBT-C ZLV DEPART TD AUX CLIM LOCAL 126 SECT.1 SD DISJ. QF7963 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 11 | 13101 | 6 | 16416 | 1624 | 6 | EL6021_M178 |  | BITVAL
EQF6964F | TGBT-C ZLV DEPART TD AUX CLIM LOCAL 126 SECT.3 OF DISJ. QF7964 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 12 | 13101 | 8 | 16416 | 1625 | 0 | EL6021_M178 |  | BITVAL
EQF6964D | TGBT-C ZLV DEPART TD AUX CLIM LOCAL 126 SECT.3 SD DISJ. QF7964 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3040 | 13 | 13101 | 10 | 16416 | 1625 | 2 | EL6021_M178 |  | BITVAL
SPASCR0152 | SPARE SER 0152 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3040 | 14 | 13101 | 12 | 16416 | 1625 | 4 | EL6021_M178 |  | BITVAL
SPASCR0153 | SPARE SER 0153 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3040 | 15 | 13101 | 14 | 16416 | 1625 | 6 | EL6021_M178 |  | BITVAL
EQF6912F | TGBT-C ZLV SPARE OF DISJ. Q1-12 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 0 | 13102 | 0 | 16416 | 1626 | 0 | EL6021_M178 |  | BITVAL
EQF6912D | TGBT-C ZLV SPARE SD DISJ. Q1-12 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 1 | 13102 | 2 | 16416 | 1626 | 2 | EL6021_M178 |  | BITVAL
EQF6924F | TGBT-C ZLV SPARE OF DISJ. Q1-24 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 2 | 13102 | 4 | 16416 | 1626 | 4 | EL6021_M178 |  | BITVAL
EQF6924D | TGBT-C ZLV SPARE SD DISJ. Q1-24 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 3 | 13102 | 6 | 16416 | 1626 | 6 | EL6021_M178 |  | BITVAL
EQF6959F | TGBT-C ZLV OF DISJ. QF7959 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 4 | 13102 | 8 | 16416 | 1627 | 0 | EL6021_M178 |  | BITVAL
EQF6959D | TGBT-C ZLV SD DISJ. QF7959 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 5 | 13102 | 10 | 16416 | 1627 | 2 | EL6021_M178 |  | BITVAL
EQF6960F | TGBT-C ZLV OF DISJ. QF7960 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 6 | 13102 | 12 | 16416 | 1627 | 4 | EL6021_M178 |  | BITVAL
EQF6960D | TGBT-C ZLV SD DISJ. QF7960 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 7 | 13102 | 14 | 16416 | 1627 | 6 | EL6021_M178 |  | BITVAL
EQF6961F | TGBT-C ZLV TM 7001 CAT.II POWER SUPPLY OF DISJ. QF7961 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 8 | 13103 | 0 | 16416 | 1628 | 0 | EL6021_M178 |  | BITVAL
EQF6961D | TGBT-C ZLV TM 7001 CAT.II POWER SUPPLY SD DISJ. QF7961 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 9 | 13103 | 2 | 16416 | 1628 | 2 | EL6021_M178 |  | BITVAL
EQF6962F | TGBT-C ZLV TM 7003 CAT.I POWER SUPPLY OF DISJ. QF7962 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 10 | 13103 | 4 | 16416 | 1628 | 4 | EL6021_M178 |  | BITVAL
EQF6962D | TGBT-C ZLV TM 7003 CAT.I POWER SUPPLY SD DISJ. QF7962 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3041 | 11 | 13103 | 6 | 16416 | 1628 | 6 | EL6021_M178 |  | BITVAL
SPASCR0154 | SPARE SER 0154 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3041 | 12 | 13103 | 8 | 16416 | 1629 | 0 | EL6021_M178 |  | BITVAL
SPASCR0155 | SPARE SER 0155 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3041 | 13 | 13103 | 10 | 16416 | 1629 | 2 | EL6021_M178 |  | BITVAL
SPASCR0156 | SPARE SER 0156 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3041 | 14 | 13103 | 12 | 16416 | 1629 | 4 | EL6021_M178 |  | BITVAL
EQF6028F | TGBT ZLV DEPART COUPURE URGENCE CAT.III OF DISJ. QF7028 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3041 | 15 | 13103 | 14 | 16416 | 1629 | 6 | EL6021_M178 |  | BITVAL
EQF6028D | TGBT ZLV DEPART COUPURE URGENCE CAT.III SD DISJ. QF7028 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 0 | 13104 | 0 | 16416 | 1630 | 0 | EL6021_M178 |  | BITVAL
EQF6029F | TGBT ZLV DEPART PRECHAUFFAGE XS7001 OF DISJ. QF7029 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 1 | 13104 | 2 | 16416 | 1630 | 2 | EL6021_M178 |  | BITVAL
EQF6029D | TGBT ZLV DEPART PRECHAUFFAGE XS7001 SD DISJ. QF7029 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 2 | 13104 | 4 | 16416 | 1630 | 4 | EL6021_M178 |  | BITVAL
EQF6034F | TGBT ZLV DEPART TD SURPRESSEUR OF DISJ. QF7044 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 3 | 13104 | 6 | 16416 | 1630 | 6 | EL6021_M178 |  | BITVAL
EQF6034D | TGBT ZLV DEPART TD SURPRESSEUR SD DISJ. QF7044 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 4 | 13104 | 8 | 16416 | 1631 | 0 | EL6021_M178 |  | BITVAL
EQF6035F | TGBT ZLV DEPART HPB1 OF DISJ. QF7043 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3042 | 5 | 13104 | 10 | 16416 | 1631 | 2 | EL6021_M178 |  | BITVAL
EQF6035D | TGBT ZLV DEPART HPB1 SD DISJ. QF7043 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3042 | 6 | 13104 | 12 | 16416 | 1631 | 4 | EL6021_M178 |  | BITVAL
EQF6036F | TGBT ZLV DEPART AUTOMATE PLC OF DISJ. QF7036 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 7 | 13104 | 14 | 16416 | 1631 | 6 | EL6021_M178 |  | BITVAL
EQF6036D | TGBT ZLV DEPART AUTOMATE PLC SD DISJ. QF7036 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 8 | 13105 | 0 | 16416 | 1632 | 0 | EL6021_M178 |  | BITVAL
EQF6037F | TGBT ZLV DEPART MB103 TM7002 OF DISJ. QF7037 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 9 | 13105 | 2 | 16416 | 1632 | 2 | EL6021_M178 |  | BITVAL
EQF6037D | TGBT ZLV DEPART MB103 TM7002 SD DISJ. QF7037 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 10 | 13105 | 4 | 16416 | 1632 | 4 | EL6021_M178 |  | BITVAL
EQF6038F | TGBT ZLV DEPART MB103 TM7004 OF DISJ. QF7038 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 11 | 13105 | 6 | 16416 | 1632 | 6 | EL6021_M178 |  | BITVAL
EQF6038D | TGBT ZLV DEPART MB103 TM7004 SD DISJ. QF7038 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 12 | 13105 | 8 | 16416 | 1633 | 0 | EL6021_M178 |  | BITVAL
EQF6436F | TGBT ZLV HPS P80 OF DISJ. QF7035 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 13 | 13105 | 10 | 16416 | 1633 | 2 | EL6021_M178 |  | BITVAL
EQF6436D | TGBT ZLV HPS P80 SD DISJ. QF7035 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 14 | 13105 | 12 | 16416 | 1633 | 4 | EL6021_M178 |  | BITVAL
EQF6444F | TGBT ZLV SPARE CIRCUIT BREAKER 2 OF DISJ. Q4-44 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3042 | 15 | 13105 | 14 | 16416 | 1633 | 6 | EL6021_M178 |  | BITVAL
EQF6444D | TGBT ZLV SPARE CIRCUIT BREAKER 2 SD DISJ. Q4-44 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3043 | 0 | 13106 | 0 | 16416 | 1634 | 0 | EL6021_M178 |  | BITVAL
EQF6452F | TGBT ZLV PC PFRCS OF DISJ. QF7034 CLOSE | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3043 | 1 | 13106 | 2 | 16416 | 1634 | 2 | EL6021_M178 |  | BITVAL
EQF6452D | TGBT ZLV PC PFRCS SD DISJ. QF7034 FAULT | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | Departs supplementaires TGBT ZLV (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3043 | 2 | 13106 | 4 | 16416 | 1634 | 4 | EL6021_M178 |  | BITVAL
SPASCR0157 | SPARE SER 0157 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 3 | 13106 | 6 | 16416 | 1634 | 6 | EL6021_M178 |  | BITVAL
SPASCR0158 | SPARE SER 0158 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 4 | 13106 | 8 | 16416 | 1635 | 0 | EL6021_M178 |  | BITVAL
SPASCR0159 | SPARE SER 0159 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 5 | 13106 | 10 | 16416 | 1635 | 2 | EL6021_M178 |  | BITVAL
SPASCR0160 | SPARE SER 0160 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 6 | 13106 | 12 | 16416 | 1635 | 4 | EL6021_M178 |  | BITVAL
SPASCR0161 | SPARE SER 0161 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 7 | 13106 | 14 | 16416 | 1635 | 6 | EL6021_M178 |  | BITVAL
SPASCR0162 | SPARE SER 0162 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 8 | 13107 | 0 | 16416 | 1636 | 0 | EL6021_M178 |  | BITVAL
SPASCR0163 | SPARE SER 0163 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 9 | 13107 | 2 | 16416 | 1636 | 2 | EL6021_M178 |  | BITVAL
SPASCR0164 | SPARE SER 0164 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 10 | 13107 | 4 | 16416 | 1636 | 4 | EL6021_M178 |  | BITVAL
SPASCR0165 | SPARE SER 0165 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3043 | 11 | 13107 | 6 | 16416 | 1636 | 6 | EL6021_M178 |  | BITVAL
ESA6500 | TGBT CAT.IIIA to TGBT ZLV SYNTHESE OF 1601-113-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3043 | 12 | 13107 | 8 | 16416 | 1637 | 0 | EL6021_M178 |  | BITVAL
ESA6700 | TGBT CAT.IIIB to TGBT ZLV SYNTHESE OF 1601-113-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3043 | 13 | 13107 | 10 | 16416 | 1637 | 2 | EL6021_M178 |  | BITVAL
ESA6535 | TD1 004 IIIA to TGBT ZLV SYNTHESE OF 1601-004-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3043 | 14 | 13107 | 12 | 16416 | 1637 | 4 | EL6021_M178 |  | BITVAL
ESA6550 | TD2 004 IIIA to TGBT ZLV SYNTHESE OF 1601-004-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3043 | 15 | 13107 | 14 | 16416 | 1637 | 6 | EL6021_M178 |  | BITVAL
ESA6735 | TD1 004 IIIB to TGBT ZLV SYNTHESE OF 1601-004-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 0 | 13108 | 0 | 16416 | 1638 | 0 | EL6021_M178 |  | BITVAL
ESA6750 | TD2 004 IIIB to TGBT ZLV SYNTHESE OF 1601-004-34 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 1 | 13108 | 2 | 16416 | 1638 | 2 | EL6021_M178 |  | BITVAL
ESA6520 | TD 013 IIIA to TGBT ZLV SYNTHESE OF 1601-013-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 2 | 13108 | 4 | 16416 | 1638 | 4 | EL6021_M178 |  | BITVAL
ESA6720 | TD 013 IIIB to TGBT ZLV SYNTHESE OF 1601-013-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 3 | 13108 | 6 | 16416 | 1638 | 6 | EL6021_M178 |  | BITVAL
ESA6565 | TD1 103 IIIA to TGBT ZLV SYNTHESE OF 1601-103-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 4 | 13108 | 8 | 16416 | 1639 | 0 | EL6021_M178 |  | BITVAL
ESA6580 | TD2 103 IIIA to TGBT ZLV SYNTHESE OF 1601-103-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 5 | 13108 | 10 | 16416 | 1639 | 2 | EL6021_M178 |  | BITVAL
ESA6595 | TD3 103 IIIA to TGBT ZLV SYNTHESE OF 1601-103-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 6 | 13108 | 12 | 16416 | 1639 | 4 | EL6021_M178 |  | BITVAL
ESA6610 | TD4 103 IIIA to TGBT ZLV SYNTHESE OF 1601-103-33 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 7 | 13108 | 14 | 16416 | 1639 | 6 | EL6021_M178 |  | BITVAL
ESA6665 | TD1 103 IIIB to TGBT ZLV SYNTHESE OF 1601-103-34 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 8 | 13109 | 0 | 16416 | 1640 | 0 | EL6021_M178 |  | BITVAL
ESA6780 | TD2 103 IIIB to TGBT ZLV SYNTHESE OF 1601-103-35 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 9 | 13109 | 2 | 16416 | 1640 | 2 | EL6021_M178 |  | BITVAL
ESA6795 | TD3 103 IIIB to TGBT ZLV SYNTHESE OF 1601-103-36 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 10 | 13109 | 4 | 16416 | 1640 | 4 | EL6021_M178 |  | BITVAL
ESA6810 | TD4 103 IIIB to TGBT ZLV SYNTHESE OF 1601-103-37 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 11 | 13109 | 6 | 16416 | 1640 | 6 | EL6021_M178 |  | BITVAL
ESA6900 | TD III CUB to TGBT ZLV SYNTHESE OF 1601-101-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 14 | 13109 | 12 | 16416 | 1641 | 4 | EL6021_M178 |  | BITVAL
ESA6915 | TD III CUH to TGBT ZLV LEVEL 21.2m SYNTHESE OF 1607-34000-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3044 | 15 | 13109 | 14 | 16416 | 1641 | 6 | EL6021_M178 |  | BITVAL
ESA6001 | T AUX UPS IIIA to TGBT ZLV POSITION QM7001 1602-113-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energie TGBT et UPS VEGA (E); Energy TD |  | 4 |  |  | 3045 | 0 | 13110 | 0 | 16416 | 1642 | 0 | EL6021_M178 |  | BITVAL
ESA6002 | T AUX UPS IIIA to TGBT ZLV POSITION QM7002 1602-113-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energy TD |  | 4 |  |  | 3045 | 1 | 13110 | 2 | 16416 | 1642 | 2 | EL6021_M178 |  | BITVAL
ESA6003 | T AUX UPS IIIB to TGBT ZLV POSITION QM7003 1602-113-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energy TD |  | 4 |  |  | 3045 | 2 | 13110 | 4 | 16416 | 1642 | 4 | EL6021_M178 |  | BITVAL
ESA6004 | T AUX UPS IIIB to TGBT ZLV POSITION QM7004 1602-113-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energy TD |  | 4 |  |  | 3045 | 3 | 13110 | 6 | 16416 | 1642 | 6 | EL6021_M178 |  | BITVAL
ESA6007 | T AUX UPS IIIA to TGBT ZLV BYPASS EXTERNE UL1 & 2 QM7007 1602-113-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energy TD |  | 4 |  |  | 3045 | 4 | 13110 | 8 | 16416 | 1643 | 0 | EL6021_M178 |  | BITVAL
ESA6008 | T AUX UPS IIIB to TGBT ZLV BYPASS EXTERNE UL3 & 4 QM7008 1602-113-32 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E63 | Energy TD |  | 4 |  |  | 3045 | 5 | 13110 | 10 | 16416 | 1643 | 2 | EL6021_M178 |  | BITVAL
ESA6005F | T AUX 1 UPS CUB CUH to TGBT ZLV POSITION : QM7005 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3045 | 6 | 13110 | 12 | 16416 | 1643 | 4 | EL6021_M178 |  | BITVAL
ESA6005O | T AUX 1 UPS CUB CUH to TGBT ZLV POSITION : QM7005 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3045 | 7 | 13110 | 14 | 16416 | 1643 | 6 | EL6021_M178 |  | BITVAL
ESA6006F | T AUX 1 UPS CUB CUH to TGBT ZLV POSITION : QM7006 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3045 | 8 | 13111 | 0 | 16416 | 1644 | 0 | EL6021_M178 |  | BITVAL
ESA6006O | T AUX 1 UPS CUB CUH to TGBT ZLV POSITION : QM7006 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3045 | 9 | 13111 | 2 | 16416 | 1644 | 2 | EL6021_M178 |  | BITVAL
ESA6009F | T AUX 1 UPS CUB CUH to TGBT ZLV SWITCH SA7009 IN POSITION 1 (50HZ) BYPASS EUL7005 OF1 : QM7009 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E65 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3045 | 10 | 13111 | 4 | 16416 | 1644 | 4 | EL6021_M178 |  | BITVAL
ESA6009O | T AUX 1 UPS CUB CUH to TGBT ZLV SWITCH SA7009 IN POSITION 2 (60HZ) BYPASS EUL7005 OF2 : QM7009 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E65 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3045 | 11 | 13111 | 6 | 16416 | 1644 | 6 | EL6021_M178 |  | BITVAL
ESA6010F | T AUX 1 UPS CUB CUH to TGBT ZLV SWITCH SA7010 IN POSITION 1 (60HZ) BYPASS EUL7006 OF1 : QM7010 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E65 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3045 | 12 | 13111 | 8 | 16416 | 1645 | 0 | EL6021_M178 |  | BITVAL
ESA6010O | T AUX 1 UPS CUB CUH to TGBT ZLV SWITCH SA7010 IN POSITION 2 (50HZ) BYPASS EUL7006 OF2 : QM7010 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E65 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3045 | 13 | 13111 | 10 | 16416 | 1645 | 2 | EL6021_M178 |  | BITVAL
ESA6011 | T AUX 1 UPS CUB CUH to TGBT ZLV BYPASS EXTERNE UL5 QM7011 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3045 | 14 | 13111 | 12 | 16416 | 1645 | 4 | EL6021_M178 |  | BITVAL
ESA6012 | T AUX 1 UPS CUB CUH to TGBT ZLV BYPASS EXTERNE UL6 QM7012 | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3045 | 15 | 13111 | 14 | 16416 | 1645 | 6 | EL6021_M178 |  | BITVAL
EQF6220F | T AUX 1 UPS CUB CUH to TGBT ZLV OF DISJ. QF7020 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3046 | 0 | 13112 | 0 | 16416 | 1646 | 0 | EL6021_M178 |  | BITVAL
EQF6221F | T AUX 1 UPS CUB CUH to TGBT ZLV OF DISJ. QF7021 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3046 | 1 | 13112 | 2 | 16416 | 1646 | 2 | EL6021_M178 |  | BITVAL
EQF6230F | T AUX 2 UPS CUB CUH to TGBT ZLV OF DISJ. QF7030 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3046 | 2 | 13112 | 4 | 16416 | 1646 | 4 | EL6021_M178 |  | BITVAL
ESA6030O | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7030 IN POSITION 2 OF1 : QM7030 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 3 | 13112 | 6 | 16416 | 1646 | 6 | EL6021_M178 |  | BITVAL
ESA6030F | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7030 IN POSITION 1 OF2 : QM7030 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 4 | 13112 | 8 | 16416 | 1647 | 0 | EL6021_M178 |  | BITVAL
EQF6232F | T AUX 2 UPS CUB CUH to TGBT ZLV OF DISJ. QF7032 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD |  | 4 |  |  | 3046 | 5 | 13112 | 10 | 16416 | 1647 | 2 | EL6021_M178 |  | BITVAL
ESA6032O | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7032 IN POSITION 2 OF1 : QM7032 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 6 | 13112 | 12 | 16416 | 1647 | 4 | EL6021_M178 |  | BITVAL
ESA6032F | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7032 IN POSITION 1 OF2 : QM7032 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 7 | 13112 | 14 | 16416 | 1647 | 6 | EL6021_M178 |  | BITVAL
ESA6031O | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7031 IN POSITION 2 OF1 : QM7031 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 8 | 13113 | 0 | 16416 | 1648 | 0 | EL6021_M178 |  | BITVAL
ESA6031F | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7031 IN POSITION 1 OF2 : QM7031 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 9 | 13113 | 2 | 16416 | 1648 | 2 | EL6021_M178 |  | BITVAL
ESA6033O | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7033 IN POSITION 2 OF1 : QM7033 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 10 | 13113 | 4 | 16416 | 1648 | 4 | EL6021_M178 |  | BITVAL
ESA6033F | T AUX 2 UPS CUB CUH to TGBT ZLV SWITCH SA7033 IN POSITION 1 OF2 : QM7033 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3046 | 11 | 13113 | 6 | 16416 | 1648 | 6 | EL6021_M178 |  | BITVAL
SPASCR0166 | SPARE SER 0166 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3046 | 12 | 13113 | 8 | 16416 | 1649 | 0 | EL6021_M178 |  | BITVAL
SPASCR0167 | SPARE SER 0167 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3046 | 13 | 13113 | 10 | 16416 | 1649 | 2 | EL6021_M178 |  | BITVAL
SPASCR0168 | SPARE SER 0168 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3046 | 14 | 13113 | 12 | 16416 | 1649 | 4 | EL6021_M178 |  | BITVAL
SPASCR0169 | SPARE SER 0169 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3046 | 15 | 13113 | 14 | 16416 | 1649 | 6 | EL6021_M178 |  | BITVAL
ESA6630 | TDGA IIIA to TGBT ZLV SYNTHESE OF 1602-101-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 0 | 13114 | 0 | 16416 | 1650 | 0 | EL6021_M178 |  | BITVAL
ESA6830 | TDGA IIIB to TGBT ZLV SYNTHESE OF 1602-101-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 1 | 13114 | 2 | 16416 | 1650 | 2 | EL6021_M178 |  | BITVAL
ESA6640 | TD1 21200 IIIA to TGBT ZLV SYNTHESE OF 1602-201-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 2 | 13114 | 4 | 16416 | 1650 | 4 | EL6021_M178 |  | BITVAL
ESA6840 | TD1 21200 IIIB to TGBT ZLV SYNTHESE OF 1602-201-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 3 | 13114 | 6 | 16416 | 1650 | 6 | EL6021_M178 |  | BITVAL
ESA6655 | TD1 29200 IIIA to TGBT ZLV SYNTHESE OF 1602-501-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 4 | 13114 | 8 | 16416 | 1651 | 0 | EL6021_M178 |  | BITVAL
ESA6670 | TD2 29200 IIIA to TGBT ZLV SYNTHESE OF 1602-502-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 5 | 13114 | 10 | 16416 | 1651 | 2 | EL6021_M178 |  | BITVAL
ESA6855 | TD1 29200 IIIB to TGBT ZLV SYNTHESE OF 1602-501-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 6 | 13114 | 12 | 16416 | 1651 | 4 | EL6021_M178 |  | BITVAL
ESA6870 | TD2 29200 IIIB to TGBT ZLV SYNTHESE OF 1602-502-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70;E67 | Energy TD |  | 4 |  |  | 3047 | 7 | 13114 | 14 | 16416 | 1651 | 6 | EL6021_M178 |  | BITVAL
ESA6160 | TD LOCAL 117 to TGBT ZLV SYNTHESE OF 1601-117-20 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD (E) |  | 4 |  |  | 3047 | 12 | 13115 | 8 | 16416 | 1653 | 0 | EL6021_M178 |  | BITVAL
ESA6625 | TD1 002 IIIA to TGBT ZLV SYNTHESE OF 1601-002-30 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD (E) |  | 4 |  |  | 3047 | 13 | 13115 | 10 | 16416 | 1653 | 2 | EL6021_M178 |  | BITVAL
ESA6920 | TD1 002 IIIB to TGBT ZLV SYNTHESE OF 1601-002-31 | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E70 | Energy TD (E) |  | 4 |  |  | 3047 | 14 | 13115 | 12 | 16416 | 1653 | 4 | EL6021_M178 |  | BITVAL
SPASCR0170 | SPARE SER 0170 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3047 | 15 | 13115 | 14 | 16416 | 1653 | 6 | EL6021_M178 |  | BITVAL
EUL6071M | Onduleur IIIA-1 UL7001 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6071D1 | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 0 | 13116 | 0 | 16416 | 1654 | 0 | EL6021_M178 |  | BITVAL
EKM6071F | Onduleur IIIA-1 UL7001 Operation on static switch | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3048 | 1 | 13116 | 2 | 16416 | 1654 | 2 | EL6021_M178 |  | BITVAL
EUL6072M | Onduleur IIIA-2 UL7002 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6072D1 | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 2 | 13116 | 4 | 16416 | 1654 | 4 | EL6021_M178 |  | BITVAL
EKM6072F | Onduleur IIIA-2 UL7002 Operation on static switch | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3048 | 3 | 13116 | 6 | 16416 | 1654 | 6 | EL6021_M178 |  | BITVAL
EUL6073M | Onduleur IIIB-1 UL7003 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6073D1 | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 4 | 13116 | 8 | 16416 | 1655 | 0 | EL6021_M178 |  | BITVAL
EKM6073F | Onduleur IIIB-1 UL7003 Operation on static switch | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3048 | 5 | 13116 | 10 | 16416 | 1655 | 2 | EL6021_M178 |  | BITVAL
EUL6074M | Onduleur IIIB-2 UL7004 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6074D1 | E63 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 6 | 13116 | 12 | 16416 | 1655 | 4 | EL6021_M178 |  | BITVAL
EKM6074F | Onduleur IIIB-2 UL7004 Operation on static switch | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3048 | 7 | 13116 | 14 | 16416 | 1655 | 6 | EL6021_M178 |  | BITVAL
EUL6075M | Onduleur III CUB UL7005 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6075D1 | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 8 | 13117 | 0 | 16416 | 1656 | 0 | EL6021_M178 |  | BITVAL
EKM6075F | Onduleur III CUB UL7005 Operation on static switch | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3048 | 9 | 13117 | 2 | 16416 | 1656 | 2 | EL6021_M178 |  | BITVAL
EUL6076M | Onduleur III CUH UL7006 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6076D1 | E64 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 10 | 13117 | 4 | 16416 | 1656 | 4 | EL6021_M178 |  | BITVAL
EKM6076F | Onduleur III CUH UL7006 Operation on static switch | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3048 | 11 | 13117 | 6 | 16416 | 1656 | 6 | EL6021_M178 |  | BITVAL
EUL6077M | Frequency Converter UL7007 UPS coupled | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 | ESY6077D1 | E65 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3048 | 12 | 13117 | 8 | 16416 | 1657 | 0 | EL6021_M178 |  | BITVAL
SPASCR0171 | SPARE SER 0171 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3048 | 13 | 13117 | 10 | 16416 | 1657 | 2 | EL6021_M178 |  | BITVAL
SPASCR0172 | SPARE SER 0172 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3048 | 14 | 13117 | 12 | 16416 | 1657 | 4 | EL6021_M178 |  | BITVAL
SPASCR0173 | SPARE SER 0173 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 4 |  |  | 3048 | 15 | 13117 | 14 | 16416 | 1657 | 6 | EL6021_M178 |  | BITVAL
ESA6000 | TGBT ZLV LOCAL - REMOTE SELECTOR | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E61 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3049 | 0 | 13118 | 0 | 16416 | 1658 | 0 | EL6021_M178 |  | BITVAL
ESA6950 | TGBT-C ZLV LOCAL - REMOTE SELECTOR | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E62 | Energie TGBT et UPS VEGA (E) |  | 4 |  |  | 3049 | 1 | 13118 | 2 | 16416 | 1658 | 2 | EL6021_M178 |  | BITVAL
VFN6002S1 | Desenfumage 002 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 0 | 13120 | 0 | 16416 | 1662 | 0 | EL6021_M178 |  | BITVAL
SZI7017W | Alarme Feu Lagrange Battery room 0014 ZDA14 Z2 - ZONE 17 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1036 | 2 | [7 empty] | BITVAL
VFN6002S3 | Desenfumage 002 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 2 | 13120 | 4 | 16416 | 1662 | 4 | EL6021_M178 |  | BITVAL
VFN6002S4 | Desenfumage 002 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 3 | 13120 | 6 | 16416 | 1662 | 6 | EL6021_M178 |  | BITVAL
VFN6004S1 | Desenfumage 004 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 4 | 13120 | 8 | 16416 | 1663 | 0 | EL6021_M178 |  | BITVAL
SZI7018W | Alarme Feu Lagrange Local clim RDC 0020 ZDA15 - ZONE 18 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1036 | 6 | [7 empty] | BITVAL
VFN6004S3 | Desenfumage 004 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 6 | 13120 | 12 | 16416 | 1663 | 4 | EL6021_M178 |  | BITVAL
VFN6004S4 | Desenfumage 004 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 7 | 13120 | 14 | 16416 | 1663 | 6 | EL6021_M178 |  | BITVAL
VFN6007S1 | Desenfumage 007 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 8 | 13121 | 0 | 16416 | 1664 | 0 | EL6021_M178 |  | BITVAL
SZI7019W | Alarme Feu Lagrange Local de repos 0025 ZDA16 - ZONE 19 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1036 | 10 | [7 empty] | BITVAL
VFN6007S3 | Desenfumage 007 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 10 | 13121 | 4 | 16416 | 1664 | 4 | EL6021_M178 |  | BITVAL
VFN6007S4 | Desenfumage 007 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 11 | 13121 | 6 | 16416 | 1664 | 6 | EL6021_M178 |  | BITVAL
VFN6008S1 | Desenfumage 008 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 12 | 13121 | 8 | 16416 | 1665 | 0 | EL6021_M178 |  | BITVAL
SZI7020W | Alarme Feu Lagrange Local imprimerie 0048 ZDA17 - ZONE 20 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1036 | 14 | [7 empty] | BITVAL
VFN6008S3 | Desenfumage 008 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 14 | 13121 | 12 | 16416 | 1665 | 4 | EL6021_M178 |  | BITVAL
VFN6008S4 | Desenfumage 008 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 15 | 13121 | 14 | 16416 | 1665 | 6 | EL6021_M178 |  | BITVAL
VFN6009S1 | Desenfumage 009 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 0 | 13122 | 0 | 16416 | 1666 | 0 | EL6021_M178 |  | BITVAL
SZI7021W | Alarme Feu Lagrange Couloir étage 0100 ZDA18 - ZONE 21 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 2 | [7 empty] | BITVAL
VFN6009S3 | Desenfumage 009 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 2 | 13122 | 4 | 16416 | 1666 | 4 | EL6021_M178 |  | BITVAL
VFN6009S4 | Desenfumage 009 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 3 | 13122 | 6 | 16416 | 1666 | 6 | EL6021_M178 |  | BITVAL
VFN6010S1 | Desenfumage 010 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 4 | 13122 | 8 | 16416 | 1667 | 0 | EL6021_M178 |  | BITVAL
SZI7022W | DM rdc Alarme Feu Lagrange ZDM19 - ZONE 22 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 6 | [7 empty] | BITVAL
VFN6010S3 | Desenfumage 010 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 6 | 13122 | 12 | 16416 | 1667 | 4 | EL6021_M178 |  | BITVAL
VFN6010S4 | Desenfumage 010 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 7 | 13122 | 14 | 16416 | 1667 | 6 | EL6021_M178 |  | BITVAL
VFN6012S1 | Desenfumage 012 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 8 | 13123 | 0 | 16416 | 1668 | 0 | EL6021_M178 |  | BITVAL
SZI7023W | DM 1°étage Alarme Feu Lagrange ZDM20 - ZONE 23 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 10 | [7 empty] | BITVAL
VFN6012S3 | Desenfumage 012 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 10 | 13123 | 4 | 16416 | 1668 | 4 | EL6021_M178 |  | BITVAL
VFN6012S4 | Desenfumage 012 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 11 | 13123 | 6 | 16416 | 1668 | 6 | EL6021_M178 |  | BITVAL
VFN6013S1 | Desenfumage 013 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 12 | 13123 | 8 | 16416 | 1669 | 0 | EL6021_M178 |  | BITVAL
SZI7024W | Alarme Feu Lagrange DEFAUT PORTE OUVERTE - ZONE 24 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 14 | [7 empty] | BITVAL
VFN6013S3 | Desenfumage 013 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 14 | 13123 | 12 | 16416 | 1669 | 4 | EL6021_M178 |  | BITVAL
VFN6013S4 | Desenfumage 013 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 15 | 13123 | 14 | 16416 | 1669 | 6 | EL6021_M178 |  | BITVAL
VFN6014S1 | Desenfumage 014 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 0 | 13124 | 0 | 16416 | 1670 | 0 | EL6021_M178 |  | BITVAL
SZI7025W | Alarme Feu Lagrange DEFAUT PARAFOUDRE 230V - ZONE 25 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1038 | 2 | [7 empty] | BITVAL
VFN6014S3 | Desenfumage 014 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 2 | 13124 | 4 | 16416 | 1670 | 4 | EL6021_M178 |  | BITVAL
VFN6014S4 | Desenfumage 014 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 3 | 13124 | 6 | 16416 | 1670 | 6 | EL6021_M178 |  | BITVAL
VFN6101S1 | Desenfumage 101 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 4 | 13124 | 8 | 16416 | 1671 | 0 | EL6021_M178 |  | BITVAL
SZI7026W | Alarme Feu Lagrange DEFAUT UGA - ZONE 26 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1038 | 6 | [7 empty] | BITVAL
VFN6101S3 | Desenfumage 101 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 6 | 13124 | 12 | 16416 | 1671 | 4 | EL6021_M178 |  | BITVAL
VFN6101S4 | Desenfumage 101 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 7 | 13124 | 14 | 16416 | 1671 | 6 | EL6021_M178 |  | BITVAL
VFN6109S1 | Desenfumage 109 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 8 | 13125 | 0 | 16416 | 1672 | 0 | EL6021_M178 |  | BITVAL
SCG7000DT | LAGRANGE DETG CENTRAL BATTERY LOW | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 0 | [7 empty] | BITVAL
VFN6109S3 | Desenfumage 109 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 10 | 13125 | 4 | 16416 | 1672 | 4 | EL6021_M178 |  | BITVAL
VFN6109S4 | Desenfumage 109 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 11 | 13125 | 6 | 16416 | 1672 | 6 | EL6021_M178 |  | BITVAL
VFN6111S1 | Desenfumage 111 Interrupteur alimentation ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 12 | 13125 | 8 | 16416 | 1673 | 0 | EL6021_M178 |  | BITVAL
VFN6111S4 | Desenfumage 111 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 13 | 13125 | 10 | 16416 | 1673 | 2 | EL6021_M178 |  | BITVAL
VFN6112S1 | Desenfumage 112 Interrupteur alimentation ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 14 | 13125 | 12 | 16416 | 1673 | 4 | EL6021_M178 |  | BITVAL
VFN6112S4 | Desenfumage 112 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 15 | 13125 | 14 | 16416 | 1673 | 6 | EL6021_M178 |  | BITVAL
VFN6113S1 | Desenfumage 113 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 0 | 13126 | 0 | 16416 | 1674 | 0 | EL6021_M178 |  | BITVAL
SCG7000DP | LAGRANGE DETG CENTRAL MAIN SUPPLY FAIL | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 2 | [7 empty] | BITVAL
VFN6113S3 | Desenfumage 113 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 2 | 13126 | 4 | 16416 | 1674 | 4 | EL6021_M178 |  | BITVAL
VFN6113S4 | Desenfumage 113 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 3 | 13126 | 6 | 16416 | 1674 | 6 | EL6021_M178 |  | BITVAL
VFN6117S1 | Desenfumage 117 Etat selecteur du moteur ON | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 4 | 13126 | 8 | 16416 | 1675 | 0 | EL6021_M178 |  | BITVAL
SCG7000DB | LAGRANGE DETG CENTRAL COMMON ALARM LOW RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 4 | [7 empty] | BITVAL
VFN6117S3 | Desenfumage 117 Volet Ouvert | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 6 | 13126 | 12 | 16416 | 1675 | 4 | EL6021_M178 |  | BITVAL
VFN6117S4 | Desenfumage 117 Désenfumage en marche | CR | N | RES | 1 | E | [26 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 7 | 13126 | 14 | 16416 | 1675 | 6 | EL6021_M178 |  | BITVAL
SPASCR0174 | SPARE SER 0174 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 8 | 13127 | 0 | 16416 | 1676 | 0 | EL6021_M178 |  | BITVAL
SPASCR0175 | SPARE SER 0175 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 9 | 13127 | 2 | 16416 | 1676 | 2 | EL6021_M178 |  | BITVAL
SPASCR0176 | SPARE SER 0176 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 10 | 13127 | 4 | 16416 | 1676 | 4 | EL6021_M178 |  | BITVAL
SPASCR0177 | SPARE SER 0177 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 11 | 13127 | 6 | 16416 | 1676 | 6 | EL6021_M178 |  | BITVAL
SPASCR0178 | SPARE SER 0178 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 12 | 13127 | 8 | 16416 | 1677 | 0 | EL6021_M178 |  | BITVAL
SPASCR0179 | SPARE SER 0179 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 13 | 13127 | 10 | 16416 | 1677 | 2 | EL6021_M178 |  | BITVAL
SPASCR0180 | SPARE SER 0180 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 14 | 13127 | 12 | 16416 | 1677 | 4 | EL6021_M178 |  | BITVAL
SPASCR0181 | SPARE SER 0181 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3053 | 15 | 13127 | 14 | 16416 | 1677 | 6 | EL6021_M178 |  | BITVAL
SPASCR0304 | SPARE SER 0304 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 5 |  |  | 3000 | 4 | 13442 | 8 | 16416 | 2307 | 0 | EL6021_M179 |  | BITVAL
SPASCR0305 | SPARE SER 0305 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 8 | 13443 | 0 | 16416 | 2308 | 0 | EL6021_M179 |  | BITVAL
SPASCR0306 | SPARE SER 0306 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 9 | 13443 | 2 | 16416 | 2308 | 2 | EL6021_M179 |  | BITVAL
SPASCR0307 | SPARE SER 0307 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 10 | 13443 | 4 | 16416 | 2308 | 4 | EL6021_M179 |  | BITVAL
SPASCR0308 | SPARE SER 0308 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 11 | 13443 | 6 | 16416 | 2308 | 6 | EL6021_M179 |  | BITVAL
SPASCR0309 | SPARE SER 0309 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 12 | 13443 | 8 | 16416 | 2309 | 0 | EL6021_M179 |  | BITVAL
SPASCR0310 | SPARE SER 0310 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 13 | 13443 | 10 | 16416 | 2309 | 2 | EL6021_M179 |  | BITVAL
SPASCR0311 | SPARE SER 0311 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 14 | 13443 | 12 | 16416 | 2309 | 4 | EL6021_M179 |  | BITVAL
SPASCR0312 | SPARE SER 0312 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3000 | 15 | 13443 | 14 | 16416 | 2309 | 6 | EL6021_M179 |  | BITVAL
SPASCR0313 | SPARE SER 0313 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 5 |  |  | 3001 | 6 | 13444 | 12 | 16416 | 2311 | 4 | EL6021_M179 |  | BITVAL
SPASCR0314 | SPARE SER 0314 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 5 |  |  | 3001 | 7 | 13444 | 14 | 16416 | 2311 | 6 | EL6021_M179 |  | BITVAL
SPASCR0315 | SPARE SER 0315 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 8 | 13445 | 0 | 16416 | 2312 | 0 | EL6021_M179 |  | BITVAL
SPASCR0316 | SPARE SER 0316 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 9 | 13445 | 2 | 16416 | 2312 | 2 | EL6021_M179 |  | BITVAL
SPASCR0317 | SPARE SER 0317 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 10 | 13445 | 4 | 16416 | 2312 | 4 | EL6021_M179 |  | BITVAL
SPASCR0318 | SPARE SER 0318 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 11 | 13445 | 6 | 16416 | 2312 | 6 | EL6021_M179 |  | BITVAL
SPASCR0319 | SPARE SER 0319 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 12 | 13445 | 8 | 16416 | 2313 | 0 | EL6021_M179 |  | BITVAL
SPASCR0320 | SPARE SER 0320 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 13 | 13445 | 10 | 16416 | 2313 | 2 | EL6021_M179 |  | BITVAL
SPASCR0321 | SPARE SER 0321 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 14 | 13445 | 12 | 16416 | 2313 | 4 | EL6021_M179 |  | BITVAL
SPASCR0322 | SPARE SER 0322 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3001 | 15 | 13445 | 14 | 16416 | 2313 | 6 | EL6021_M179 |  | BITVAL
SPASCR0323 | SPARE SER 0323 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 4 | 13448 | 8 | 16416 | 2319 | 0 | EL6021_M179 |  | BITVAL
SPASCR0324 | SPARE SER 0324 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 5 | 13448 | 10 | 16416 | 2319 | 2 | EL6021_M179 |  | BITVAL
SPASCR0325 | SPARE SER 0325 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 6 | 13448 | 12 | 16416 | 2319 | 4 | EL6021_M179 |  | BITVAL
SPASCR0326 | SPARE SER 0326 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 7 | 13448 | 14 | 16416 | 2319 | 6 | EL6021_M179 |  | BITVAL
SPASCR0327 | SPARE SER 0327 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 8 | 13449 | 0 | 16416 | 2320 | 0 | EL6021_M179 |  | BITVAL
SPASCR0328 | SPARE SER 0328 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 9 | 13449 | 2 | 16416 | 2320 | 2 | EL6021_M179 |  | BITVAL
SPASCR0329 | SPARE SER 0329 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 10 | 13449 | 4 | 16416 | 2320 | 4 | EL6021_M179 |  | BITVAL
SPASCR0330 | SPARE SER 0330 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 11 | 13449 | 6 | 16416 | 2320 | 6 | EL6021_M179 |  | BITVAL
SPASCR0331 | SPARE SER 0331 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 12 | 13449 | 8 | 16416 | 2321 | 0 | EL6021_M179 |  | BITVAL
SPASCR0332 | SPARE SER 0332 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 13 | 13449 | 10 | 16416 | 2321 | 2 | EL6021_M179 |  | BITVAL
SPASCR0333 | SPARE SER 0333 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 14 | 13449 | 12 | 16416 | 2321 | 4 | EL6021_M179 |  | BITVAL
SPASCR0334 | SPARE SER 0334 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 3003 | 15 | 13449 | 14 | 16416 | 2321 | 6 | EL6021_M179 |  | BITVAL
EQM6001F | POSITION IM CAT.I 1D60 Disconnector position | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 2000 | 0 | 13457 | 0 | 16416 | 2336 | 0 | EL6021_M179 |  | BITVAL
EQM6002F | POSITION IM CAT.II 1D60 Disconnector position | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 2000 | 1 | 13457 | 2 | 16416 | 2336 | 2 | EL6021_M179 |  | BITVAL
EQT6142O | CAT.I 1D60 TO 1D42 Earthing switch position | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 2000 | 4 | 13457 | 8 | 16416 | 2337 | 0 | EL6021_M179 |  | BITVAL
EQT6242O | CAT.II 1D60 TO 1D42 Earthing switch position | CR | N | RES | 1 | E | [26 empty] | NOT | 1000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 2000 | 5 | 13457 | 10 | 16416 | 2337 | 2 | EL6021_M179 |  | BITVAL
SPASCR0335 | SPARE SER 0335 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 5 |  |  | 2000 | 6 | 13457 | 12 | 16416 | 2337 | 4 | EL6021_M179 |  | BITVAL
SPASCR0336 | SPARE SER 0336 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 5 |  |  | 2000 | 7 | 13457 | 14 | 16416 | 2337 | 6 | EL6021_M179 |  | BITVAL
SPASCR0337 | SPARE SER 0337 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 8 | 13458 | 0 | 16416 | 2338 | 0 | EL6021_M179 |  | BITVAL
SPASCR0338 | SPARE SER 0338 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 9 | 13458 | 2 | 16416 | 2338 | 2 | EL6021_M179 |  | BITVAL
SPASCR0339 | SPARE SER 0339 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 10 | 13458 | 4 | 16416 | 2338 | 4 | EL6021_M179 |  | BITVAL
SPASCR0340 | SPARE SER 0340 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 11 | 13458 | 6 | 16416 | 2338 | 6 | EL6021_M179 |  | BITVAL
SPASCR0341 | SPARE SER 0341 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 12 | 13458 | 8 | 16416 | 2339 | 0 | EL6021_M179 |  | BITVAL
SPASCR0342 | SPARE SER 0342 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 13 | 13458 | 10 | 16416 | 2339 | 2 | EL6021_M179 |  | BITVAL
SPASCR0343 | SPARE SER 0343 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 14 | 13458 | 12 | 16416 | 2339 | 4 | EL6021_M179 |  | BITVAL
SPASCR0344 | SPARE SER 0344 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 2000 | 15 | 13458 | 14 | 16416 | 2339 | 6 | EL6021_M179 |  | BITVAL
SPASCR0434 | SPARE SER 0434 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3003 | 11 | 13759 | 6 | 16416 | 2940 | 6 | EL6021_M180 |  | BITVAL
SPASCR0435 | SPARE SER 0435 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3003 | 12 | 13759 | 8 | 16416 | 2941 | 0 | EL6021_M180 |  | BITVAL
SPASCR0436 | SPARE SER 0436 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3003 | 13 | 13759 | 10 | 16416 | 2941 | 2 | EL6021_M180 |  | BITVAL
SPASCR0437 | SPARE SER 0437 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3003 | 14 | 13759 | 12 | 16416 | 2941 | 4 | EL6021_M180 |  | BITVAL
SPASCR0438 | SPARE SER 0438 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 5 | 13770 | 10 | 16416 | 2963 | 2 | EL6021_M180 |  | BITVAL
SPASCR0439 | SPARE SER 0439 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 8 | 13771 | 0 | 16416 | 2964 | 0 | EL6021_M180 |  | BITVAL
SPASCR0440 | SPARE SER 0440 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 9 | 13771 | 2 | 16416 | 2964 | 2 | EL6021_M180 |  | BITVAL
SPASCR0441 | SPARE SER 0441 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 10 | 13771 | 4 | 16416 | 2964 | 4 | EL6021_M180 |  | BITVAL
SPASCR0442 | SPARE SER 0442 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 11 | 13771 | 6 | 16416 | 2964 | 6 | EL6021_M180 |  | BITVAL
SPASCR0443 | SPARE SER 0443 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 12 | 13771 | 8 | 16416 | 2965 | 0 | EL6021_M180 |  | BITVAL
SPASCR0444 | SPARE SER 0444 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 13 | 13771 | 10 | 16416 | 2965 | 2 | EL6021_M180 |  | BITVAL
SPASCR0445 | SPARE SER 0445 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 14 | 13771 | 12 | 16416 | 2965 | 4 | EL6021_M180 |  | BITVAL
SPASCR0446 | SPARE SER 0446 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3009 | 15 | 13771 | 14 | 16416 | 2965 | 6 | EL6021_M180 |  | BITVAL
SPASCR0447 | SPARE SER 0447 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 3 | 13772 | 6 | 16416 | 2966 | 6 | EL6021_M180 |  | BITVAL
SPASCR0448 | SPARE SER 0448 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 6 | 13772 | 12 | 16416 | 2967 | 4 | EL6021_M180 |  | BITVAL
SPASCR0449 | SPARE SER 0449 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 7 | 13772 | 14 | 16416 | 2967 | 6 | EL6021_M180 |  | BITVAL
SPASCR0450 | SPARE SER 0450 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 8 | 13773 | 0 | 16416 | 2968 | 0 | EL6021_M180 |  | BITVAL
SPASCR0451 | SPARE SER 0451 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 9 | 13773 | 2 | 16416 | 2968 | 2 | EL6021_M180 |  | BITVAL
SPASCR0452 | SPARE SER 0452 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 10 | 13773 | 4 | 16416 | 2968 | 4 | EL6021_M180 |  | BITVAL
SPASCR0453 | SPARE SER 0453 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 11 | 13773 | 6 | 16416 | 2968 | 6 | EL6021_M180 |  | BITVAL
SPASCR0454 | SPARE SER 0454 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 12 | 13773 | 8 | 16416 | 2969 | 0 | EL6021_M180 |  | BITVAL
SPASCR0455 | SPARE SER 0455 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 13 | 13773 | 10 | 16416 | 2969 | 2 | EL6021_M180 |  | BITVAL
SPASCR0456 | SPARE SER 0456 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 14 | 13773 | 12 | 16416 | 2969 | 4 | EL6021_M180 |  | BITVAL
SPASCR0457 | SPARE SER 0457 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3010 | 15 | 13773 | 14 | 16416 | 2969 | 6 | EL6021_M180 |  | BITVAL
SPASCR0458 | SPARE SER 0458 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3011 | 2 | 13774 | 4 | 16416 | 2970 | 4 | EL6021_M180 |  | BITVAL
SPASCR0459 | SPARE SER 0459 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3011 | 9 | 13775 | 2 | 16416 | 2972 | 2 | EL6021_M180 |  | BITVAL
SPASCR0460 | SPARE SER 0460 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3012 | 1 | 13776 | 2 | 16416 | 2974 | 2 | EL6021_M180 |  | BITVAL
SPASCR0461 | SPARE SER 0461 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3012 | 2 | 13776 | 4 | 16416 | 2974 | 4 | EL6021_M180 |  | BITVAL
SPASCR0462 | SPARE SER 0462 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3012 | 5 | 13776 | 10 | 16416 | 2975 | 2 | EL6021_M180 |  | BITVAL
SPASCR0463 | SPARE SER 0463 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3012 | 6 | 13776 | 12 | 16416 | 2975 | 4 | EL6021_M180 |  | BITVAL
SPASCR0464 | SPARE SER 0464 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3012 | 15 | 13777 | 14 | 16416 | 2977 | 6 | EL6021_M180 |  | BITVAL
SPASCR0465 | SPARE SER 0465 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3013 | 0 | 13778 | 0 | 16416 | 2978 | 0 | EL6021_M180 |  | BITVAL
SPASCR0466 | SPARE SER 0466 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3013 | 3 | 13778 | 6 | 16416 | 2978 | 6 | EL6021_M180 |  | BITVAL
SPASCR0467 | SPARE SER 0467 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3013 | 4 | 13778 | 8 | 16416 | 2979 | 0 | EL6021_M180 |  | BITVAL
SPASCR0468 | SPARE SER 0468 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3013 | 5 | 13778 | 10 | 16416 | 2979 | 2 | EL6021_M180 |  | BITVAL
SPASCR0469 | SPARE SER 0469 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3014 | 12 | 13781 | 8 | 16416 | 2985 | 0 | EL6021_M180 |  | BITVAL
SPASCR0470 | SPARE SER 0470 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3015 | 1 | 13782 | 2 | 16416 | 2986 | 2 | EL6021_M180 |  | BITVAL
SPASCR0471 | SPARE SER 0471 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3015 | 2 | 13782 | 4 | 16416 | 2986 | 4 | EL6021_M180 |  | BITVAL
SPASCR0472 | SPARE SER 0472 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3015 | 3 | 13782 | 6 | 16416 | 2986 | 6 | EL6021_M180 |  | BITVAL
SPASCR0473 | SPARE SER 0473 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3016 | 13 | 13785 | 10 | 16416 | 2993 | 2 | EL6021_M180 |  | BITVAL
SPASCR0474 | SPARE SER 0474 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3016 | 14 | 13785 | 12 | 16416 | 2993 | 4 | EL6021_M180 |  | BITVAL
SPASCR0475 | SPARE SER 0475 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 6 | 13786 | 12 | 16416 | 2995 | 4 | EL6021_M180 |  | BITVAL
SPASCR0476 | SPARE SER 0476 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 7 | 13786 | 14 | 16416 | 2995 | 6 | EL6021_M180 |  | BITVAL
SPASCR0477 | SPARE SER 0477 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 8 | 13787 | 0 | 16416 | 2996 | 0 | EL6021_M180 |  | BITVAL
SPASCR0478 | SPARE SER 0478 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 9 | 13787 | 2 | 16416 | 2996 | 2 | EL6021_M180 |  | BITVAL
SPASCR0479 | SPARE SER 0479 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 10 | 13787 | 4 | 16416 | 2996 | 4 | EL6021_M180 |  | BITVAL
SPASCR0480 | SPARE SER 0480 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 11 | 13787 | 6 | 16416 | 2996 | 6 | EL6021_M180 |  | BITVAL
SPASCR0481 | SPARE SER 0481 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 12 | 13787 | 8 | 16416 | 2997 | 0 | EL6021_M180 |  | BITVAL
SPASCR0482 | SPARE SER 0482 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 13 | 13787 | 10 | 16416 | 2997 | 2 | EL6021_M180 |  | BITVAL
SPASCR0483 | SPARE SER 0483 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 14 | 13787 | 12 | 16416 | 2997 | 4 | EL6021_M180 |  | BITVAL
SPASCR0484 | SPARE SER 0484 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3017 | 15 | 13787 | 14 | 16416 | 2997 | 6 | EL6021_M180 |  | BITVAL
SPASCR0485 | SPARE SER 0485 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 4 | 16040 | 8 | 16416 | 7503 | 0 | EL6021_M180 |  | BITVAL
SPASCR0486 | SPARE SER 0486 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 5 | 16040 | 10 | 16416 | 7503 | 2 | EL6021_M180 |  | BITVAL
SPASCR0487 | SPARE SER 0487 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 6 | 16040 | 12 | 16416 | 7503 | 4 | EL6021_M180 |  | BITVAL
SPASCR0488 | SPARE SER 0488 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 7 | 16040 | 14 | 16416 | 7503 | 6 | EL6021_M180 |  | BITVAL
SPASCR0489 | SPARE SER 0489 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 9 | 16041 | 2 | 16416 | 7504 | 2 | EL6021_M180 |  | BITVAL
SPASCR0490 | SPARE SER 0490 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 14 | 16041 | 12 | 16416 | 7505 | 4 | EL6021_M180 |  | BITVAL
SPASCR0491 | SPARE SER 0491 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3018 | 15 | 16041 | 14 | 16416 | 7505 | 6 | EL6021_M180 |  | BITVAL
SPASCR0492 | SPARE SER 0492 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 1 | 16042 | 2 | 16416 | 7506 | 2 | EL6021_M180 |  | BITVAL
SPASCR0493 | SPARE SER 0493 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 2 | 16042 | 4 | 16416 | 7506 | 4 | EL6021_M180 |  | BITVAL
SPASCR0494 | SPARE SER 0494 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 3 | 16042 | 6 | 16416 | 7506 | 6 | EL6021_M180 |  | BITVAL
SPASCR0495 | SPARE SER 0495 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 6 | 16042 | 12 | 16416 | 7507 | 4 | EL6021_M180 |  | BITVAL
SPASCR0496 | SPARE SER 0496 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 7 | 16042 | 14 | 16416 | 7507 | 6 | EL6021_M180 |  | BITVAL
SPASCR0497 | SPARE SER 0497 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 11 | 16043 | 6 | 16416 | 7508 | 6 | EL6021_M180 |  | BITVAL
SPASCR0498 | SPARE SER 0498 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 12 | 16043 | 8 | 16416 | 7509 | 0 | EL6021_M180 |  | BITVAL
SPASCR0499 | SPARE SER 0499 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 13 | 16043 | 10 | 16416 | 7509 | 2 | EL6021_M180 |  | BITVAL
SPASCR0500 | SPARE SER 0500 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 14 | 16043 | 12 | 16416 | 7509 | 4 | EL6021_M180 |  | BITVAL
SPASCR0501 | SPARE SER 0501 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3019 | 15 | 16043 | 14 | 16416 | 7509 | 6 | EL6021_M180 |  | BITVAL
SPASCR0502 | SPARE SER 0502 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 4 | 13790 | 8 | 16416 | 3003 | 0 | EL6021_M180 |  | BITVAL
SPASCR0503 | SPARE SER 0503 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 5 | 13790 | 10 | 16416 | 3003 | 2 | EL6021_M180 |  | BITVAL
SPASCR0504 | SPARE SER 0504 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 6 | 13790 | 12 | 16416 | 3003 | 4 | EL6021_M180 |  | BITVAL
SPASCR0505 | SPARE SER 0505 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 7 | 13790 | 14 | 16416 | 3003 | 6 | EL6021_M180 |  | BITVAL
SPASCR0506 | SPARE SER 0506 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 12 | 13791 | 8 | 16416 | 3005 | 0 | EL6021_M180 |  | BITVAL
SPASCR0507 | SPARE SER 0507 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 13 | 13791 | 10 | 16416 | 3005 | 2 | EL6021_M180 |  | BITVAL
SPASCR0508 | SPARE SER 0508 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 14 | 13791 | 12 | 16416 | 3005 | 4 | EL6021_M180 |  | BITVAL
SPASCR0509 | SPARE SER 0509 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3020 | 15 | 13791 | 14 | 16416 | 3005 | 6 | EL6021_M180 |  | BITVAL
SPASCR0510 | SPARE SER 0510 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 3 | 13792 | 6 | 16416 | 3006 | 6 | EL6021_M180 |  | BITVAL
SPASCR0511 | SPARE SER 0511 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 5 | 13792 | 10 | 16416 | 3007 | 2 | EL6021_M180 |  | BITVAL
SPASCR0512 | SPARE SER 0512 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 6 | 13792 | 12 | 16416 | 3007 | 4 | EL6021_M180 |  | BITVAL
SPASCR0513 | SPARE SER 0513 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 10 | 13793 | 4 | 16416 | 3008 | 4 | EL6021_M180 |  | BITVAL
SPASCR0514 | SPARE SER 0514 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 11 | 13793 | 6 | 16416 | 3008 | 6 | EL6021_M180 |  | BITVAL
SPASCR0515 | SPARE SER 0515 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 12 | 13793 | 8 | 16416 | 3009 | 0 | EL6021_M180 |  | BITVAL
SPASCR0516 | SPARE SER 0516 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 13 | 13793 | 10 | 16416 | 3009 | 2 | EL6021_M180 |  | BITVAL
SPASCR0517 | SPARE SER 0517 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 14 | 13793 | 12 | 16416 | 3009 | 4 | EL6021_M180 |  | BITVAL
SPASCR0518 | SPARE SER 0518 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3021 | 15 | 13793 | 14 | 16416 | 3009 | 6 | EL6021_M180 |  | BITVAL
SPASCR0519 | SPARE SER 0519 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 5 | 13794 | 10 | 16416 | 3011 | 2 | EL6021_M180 |  | BITVAL
SPASCR0520 | SPARE SER 0520 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 6 | 13794 | 12 | 16416 | 3011 | 4 | EL6021_M180 |  | BITVAL
SPASCR0521 | SPARE SER 0521 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 11 | 13795 | 6 | 16416 | 3012 | 6 | EL6021_M180 |  | BITVAL
SPASCR0522 | SPARE SER 0522 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 12 | 13795 | 8 | 16416 | 3013 | 0 | EL6021_M180 |  | BITVAL
SPASCR0523 | SPARE SER 0523 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 13 | 13795 | 10 | 16416 | 3013 | 2 | EL6021_M180 |  | BITVAL
SPASCR0524 | SPARE SER 0524 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 14 | 13795 | 12 | 16416 | 3013 | 4 | EL6021_M180 |  | BITVAL
SPASCR0525 | SPARE SER 0525 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3022 | 15 | 13795 | 14 | 16416 | 3013 | 6 | EL6021_M180 |  | BITVAL
SPASCR0526 | SPARE SER 0526 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 3 | 13796 | 6 | 16416 | 3014 | 6 | EL6021_M180 |  | BITVAL
SPASCR0527 | SPARE SER 0527 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 7 | 13796 | 14 | 16416 | 3015 | 6 | EL6021_M180 |  | BITVAL
SPASCR0528 | SPARE SER 0528 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 11 | 13797 | 6 | 16416 | 3016 | 6 | EL6021_M180 |  | BITVAL
SPASCR0529 | SPARE SER 0529 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 12 | 13797 | 8 | 16416 | 3017 | 0 | EL6021_M180 |  | BITVAL
SPASCR0530 | SPARE SER 0530 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 13 | 13797 | 10 | 16416 | 3017 | 2 | EL6021_M180 |  | BITVAL
SPASCR0531 | SPARE SER 0531 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 14 | 13797 | 12 | 16416 | 3017 | 4 | EL6021_M180 |  | BITVAL
SPASCR0532 | SPARE SER 0532 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3023 | 15 | 13797 | 14 | 16416 | 3017 | 6 | EL6021_M180 |  | BITVAL
SPASCR0533 | SPARE SER 0533 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 5 | 13798 | 10 | 16416 | 3019 | 2 | EL6021_M180 |  | BITVAL
SPASCR0534 | SPARE SER 0534 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 6 | 13798 | 12 | 16416 | 3019 | 4 | EL6021_M180 |  | BITVAL
SPASCR0535 | SPARE SER 0535 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 7 | 13798 | 14 | 16416 | 3019 | 6 | EL6021_M180 |  | BITVAL
SPASCR0536 | SPARE SER 0536 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 8 | 13799 | 0 | 16416 | 3020 | 0 | EL6021_M180 |  | BITVAL
SPASCR0537 | SPARE SER 0537 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 9 | 13799 | 2 | 16416 | 3020 | 2 | EL6021_M180 |  | BITVAL
SPASCR0538 | SPARE SER 0538 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 10 | 13799 | 4 | 16416 | 3020 | 4 | EL6021_M180 |  | BITVAL
SPASCR0539 | SPARE SER 0539 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 11 | 13799 | 6 | 16416 | 3020 | 6 | EL6021_M180 |  | BITVAL
SPASCR0540 | SPARE SER 0540 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 12 | 13799 | 8 | 16416 | 3021 | 0 | EL6021_M180 |  | BITVAL
SPASCR0541 | SPARE SER 0541 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 13 | 13799 | 10 | 16416 | 3021 | 2 | EL6021_M180 |  | BITVAL
SPASCR0542 | SPARE SER 0542 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 14 | 13799 | 12 | 16416 | 3021 | 4 | EL6021_M180 |  | BITVAL
SPASCR0543 | SPARE SER 0543 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3024 | 15 | 13799 | 14 | 16416 | 3021 | 6 | EL6021_M180 |  | BITVAL
GGF6001M | VEGA BUNKER PLC : CHILLER 1 ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3025 | 0 | 13800 | 0 | 16416 | 3022 | 0 | EL6021_M180 |  | BITVAL
GGF6002M | VEGA BUNKER PLC : CHILLER 2 ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3025 | 1 | 13800 | 2 | 16416 | 3022 | 2 | EL6021_M180 |  | BITVAL
GGF6003M | VEGA BUNKER PLC : CHILLER 3 ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3025 | 2 | 13800 | 4 | 16416 | 3022 | 4 | EL6021_M180 |  | BITVAL
GPP6004M1 | VEGA BUNKER PLC : COLD WATER PUMP M04 (BUNKER) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3025 | 3 | 13800 | 6 | 16416 | 3022 | 6 | EL6021_M180 |  | BITVAL
GPP6001M1 | VEGA BUNKER PLC : COLD WATER PUMP P01 (GANTRY) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3025 | 4 | 13800 | 8 | 16416 | 3023 | 0 | EL6021_M180 |  | BITVAL
CPP6004M3 | VEGA BUNKER PLC : HOT WATER PUMP M04 (BUNKER/GANTRY) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3025 | 5 | 13800 | 10 | 16416 | 3023 | 2 | EL6021_M180 |  | BITVAL
VRP6118O3 | VEGA BUNKER PLC : FRESH AIR MOTORISED DAMPER 118.3 (CTA 1) OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 6 | 13800 | 12 | 16416 | 3023 | 4 | EL6021_M180 |  | BITVAL
VRP6118F3 | VEGA BUNKER PLC : FRESH AIR MOTORISED DAMPER 118.3 (CTA 1) CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 7 | 13800 | 14 | 16416 | 3023 | 6 | EL6021_M180 |  | BITVAL
VRP6118O4 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 118.4 (CTA 1) OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04;HVAC05;HVAC06;HVAC13 | HVAC |  | 6 |  |  | 3025 | 8 | 13801 | 0 | 16416 | 3024 | 0 | EL6021_M180 |  | BITVAL
VRP6118F4 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 118.4 (CTA 1) CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04;HVAC05;HVAC06 | HVAC |  | 6 |  |  | 3025 | 9 | 13801 | 2 | 16416 | 3024 | 2 | EL6021_M180 |  | BITVAL
VCT6001M | VEGA BUNKER PLC : FAN CTA M01 ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 10 | 13801 | 4 | 16416 | 3024 | 4 | EL6021_M180 |  | BITVAL
VRP6127O1 | VEGA BUNKER PLC : LOCAL FRESH AIR MOTORISED DAMPER 127.1 OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 11 | 13801 | 6 | 16416 | 3024 | 6 | EL6021_M180 |  | BITVAL
VRP6127F1 | VEGA BUNKER PLC : LOCAL FRESH AIR MOTORISED DAMPER 127.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 12 | 13801 | 8 | 16416 | 3025 | 0 | EL6021_M180 |  | BITVAL
VRP6127O2 | VEGA BUNKER PLC : DISTANT FRESH AIR MOTORISED DAMPER 127.2 OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 13 | 13801 | 10 | 16416 | 3025 | 2 | EL6021_M180 |  | BITVAL
VRP6127F2 | VEGA BUNKER PLC : DISTANT FRESH AIR MOTORISED DAMPER 127.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 14 | 13801 | 12 | 16416 | 3025 | 4 | EL6021_M180 |  | BITVAL
VFN6003M | VEGA BUNKER PLC : DISTANT FRESH AIR FAN M03 ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3025 | 15 | 13801 | 14 | 16416 | 3025 | 6 | EL6021_M180 |  | BITVAL
VCF6004F1 | VEGA BUNKER PLC : FIRE DAMPER 004.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 0 | 13802 | 0 | 16416 | 3026 | 0 | EL6021_M180 |  | BITVAL
VCF6004O1 | VEGA BUNKER PLC : FIRE DAMPER 004.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 1 | 13802 | 2 | 16416 | 3026 | 2 | EL6021_M180 |  | BITVAL
VCF6007F1 | VEGA BUNKER PLC : FIRE DAMPER 007.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 2 | 13802 | 4 | 16416 | 3026 | 4 | EL6021_M180 |  | BITVAL
VCF6007O1 | VEGA BUNKER PLC : FIRE DAMPER 007.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 3 | 13802 | 6 | 16416 | 3026 | 6 | EL6021_M180 |  | BITVAL
VCF6007F2 | VEGA BUNKER PLC : FIRE DAMPER 007.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 4 | 13802 | 8 | 16416 | 3027 | 0 | EL6021_M180 |  | BITVAL
VCF6007O2 | VEGA BUNKER PLC : FIRE DAMPER 007.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 5 | 13802 | 10 | 16416 | 3027 | 2 | EL6021_M180 |  | BITVAL
VCF6008F1 | VEGA BUNKER PLC : FIRE DAMPER 008.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 6 | 13802 | 12 | 16416 | 3027 | 4 | EL6021_M180 |  | BITVAL
VCF6008O1 | VEGA BUNKER PLC : FIRE DAMPER 008.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 7 | 13802 | 14 | 16416 | 3027 | 6 | EL6021_M180 |  | BITVAL
VCF6008F2 | VEGA BUNKER PLC : FIRE DAMPER 008.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 8 | 13803 | 0 | 16416 | 3028 | 0 | EL6021_M180 |  | BITVAL
VCF6008O2 | VEGA BUNKER PLC : FIRE DAMPER 008.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 9 | 13803 | 2 | 16416 | 3028 | 2 | EL6021_M180 |  | BITVAL
VCF6009F1 | VEGA BUNKER PLC : FIRE DAMPER 009.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 10 | 13803 | 4 | 16416 | 3028 | 4 | EL6021_M180 |  | BITVAL
VCF6009O1 | VEGA BUNKER PLC : FIRE DAMPER 009.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 11 | 13803 | 6 | 16416 | 3028 | 6 | EL6021_M180 |  | BITVAL
VCF6013F1 | VEGA BUNKER PLC : FIRE DAMPER 013.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 12 | 13803 | 8 | 16416 | 3029 | 0 | EL6021_M180 |  | BITVAL
VCF6013O1 | VEGA BUNKER PLC : FIRE DAMPER 013.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 13 | 13803 | 10 | 16416 | 3029 | 2 | EL6021_M180 |  | BITVAL
VCF6013F2 | VEGA BUNKER PLC : FIRE DAMPER 013.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 14 | 13803 | 12 | 16416 | 3029 | 4 | EL6021_M180 |  | BITVAL
VCF6013O2 | VEGA BUNKER PLC : FIRE DAMPER 013.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3026 | 15 | 13803 | 14 | 16416 | 3029 | 6 | EL6021_M180 |  | BITVAL
VCF6013F3 | VEGA BUNKER PLC : FIRE DAMPER 013.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 0 | 13804 | 0 | 16416 | 3030 | 0 | EL6021_M180 |  | BITVAL
VCF6013O3 | VEGA BUNKER PLC : FIRE DAMPER 013.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 1 | 13804 | 2 | 16416 | 3030 | 2 | EL6021_M180 |  | BITVAL
VCF6103F1 | VEGA BUNKER PLC : FIRE DAMPER 103.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 2 | 13804 | 4 | 16416 | 3030 | 4 | EL6021_M180 |  | BITVAL
VCF6103O1 | VEGA BUNKER PLC : FIRE DAMPER 103.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 3 | 13804 | 6 | 16416 | 3030 | 6 | EL6021_M180 |  | BITVAL
VCF6103F2 | VEGA BUNKER PLC : FIRE DAMPER 103.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 4 | 13804 | 8 | 16416 | 3031 | 0 | EL6021_M180 |  | BITVAL
VCF6103O2 | VEGA BUNKER PLC : FIRE DAMPER 103.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 5 | 13804 | 10 | 16416 | 3031 | 2 | EL6021_M180 |  | BITVAL
VCF6106F1 | VEGA BUNKER PLC : FIRE DAMPER 106.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 6 | 13804 | 12 | 16416 | 3031 | 4 | EL6021_M180 |  | BITVAL
VCF6106O1 | VEGA BUNKER PLC : FIRE DAMPER 106.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 7 | 13804 | 14 | 16416 | 3031 | 6 | EL6021_M180 |  | BITVAL
VCF6111F1 | VEGA BUNKER PLC : FIRE DAMPER 111.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 8 | 13805 | 0 | 16416 | 3032 | 0 | EL6021_M180 |  | BITVAL
VCF6111O1 | VEGA BUNKER PLC : FIRE DAMPER 111.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 9 | 13805 | 2 | 16416 | 3032 | 2 | EL6021_M180 |  | BITVAL
VCF6111F2 | VEGA BUNKER PLC : FIRE DAMPER 111.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 10 | 13805 | 4 | 16416 | 3032 | 4 | EL6021_M180 |  | BITVAL
VCF6111O2 | VEGA BUNKER PLC : FIRE DAMPER 111.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 11 | 13805 | 6 | 16416 | 3032 | 6 | EL6021_M180 |  | BITVAL
VCF6112F1 | VEGA BUNKER PLC : FIRE DAMPER 112.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 12 | 13805 | 8 | 16416 | 3033 | 0 | EL6021_M180 |  | BITVAL
VCF6112O1 | VEGA BUNKER PLC : FIRE DAMPER 112.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 13 | 13805 | 10 | 16416 | 3033 | 2 | EL6021_M180 |  | BITVAL
VCF6113F1 | VEGA BUNKER PLC : FIRE DAMPER 113.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 14 | 13805 | 12 | 16416 | 3033 | 4 | EL6021_M180 |  | BITVAL
VCF6113O1 | VEGA BUNKER PLC : FIRE DAMPER 113.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3027 | 15 | 13805 | 14 | 16416 | 3033 | 6 | EL6021_M180 |  | BITVAL
VCF6115F1 | VEGA BUNKER PLC : FIRE DAMPER 115.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 0 | 13806 | 0 | 16416 | 3034 | 0 | EL6021_M180 |  | BITVAL
VCF6115O1 | VEGA BUNKER PLC : FIRE DAMPER 115.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 1 | 13806 | 2 | 16416 | 3034 | 2 | EL6021_M180 |  | BITVAL
VCF6115F2 | VEGA BUNKER PLC : FIRE DAMPER 115.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 2 | 13806 | 4 | 16416 | 3034 | 4 | EL6021_M180 |  | BITVAL
VCF6115O2 | VEGA BUNKER PLC : FIRE DAMPER 115.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 3 | 13806 | 6 | 16416 | 3034 | 6 | EL6021_M180 |  | BITVAL
VCF6115F3 | VEGA BUNKER PLC : FIRE DAMPER 115.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 4 | 13806 | 8 | 16416 | 3035 | 0 | EL6021_M180 |  | BITVAL
VCF6115O3 | VEGA BUNKER PLC : FIRE DAMPER 115.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 5 | 13806 | 10 | 16416 | 3035 | 2 | EL6021_M180 |  | BITVAL
VCF6116F1 | VEGA BUNKER PLC : FIRE DAMPER 116.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 6 | 13806 | 12 | 16416 | 3035 | 4 | EL6021_M180 |  | BITVAL
VCF6116O1 | VEGA BUNKER PLC : FIRE DAMPER 116.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 7 | 13806 | 14 | 16416 | 3035 | 6 | EL6021_M180 |  | BITVAL
VCF6118F1 | VEGA BUNKER PLC : FIRE DAMPER 118.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 8 | 13807 | 0 | 16416 | 3036 | 0 | EL6021_M180 |  | BITVAL
VCF6118O1 | VEGA BUNKER PLC : FIRE DAMPER 118.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 9 | 13807 | 2 | 16416 | 3036 | 2 | EL6021_M180 |  | BITVAL
VCF6118F2 | VEGA BUNKER PLC : FIRE DAMPER 118.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 10 | 13807 | 4 | 16416 | 3036 | 4 | EL6021_M180 |  | BITVAL
VCF6118O2 | VEGA BUNKER PLC : FIRE DAMPER 118.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3028 | 11 | 13807 | 6 | 16416 | 3036 | 6 | EL6021_M180 |  | BITVAL
VRP6004F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 004.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3028 | 12 | 13807 | 8 | 16416 | 3037 | 0 | EL6021_M180 |  | BITVAL
VRP6004O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 004.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3028 | 13 | 13807 | 10 | 16416 | 3037 | 2 | EL6021_M180 |  | BITVAL
VRP6007F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 007.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3028 | 14 | 13807 | 12 | 16416 | 3037 | 4 | EL6021_M180 |  | BITVAL
VRP6007O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 007.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3028 | 15 | 13807 | 14 | 16416 | 3037 | 6 | EL6021_M180 |  | BITVAL
VRP6008F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 008.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 0 | 13808 | 0 | 16416 | 3038 | 0 | EL6021_M180 |  | BITVAL
VRP6008O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 008.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 1 | 13808 | 2 | 16416 | 3038 | 2 | EL6021_M180 |  | BITVAL
VRP6009F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 009.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 2 | 13808 | 4 | 16416 | 3038 | 4 | EL6021_M180 |  | BITVAL
VRP6009O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 009.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 3 | 13808 | 6 | 16416 | 3038 | 6 | EL6021_M180 |  | BITVAL
VRP6013F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 013.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 4 | 13808 | 8 | 16416 | 3039 | 0 | EL6021_M180 |  | BITVAL
VRP6013O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 013.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 5 | 13808 | 10 | 16416 | 3039 | 2 | EL6021_M180 |  | BITVAL
VRP6101F11 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 101.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 6 | 13808 | 12 | 16416 | 3039 | 4 | EL6021_M180 |  | BITVAL
VRP6101O11 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 101.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 7 | 13808 | 14 | 16416 | 3039 | 6 | EL6021_M180 |  | BITVAL
VRP6103F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 103.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 8 | 13809 | 0 | 16416 | 3040 | 0 | EL6021_M180 |  | BITVAL
VRP6103O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 103.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 9 | 13809 | 2 | 16416 | 3040 | 2 | EL6021_M180 |  | BITVAL
VRP6111F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 111.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 10 | 13809 | 4 | 16416 | 3040 | 4 | EL6021_M180 |  | BITVAL
VRP6111O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 111.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 11 | 13809 | 6 | 16416 | 3040 | 6 | EL6021_M180 |  | BITVAL
VRP6112F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 112.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 12 | 13809 | 8 | 16416 | 3041 | 0 | EL6021_M180 |  | BITVAL
VRP6112O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 112.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 13 | 13809 | 10 | 16416 | 3041 | 2 | EL6021_M180 |  | BITVAL
VRP6113F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 113.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 14 | 13809 | 12 | 16416 | 3041 | 4 | EL6021_M180 |  | BITVAL
VRP6113O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 113.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3029 | 15 | 13809 | 14 | 16416 | 3041 | 6 | EL6021_M180 |  | BITVAL
VRP6115F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 115.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 0 | 13810 | 0 | 16416 | 3042 | 0 | EL6021_M180 |  | BITVAL
VRP6115O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 115.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 1 | 13810 | 2 | 16416 | 3042 | 2 | EL6021_M180 |  | BITVAL
VRP6116F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 116.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3030 | 2 | 13810 | 4 | 16416 | 3042 | 4 | EL6021_M180 |  | BITVAL
VRP6116O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 116.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3030 | 3 | 13810 | 6 | 16416 | 3042 | 6 | EL6021_M180 |  | BITVAL
VRP6106F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 106.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3030 | 4 | 13810 | 8 | 16416 | 3043 | 0 | EL6021_M180 |  | BITVAL
VRP6106O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 106.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3030 | 5 | 13810 | 10 | 16416 | 3043 | 2 | EL6021_M180 |  | BITVAL
VRP6004F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 004.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 6 | 13810 | 12 | 16416 | 3043 | 4 | EL6021_M180 |  | BITVAL
VRP6004O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 004.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 7 | 13810 | 14 | 16416 | 3043 | 6 | EL6021_M180 |  | BITVAL
VRP6007F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 007.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 8 | 13811 | 0 | 16416 | 3044 | 0 | EL6021_M180 |  | BITVAL
VRP6007O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 007.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 9 | 13811 | 2 | 16416 | 3044 | 2 | EL6021_M180 |  | BITVAL
VRP6008F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 008.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 10 | 13811 | 4 | 16416 | 3044 | 4 | EL6021_M180 |  | BITVAL
VRP6008O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 008.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 11 | 13811 | 6 | 16416 | 3044 | 6 | EL6021_M180 |  | BITVAL
VRP6009F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 009.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 12 | 13811 | 8 | 16416 | 3045 | 0 | EL6021_M180 |  | BITVAL
VRP6009O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 009.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 13 | 13811 | 10 | 16416 | 3045 | 2 | EL6021_M180 |  | BITVAL
VRP6002F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 002.2 (ROOMS 002 AND 013) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 14 | 13811 | 12 | 16416 | 3045 | 4 | EL6021_M180 |  | BITVAL
VRP6002O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 002.2 (ROOMS 002 AND 013) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3030 | 15 | 13811 | 14 | 16416 | 3045 | 6 | EL6021_M180 |  | BITVAL
VRP6101F12 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 101.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 0 | 13812 | 0 | 16416 | 3046 | 0 | EL6021_M180 |  | BITVAL
VRP6101O12 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 101.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 1 | 13812 | 2 | 16416 | 3046 | 2 | EL6021_M180 |  | BITVAL
VRP6103F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 103.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 2 | 13812 | 4 | 16416 | 3046 | 4 | EL6021_M180 |  | BITVAL
VRP6103O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 103.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 3 | 13812 | 6 | 16416 | 3046 | 6 | EL6021_M180 |  | BITVAL
VRP6111F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 111.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 4 | 13812 | 8 | 16416 | 3047 | 0 | EL6021_M180 |  | BITVAL
VRP6111O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 111.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 5 | 13812 | 10 | 16416 | 3047 | 2 | EL6021_M180 |  | BITVAL
VRP6112F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 112.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 6 | 13812 | 12 | 16416 | 3047 | 4 | EL6021_M180 |  | BITVAL
VRP6112O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 112.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 7 | 13812 | 14 | 16416 | 3047 | 6 | EL6021_M180 |  | BITVAL
VRP6113F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 113.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 8 | 13813 | 0 | 16416 | 3048 | 0 | EL6021_M180 |  | BITVAL
VRP6113O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 113.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 9 | 13813 | 2 | 16416 | 3048 | 2 | EL6021_M180 |  | BITVAL
VRP6115F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 115.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 10 | 13813 | 4 | 16416 | 3048 | 4 | EL6021_M180 |  | BITVAL
VRP6115O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 115.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3031 | 11 | 13813 | 6 | 16416 | 3048 | 6 | EL6021_M180 |  | BITVAL
VRP6116F2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 116.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3031 | 12 | 13813 | 8 | 16416 | 3049 | 0 | EL6021_M180 |  | BITVAL
VRP6116O2 | VEGA BUNKER PLC : EXTRACT N2 MOTORISED DAMPER 116.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3031 | 13 | 13813 | 10 | 16416 | 3049 | 2 | EL6021_M180 |  | BITVAL
VFN6000M | VEGA BUNKER PLC : FAN EXTRACTOR SANITATION ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3031 | 14 | 13813 | 12 | 16416 | 3049 | 4 | EL6021_M180 |  | BITVAL
GVM6001F2 | VEGA BUNKER PLC : COLD WATER VALVE SUPPLY GANTRY REAR POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3031 | 15 | 13813 | 14 | 16416 | 3049 | 6 | EL6021_M180 |  | BITVAL
GVM6001O2 | VEGA BUNKER PLC : COLD WATER VALVE SUPPLY GANTRY REAR POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 0 | 13814 | 0 | 16416 | 3050 | 0 | EL6021_M180 |  | BITVAL
GVM6003F2 | VEGA BUNKER PLC : COLD WATER VALVE RETURN GANTRY REAR POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 1 | 13814 | 2 | 16416 | 3050 | 2 | EL6021_M180 |  | BITVAL
GVM6003O2 | VEGA BUNKER PLC : COLD WATER VALVE RETURN GANTRY REAR POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 2 | 13814 | 4 | 16416 | 3050 | 4 | EL6021_M180 |  | BITVAL
CVM6001F2 | VEGA BUNKER PLC : HOT WATER VALVE SUPPLY GANTRY REAR POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 3 | 13814 | 6 | 16416 | 3050 | 6 | EL6021_M180 |  | BITVAL
CVM6001O2 | VEGA BUNKER PLC : HOT WATER VALVE SUPPLY GANTRY REAR POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 4 | 13814 | 8 | 16416 | 3051 | 0 | EL6021_M180 |  | BITVAL
CVM6003F2 | VEGA BUNKER PLC : HOT WATER VALVE RETURN GANTRY REAR POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 5 | 13814 | 10 | 16416 | 3051 | 2 | EL6021_M180 |  | BITVAL
CVM6003O2 | VEGA BUNKER PLC : HOT WATER VALVE RETURN GANTRY REAR POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 6 | 13814 | 12 | 16416 | 3051 | 4 | EL6021_M180 |  | BITVAL
GVM6002F2 | VEGA BUNKER PLC : COLD WATER VALVE SUPPLY GANTRY FORWARD POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 7 | 13814 | 14 | 16416 | 3051 | 6 | EL6021_M180 |  | BITVAL
GVM6002O2 | VEGA BUNKER PLC : COLD WATER VALVE SUPPLY GANTRY FORWARD POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 8 | 13815 | 0 | 16416 | 3052 | 0 | EL6021_M180 |  | BITVAL
GVM6004F2 | VEGA BUNKER PLC : COLD WATER VALVE RETURN GANTRY FORWARD POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 9 | 13815 | 2 | 16416 | 3052 | 2 | EL6021_M180 |  | BITVAL
GVM6004O2 | VEGA BUNKER PLC : COLD WATER VALVE RETURN GANTRY FORWARD POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 10 | 13815 | 4 | 16416 | 3052 | 4 | EL6021_M180 |  | BITVAL
CVM6002F2 | VEGA BUNKER PLC : HOT WATER VALVE SUPPLY GANTRY FORWARD POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 11 | 13815 | 6 | 16416 | 3052 | 6 | EL6021_M180 |  | BITVAL
CVM6002O2 | VEGA BUNKER PLC : HOT WATER VALVE SUPPLY GANTRY FORWARD POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 12 | 13815 | 8 | 16416 | 3053 | 0 | EL6021_M180 |  | BITVAL
CVM6004F2 | VEGA BUNKER PLC : HOT WATER VALVE RETURN GANTRY FORWARD POSITION CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 13 | 13815 | 10 | 16416 | 3053 | 2 | EL6021_M180 |  | BITVAL
CVM6004O2 | VEGA BUNKER PLC : HOT WATER VALVE RETURN GANTRY FORWARD POSITION OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3032 | 14 | 13815 | 12 | 16416 | 3053 | 4 | EL6021_M180 |  | BITVAL
SPASCR0544 | SPARE SER 0544 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3032 | 15 | 13815 | 14 | 16416 | 3053 | 6 | EL6021_M180 |  | BITVAL
SPASCR0545 | SPARE SER 0545 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 0 | 13816 | 0 | 16416 | 3054 | 0 | EL6021_M180 |  | BITVAL
SPASCR0546 | SPARE SER 0546 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 1 | 13816 | 2 | 16416 | 3054 | 2 | EL6021_M180 |  | BITVAL
SPASCR0547 | SPARE SER 0547 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 2 | 13816 | 4 | 16416 | 3054 | 4 | EL6021_M180 |  | BITVAL
SPASCR0548 | SPARE SER 0548 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 3 | 13816 | 6 | 16416 | 3054 | 6 | EL6021_M180 |  | BITVAL
SPASCR0549 | SPARE SER 0549 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 4 | 13816 | 8 | 16416 | 3055 | 0 | EL6021_M180 |  | BITVAL
SPASCR0550 | SPARE SER 0550 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 5 | 13816 | 10 | 16416 | 3055 | 2 | EL6021_M180 |  | BITVAL
SPASCR1047 | SPARE SER 0551 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3033 | 6 | 13816 | 12 | 16416 | 3055 | 4 | EL6021_M180 |  | BITVAL
CPP6001M | VEGA BUNKER PLC : CHILLER 1 HOT WATER PUMP M01 (PRIMARY) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3033 | 7 | 13816 | 14 | 16416 | 3055 | 6 | EL6021_M180 |  | BITVAL
GPP6001M | VEGA BUNKER PLC : CHILLER 1 COLD WATER PUMP M01 (PRIMARY) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3033 | 8 | 13817 | 0 | 16416 | 3056 | 0 | EL6021_M180 |  | BITVAL
GXV6001M1 | VEGA BUNKER PLC : CHILLER 1 FAN 1 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3033 | 9 | 13817 | 2 | 16416 | 3056 | 2 | EL6021_M180 |  | BITVAL
GXV6001M2 | VEGA BUNKER PLC : CHILLER 1 FAN 2 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3033 | 10 | 13817 | 4 | 16416 | 3056 | 4 | EL6021_M180 |  | BITVAL
GXV6001M3 | VEGA BUNKER PLC : CHILLER 1 FAN 3 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3033 | 11 | 13817 | 6 | 16416 | 3056 | 6 | EL6021_M180 |  | BITVAL
GXV6001M4 | VEGA BUNKER PLC : CHILLER 1 FAN 4 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3033 | 12 | 13817 | 8 | 16416 | 3057 | 0 | EL6021_M180 |  | BITVAL
CPP6002M | VEGA BUNKER PLC : CHILLER 2 HOT WATER PUMP M02 (PRIMARY) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3033 | 13 | 13817 | 10 | 16416 | 3057 | 2 | EL6021_M180 |  | BITVAL
GPP6002M | VEGA BUNKER PLC : CHILLER 2 COLD WATER PUMP M02 (PRIMARY) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3033 | 14 | 13817 | 12 | 16416 | 3057 | 4 | EL6021_M180 |  | BITVAL
GXV6002M1 | VEGA BUNKER PLC : CHILLER 2 FAN 1 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3033 | 15 | 13817 | 14 | 16416 | 3057 | 6 | EL6021_M180 |  | BITVAL
GXV6002M2 | VEGA BUNKER PLC : CHILLER 2 FAN 2 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3034 | 0 | 13818 | 0 | 16416 | 3058 | 0 | EL6021_M180 |  | BITVAL
GXV6002M3 | VEGA BUNKER PLC : CHILLER 2 FAN 3 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3034 | 1 | 13818 | 2 | 16416 | 3058 | 2 | EL6021_M180 |  | BITVAL
GXV6002M4 | VEGA BUNKER PLC : CHILLER 2 FAN 4 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3034 | 2 | 13818 | 4 | 16416 | 3058 | 4 | EL6021_M180 |  | BITVAL
VVU6004O | VEGA BUNKER PLC : DECONTAMINATION ROOM 004 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 3 | 13818 | 6 | 16416 | 3058 | 6 | EL6021_M180 |  | BITVAL
VVU6007O | VEGA BUNKER PLC : DECONTAMINATION ROOM 007 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 4 | 13818 | 8 | 16416 | 3059 | 0 | EL6021_M180 |  | BITVAL
VVU6008O | VEGA BUNKER PLC : DECONTAMINATION ROOM 008 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 5 | 13818 | 10 | 16416 | 3059 | 2 | EL6021_M180 |  | BITVAL
VVU6009O | VEGA BUNKER PLC : DECONTAMINATION ROOM 009 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 6 | 13818 | 12 | 16416 | 3059 | 4 | EL6021_M180 |  | BITVAL
VVU6213O | VEGA BUNKER PLC : DECONTAMINATION ROOMS 002 AND 013 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 7 | 13818 | 14 | 16416 | 3059 | 6 | EL6021_M180 |  | BITVAL
VVU6101O1 | VEGA BUNKER PLC : DECONTAMINATION ROOM 101 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 8 | 13819 | 0 | 16416 | 3060 | 0 | EL6021_M180 |  | BITVAL
VVU6103O | VEGA BUNKER PLC : DECONTAMINATION ROOM 103 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 9 | 13819 | 2 | 16416 | 3060 | 2 | EL6021_M180 |  | BITVAL
VVU6111O | VEGA BUNKER PLC : DECONTAMINATION ROOM 111 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 10 | 13819 | 4 | 16416 | 3060 | 4 | EL6021_M180 |  | BITVAL
VVU6112O | VEGA BUNKER PLC : DECONTAMINATION ROOM 112 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 11 | 13819 | 6 | 16416 | 3060 | 6 | EL6021_M180 |  | BITVAL
VVU6113O | VEGA BUNKER PLC : DECONTAMINATION ROOM 113 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 12 | 13819 | 8 | 16416 | 3061 | 0 | EL6021_M180 |  | BITVAL
VVU6115O | VEGA BUNKER PLC : DECONTAMINATION ROOM 115 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC05;HVAC11 | HVAC |  | 6 |  |  | 3034 | 13 | 13819 | 10 | 16416 | 3061 | 2 | EL6021_M180 |  | BITVAL
VVU6116O | VEGA BUNKER PLC : DECONTAMINATION ROOM 116 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC06;HVAC11 | HVAC |  | 6 |  |  | 3034 | 14 | 13819 | 12 | 16416 | 3061 | 4 | EL6021_M180 |  | BITVAL
CVM6001F | VEGA BUNKER PLC : CHILLER 1 HOT WATER RECOVERY VALVE CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3034 | 15 | 13819 | 14 | 16416 | 3061 | 6 | EL6021_M180 |  | BITVAL
CVM6001O | VEGA BUNKER PLC : CHILLER 1 HOT WATER RECOVERY VALVE OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3035 | 0 | 13820 | 0 | 16416 | 3062 | 0 | EL6021_M180 |  | BITVAL
CVM6002F | VEGA BUNKER PLC : CHILLER 2 HOT WATER RECOVERY VALVE CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3035 | 1 | 13820 | 2 | 16416 | 3062 | 2 | EL6021_M180 |  | BITVAL
CVM6002O | VEGA BUNKER PLC : CHILLER 2 HOT WATER RECOVERY VALVE OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3035 | 2 | 13820 | 4 | 16416 | 3062 | 4 | EL6021_M180 |  | BITVAL
CVM6003F | VEGA BUNKER PLC : CHILLER 3 HOT WATER RECOVERY VALVE CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3035 | 3 | 13820 | 6 | 16416 | 3062 | 6 | EL6021_M180 |  | BITVAL
CVM6003O | VEGA BUNKER PLC : CHILLER 3 HOT WATER RECOVERY VALVE OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3035 | 4 | 13820 | 8 | 16416 | 3063 | 0 | EL6021_M180 |  | BITVAL
SPASCR0551 | SPARE SER 0551 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3035 | 5 | 13820 | 10 | 16416 | 3063 | 2 | EL6021_M180 |  | BITVAL
SPASCR0552 | SPARE SER 0552 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3035 | 6 | 13820 | 12 | 16416 | 3063 | 4 | EL6021_M180 |  | BITVAL
SPASCR0553 | SPARE SER 0553 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 6 |  |  | 3035 | 7 | 13820 | 14 | 16416 | 3063 | 6 | EL6021_M180 |  | BITVAL
SPASCR0554 | SPARE SER 0554 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3035 | 8 | 13821 | 0 | 16416 | 3064 | 0 | EL6021_M180 |  | BITVAL
SPASCR0555 | SPARE SER 0555 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3035 | 9 | 13821 | 2 | 16416 | 3064 | 2 | EL6021_M180 |  | BITVAL
SPASCR0556 | SPARE SER 0556 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3035 | 10 | 13821 | 4 | 16416 | 3064 | 4 | EL6021_M180 |  | BITVAL
SPASCR0557 | SPARE SER 0557 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3035 | 11 | 13821 | 6 | 16416 | 3064 | 6 | EL6021_M180 |  | BITVAL
VCN6002M1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6002DC1 | HVAC07 | HVAC |  | 6 |  |  | 3035 | 12 | 13821 | 8 | 16416 | 3065 | 0 | EL6021_M180 |  | BITVAL
VCN6004M1 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6004DC1 | HVAC07 | HVAC |  | 6 |  |  | 3035 | 13 | 13821 | 10 | 16416 | 3065 | 2 | EL6021_M180 |  | BITVAL
SPASCR0558 | SPARE SER 0558 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3035 | 14 | 13821 | 12 | 16416 | 3065 | 4 | EL6021_M180 |  | BITVAL
SPASCR0559 | SPARE SER 0559 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3035 | 15 | 13821 | 14 | 16416 | 3065 | 6 | EL6021_M180 |  | BITVAL
VVU6126RM1 | VEGA BUNKER PLC : COMMAND IN PROGRESS : STARTING HVAC INSTALLATION | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 0 | 13822 | 0 | 16416 | 3066 | 0 | EL6021_M180 |  | BITVAL
VVU6126RK | VEGA BUNKER PLC : COMMAND IN PROGRESS : OPERATING IN ECO MODE | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 1 | 13822 | 2 | 16416 | 3066 | 2 | EL6021_M180 |  | BITVAL
VVU6126RV | VEGA BUNKER PLC : COMMAND IN PROGRESS : LOCKING CONFIGURATION (D-1) | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 2 | 13822 | 4 | 16416 | 3066 | 4 | EL6021_M180 |  | BITVAL
VCF6126RF | VEGA BUNKER PLC : COMMAND IN PROGRESS : TRIGGERING FIRE DAMPERS | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 3 | 13822 | 6 | 16416 | 3066 | 6 | EL6021_M180 |  | BITVAL
VCF6126RO | VEGA BUNKER PLC : COMMAND IN PROGRESS : RESETTING FIRE DAMPERS | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 4 | 13822 | 8 | 16416 | 3067 | 0 | EL6021_M180 |  | BITVAL
VVU6126RM2 | VEGA BUNKER PLC : COMMAND IN PROGRESS : STARTING INTERNAL HVAC | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 5 | 13822 | 10 | 16416 | 3067 | 2 | EL6021_M180 |  | BITVAL
VRP6126RO1 | VEGA BUNKER PLC : COMMAND IN PROGRESS : OPENNING LOCAL FRESH AIR | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 6 | 13822 | 12 | 16416 | 3067 | 4 | EL6021_M180 |  | BITVAL
VRP6126RO2 | VEGA BUNKER PLC : COMMAND IN PROGRESS : OPENNING DISTANT FRESH AIR | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3036 | 7 | 13822 | 14 | 16416 | 3067 | 6 | EL6021_M180 |  | BITVAL
SPASCR0560 | SPARE SER 0560 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 8 | 13823 | 0 | 16416 | 3068 | 0 | EL6021_M180 |  | BITVAL
SPASCR0561 | SPARE SER 0561 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 9 | 13823 | 2 | 16416 | 3068 | 2 | EL6021_M180 |  | BITVAL
SPASCR0562 | SPARE SER 0562 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 10 | 13823 | 4 | 16416 | 3068 | 4 | EL6021_M180 |  | BITVAL
SPASCR0563 | SPARE SER 0563 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 11 | 13823 | 6 | 16416 | 3068 | 6 | EL6021_M180 |  | BITVAL
SPASCR0564 | SPARE SER 0564 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 12 | 13823 | 8 | 16416 | 3069 | 0 | EL6021_M180 |  | BITVAL
SPASCR0565 | SPARE SER 0565 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 13 | 13823 | 10 | 16416 | 3069 | 2 | EL6021_M180 |  | BITVAL
SPASCR0566 | SPARE SER 0566 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 14 | 13823 | 12 | 16416 | 3069 | 4 | EL6021_M180 |  | BITVAL
SPASCR0567 | SPARE SER 0567 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3036 | 15 | 13823 | 14 | 16416 | 3069 | 6 | EL6021_M180 |  | BITVAL
SPASCR0568 | SPARE SER 0568 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 0 | 13824 | 0 | 16416 | 3070 | 0 | EL6021_M180 |  | BITVAL
SPASCR0569 | SPARE SER 0569 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 1 | 13824 | 2 | 16416 | 3070 | 2 | EL6021_M180 |  | BITVAL
SPASCR0570 | SPARE SER 0570 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 2 | 13824 | 4 | 16416 | 3070 | 4 | EL6021_M180 |  | BITVAL
SPASCR0571 | SPARE SER 0571 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 3 | 13824 | 6 | 16416 | 3070 | 6 | EL6021_M180 |  | BITVAL
SPASCR0572 | SPARE SER 0572 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 4 | 13824 | 8 | 16416 | 3071 | 0 | EL6021_M180 |  | BITVAL
GPP6005M1 | VEGA BUNKER PLC : COLD WATER PUMP M05 (BUNKER) ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3037 | 5 | 13824 | 10 | 16416 | 3071 | 2 | EL6021_M180 |  | BITVAL
GPP6002M2 | VEGA BUNKER PLC : COLD WATER PUMP P02 (GANTRY) ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3037 | 6 | 13824 | 12 | 16416 | 3071 | 4 | EL6021_M180 |  | BITVAL
CPP6005M3 | VEGA BUNKER PLC : HOT WATER PUMP M05 (BUNKER/GANTRY) ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 6 |  |  | 3037 | 7 | 13824 | 14 | 16416 | 3071 | 6 | EL6021_M180 |  | BITVAL
VRP6118O1 | VEGA BUNKER PLC : FRESH AIR MOTORISED DAMPER 118.1 (CTA 2) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3037 | 8 | 13825 | 0 | 16416 | 3072 | 0 | EL6021_M180 |  | BITVAL
VRP6118F1 | VEGA BUNKER PLC : FRESH AIR MOTORISED DAMPER 118.1 (CTA 2) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3037 | 9 | 13825 | 2 | 16416 | 3072 | 2 | EL6021_M180 |  | BITVAL
VRP6118O2 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 118.2 (CTA 2) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC04;HVAC05;HVAC06 | HVAC |  | 6 |  |  | 3037 | 10 | 13825 | 4 | 16416 | 3072 | 4 | EL6021_M180 |  | BITVAL
VRP6118F2 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 118.2 (CTA 2) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC04;HVAC05;HVAC06 | HVAC |  | 6 |  |  | 3037 | 11 | 13825 | 6 | 16416 | 3072 | 6 | EL6021_M180 |  | BITVAL
VCT6002M | VEGA BUNKER PLC : FAN CTA M02 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC04 | HVAC |  | 6 |  |  | 3037 | 12 | 13825 | 8 | 16416 | 3073 | 0 | EL6021_M180 |  | BITVAL
SPASCR0573 | SPARE SER 0573 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 13 | 13825 | 10 | 16416 | 3073 | 2 | EL6021_M180 |  | BITVAL
SPASCR0574 | SPARE SER 0574 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 14 | 13825 | 12 | 16416 | 3073 | 4 | EL6021_M180 |  | BITVAL
SPASCR0575 | SPARE SER 0575 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3037 | 15 | 13825 | 14 | 16416 | 3073 | 6 | EL6021_M180 |  | BITVAL
SPASCR0576 | SPARE SER 0576 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3038 | 0 | 13826 | 0 | 16416 | 3074 | 0 | EL6021_M180 |  | BITVAL
SPASCR0577 | SPARE SER 0577 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3038 | 1 | 13826 | 2 | 16416 | 3074 | 2 | EL6021_M180 |  | BITVAL
VCF6001F1 | VEGA BUNKER PLC : FIRE DAMPER 001.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 2 | 13826 | 4 | 16416 | 3074 | 4 | EL6021_M180 |  | BITVAL
VCF6001O1 | VEGA BUNKER PLC : FIRE DAMPER 001.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 3 | 13826 | 6 | 16416 | 3074 | 6 | EL6021_M180 |  | BITVAL
VCF6012F1 | VEGA BUNKER PLC : FIRE DAMPER 012.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 4 | 13826 | 8 | 16416 | 3075 | 0 | EL6021_M180 |  | BITVAL
VCF6012O1 | VEGA BUNKER PLC : FIRE DAMPER 012.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 5 | 13826 | 10 | 16416 | 3075 | 2 | EL6021_M180 |  | BITVAL
VCF6012F2 | VEGA BUNKER PLC : FIRE DAMPER 012.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 6 | 13826 | 12 | 16416 | 3075 | 4 | EL6021_M180 |  | BITVAL
VCF6012O2 | VEGA BUNKER PLC : FIRE DAMPER 012.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 7 | 13826 | 14 | 16416 | 3075 | 6 | EL6021_M180 |  | BITVAL
VCF6012F3 | VEGA BUNKER PLC : FIRE DAMPER 012.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 8 | 13827 | 0 | 16416 | 3076 | 0 | EL6021_M180 |  | BITVAL
VCF6012O3 | VEGA BUNKER PLC : FIRE DAMPER 012.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 9 | 13827 | 2 | 16416 | 3076 | 2 | EL6021_M180 |  | BITVAL
VCF6003F1 | VEGA BUNKER PLC : FIRE DAMPER 003.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 10 | 13827 | 4 | 16416 | 3076 | 4 | EL6021_M180 |  | BITVAL
VCF6003O1 | VEGA BUNKER PLC : FIRE DAMPER 003.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 11 | 13827 | 6 | 16416 | 3076 | 6 | EL6021_M180 |  | BITVAL
VCF6003F2 | VEGA BUNKER PLC : FIRE DAMPER 003.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 12 | 13827 | 8 | 16416 | 3077 | 0 | EL6021_M180 |  | BITVAL
VCF6003O2 | VEGA BUNKER PLC : FIRE DAMPER 003.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 13 | 13827 | 10 | 16416 | 3077 | 2 | EL6021_M180 |  | BITVAL
VCF6003F3 | VEGA BUNKER PLC : FIRE DAMPER 003.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 14 | 13827 | 12 | 16416 | 3077 | 4 | EL6021_M180 |  | BITVAL
VCF6003O3 | VEGA BUNKER PLC : FIRE DAMPER 003.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3038 | 15 | 13827 | 14 | 16416 | 3077 | 6 | EL6021_M180 |  | BITVAL
VCF6006F1 | VEGA BUNKER PLC : FIRE DAMPER 006.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 0 | 13828 | 0 | 16416 | 3078 | 0 | EL6021_M180 |  | BITVAL
VCF6006O1 | VEGA BUNKER PLC : FIRE DAMPER 006.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 1 | 13828 | 2 | 16416 | 3078 | 2 | EL6021_M180 |  | BITVAL
VCF6006F2 | VEGA BUNKER PLC : FIRE DAMPER 006.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 2 | 13828 | 4 | 16416 | 3078 | 4 | EL6021_M180 |  | BITVAL
VCF6006O2 | VEGA BUNKER PLC : FIRE DAMPER 006.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 3 | 13828 | 6 | 16416 | 3078 | 6 | EL6021_M180 |  | BITVAL
VCF6100F1 | VEGA BUNKER PLC : FIRE DAMPER 100.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 4 | 13828 | 8 | 16416 | 3079 | 0 | EL6021_M180 |  | BITVAL
VCF6100O1 | VEGA BUNKER PLC : FIRE DAMPER 100.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 5 | 13828 | 10 | 16416 | 3079 | 2 | EL6021_M180 |  | BITVAL
VCF6100F2 | VEGA BUNKER PLC : FIRE DAMPER 100.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 6 | 13828 | 12 | 16416 | 3079 | 4 | EL6021_M180 |  | BITVAL
VCF6100O2 | VEGA BUNKER PLC : FIRE DAMPER 100.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 7 | 13828 | 14 | 16416 | 3079 | 6 | EL6021_M180 |  | BITVAL
VCF6108F1 | VEGA BUNKER PLC : FIRE DAMPER 108.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 8 | 13829 | 0 | 16416 | 3080 | 0 | EL6021_M180 |  | BITVAL
VCF6108O1 | VEGA BUNKER PLC : FIRE DAMPER 108.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 9 | 13829 | 2 | 16416 | 3080 | 2 | EL6021_M180 |  | BITVAL
VCF6117F1 | VEGA BUNKER PLC : FIRE DAMPER 117.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 10 | 13829 | 4 | 16416 | 3080 | 4 | EL6021_M180 |  | BITVAL
VCF6117O1 | VEGA BUNKER PLC : FIRE DAMPER 117.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 11 | 13829 | 6 | 16416 | 3080 | 6 | EL6021_M180 |  | BITVAL
VCF6117F2 | VEGA BUNKER PLC : FIRE DAMPER 117.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 12 | 13829 | 8 | 16416 | 3081 | 0 | EL6021_M180 |  | BITVAL
VCF6117O2 | VEGA BUNKER PLC : FIRE DAMPER 117.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 13 | 13829 | 10 | 16416 | 3081 | 2 | EL6021_M180 |  | BITVAL
VCF6126F1 | VEGA BUNKER PLC : FIRE DAMPER 126.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 14 | 13829 | 12 | 16416 | 3081 | 4 | EL6021_M180 |  | BITVAL
VCF6126O1 | VEGA BUNKER PLC : FIRE DAMPER 126.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC10 | HVAC |  | 6 |  |  | 3039 | 15 | 13829 | 14 | 16416 | 3081 | 6 | EL6021_M180 |  | BITVAL
VRP6012F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 012.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 0 | 13830 | 0 | 16416 | 3082 | 0 | EL6021_M180 |  | BITVAL
VRP6012O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 012.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 1 | 13830 | 2 | 16416 | 3082 | 2 | EL6021_M180 |  | BITVAL
VRP6100F2 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 100.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 2 | 13830 | 4 | 16416 | 3082 | 4 | EL6021_M180 |  | BITVAL
VRP6100O2 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 100.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 3 | 13830 | 6 | 16416 | 3082 | 6 | EL6021_M180 |  | BITVAL
VRP6104F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 104.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 4 | 13830 | 8 | 16416 | 3083 | 0 | EL6021_M180 |  | BITVAL
VRP6104O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 104.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 5 | 13830 | 10 | 16416 | 3083 | 2 | EL6021_M180 |  | BITVAL
VRP6107F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 107.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 6 | 13830 | 12 | 16416 | 3083 | 4 | EL6021_M180 |  | BITVAL
VRP6107O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 107.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 7 | 13830 | 14 | 16416 | 3083 | 6 | EL6021_M180 |  | BITVAL
VRP6117F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 117.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 8 | 13831 | 0 | 16416 | 3084 | 0 | EL6021_M180 |  | BITVAL
VRP6117O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 117.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 9 | 13831 | 2 | 16416 | 3084 | 2 | EL6021_M180 |  | BITVAL
VRP6012F2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 012.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 10 | 13831 | 4 | 16416 | 3084 | 4 | EL6021_M180 |  | BITVAL
VRP6012O2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 012.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 11 | 13831 | 6 | 16416 | 3084 | 6 | EL6021_M180 |  | BITVAL
VRP6104F2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 104.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 12 | 13831 | 8 | 16416 | 3085 | 0 | EL6021_M180 |  | BITVAL
VRP6104O2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 104.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 13 | 13831 | 10 | 16416 | 3085 | 2 | EL6021_M180 |  | BITVAL
VRP6107F2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 107.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 14 | 13831 | 12 | 16416 | 3085 | 4 | EL6021_M180 |  | BITVAL
VRP6107O2 | VEGA BUNKER PLC : EXTRACT AIR MOTORISED DAMPER 107.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC06 | HVAC |  | 6 |  |  | 3040 | 15 | 13831 | 14 | 16416 | 3085 | 6 | EL6021_M180 |  | BITVAL
SPASCR0578 | SPARE SER 0578 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 0 | 13832 | 0 | 16416 | 3086 | 0 | EL6021_M180 |  | BITVAL
SPASCR0579 | SPARE SER 0579 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 1 | 13832 | 2 | 16416 | 3086 | 2 | EL6021_M180 |  | BITVAL
CPP6003M | VEGA BUNKER PLC : CHILLER 3 HOT WATER PUMP M03 (PRIMARY) ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | GGF6003DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3041 | 2 | 13832 | 4 | 16416 | 3086 | 4 | EL6021_M180 |  | BITVAL
GPP6003M | VEGA BUNKER PLC : CHILLER 3 COLD WATER PUMP M03 (PRIMARY) ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | GGF6003DC | Details Groupes Froids (HVAC03);HVAC03;HVAC07;HVAC08;HVAC09;HVAC18 | HVAC |  | 6 |  |  | 3041 | 3 | 13832 | 6 | 16416 | 3086 | 6 | EL6021_M180 |  | BITVAL
GXV6003M1 | VEGA BUNKER PLC : CHILLER 3 FAN 1 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | GGF6003DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3041 | 4 | 13832 | 8 | 16416 | 3087 | 0 | EL6021_M180 |  | BITVAL
GXV6003M2 | VEGA BUNKER PLC : CHILLER 3 FAN 2 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | GGF6003DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3041 | 5 | 13832 | 10 | 16416 | 3087 | 2 | EL6021_M180 |  | BITVAL
GXV6003M3 | VEGA BUNKER PLC : CHILLER 3 FAN 3 DRY COOLER ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | GGF6003DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3041 | 6 | 13832 | 12 | 16416 | 3087 | 4 | EL6021_M180 |  | BITVAL
SPASCR0580 | SPARE SER 0580 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 7 | 13832 | 14 | 16416 | 3087 | 6 | EL6021_M180 |  | BITVAL
SPASCR0581 | SPARE SER 0581 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 8 | 13833 | 0 | 16416 | 3088 | 0 | EL6021_M180 |  | BITVAL
VCN6007M1 | VEGA BUNKER PLC : AC CABINET (STULTZ) 007.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6007DC1 | HVAC07 | HVAC |  | 6 |  |  | 3041 | 9 | 13833 | 2 | 16416 | 3088 | 2 | EL6021_M180 |  | BITVAL
VCN6007M2 | VEGA BUNKER PLC : AC CABINET (STULTZ) 007.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6007DC2 | HVAC07 | HVAC |  | 6 |  |  | 3041 | 10 | 13833 | 4 | 16416 | 3088 | 4 | EL6021_M180 |  | BITVAL
VCN6013M1 | VEGA BUNKER PLC : AC CABINET (STULTZ) 013.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6013DC1 | HVAC07 | HVAC |  | 6 |  |  | 3041 | 11 | 13833 | 6 | 16416 | 3088 | 6 | EL6021_M180 |  | BITVAL
SPASCR0582 | SPARE SER 0582 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 12 | 13833 | 8 | 16416 | 3089 | 0 | EL6021_M180 |  | BITVAL
SPASCR0583 | SPARE SER 0583 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 13 | 13833 | 10 | 16416 | 3089 | 2 | EL6021_M180 |  | BITVAL
SPASCR0584 | SPARE SER 0584 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 14 | 13833 | 12 | 16416 | 3089 | 4 | EL6021_M180 |  | BITVAL
SPASCR0585 | SPARE SER 0585 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3041 | 15 | 13833 | 14 | 16416 | 3089 | 6 | EL6021_M180 |  | BITVAL
SPASCR0586 | SPARE SER 0586 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3042 | 0 | 13834 | 0 | 16416 | 3090 | 0 | EL6021_M180 |  | BITVAL
SPASCR0587 | SPARE SER 0587 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3042 | 1 | 13834 | 2 | 16416 | 3090 | 2 | EL6021_M180 |  | BITVAL
VCN6002M2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 002.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6002DC2 | HVAC07 | HVAC |  | 6 |  |  | 3042 | 2 | 13834 | 4 | 16416 | 3090 | 4 | EL6021_M180 |  | BITVAL
VRP6002F1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 002.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3042 | 3 | 13834 | 6 | 16416 | 3090 | 6 | EL6021_M180 |  | BITVAL
VRP6002O1 | VEGA BUNKER PLC : PULSE AIR MOTORISED DAMPER 002.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC05 | HVAC |  | 6 |  |  | 3042 | 4 | 13834 | 8 | 16416 | 3091 | 0 | EL6021_M180 |  | BITVAL
VCN6004M2 | VEGA BUNKER PLC : AC CABINET (SCHNEIDER) 004.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6004DC2 | HVAC07 | HVAC |  | 6 |  |  | 3042 | 5 | 13834 | 10 | 16416 | 3091 | 2 | EL6021_M180 |  | BITVAL
VCN6101M1 | VEGA BUNKER PLC : AC CABINET (STULTZ) 101.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6101DC1 | HVAC07 | HVAC |  | 6 |  |  | 3042 | 6 | 13834 | 12 | 16416 | 3091 | 4 | EL6021_M180 |  | BITVAL
VCN6101M2 | VEGA BUNKER PLC : AC CABINET (STULTZ) 101.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6101DC2 | HVAC07 | HVAC |  | 6 |  |  | 3042 | 7 | 13834 | 14 | 16416 | 3091 | 6 | EL6021_M180 |  | BITVAL
VCN6103M1 | VEGA BUNKER PLC : AC CABINET (STULTZ) 103.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6103DC1 | HVAC07 | HVAC |  | 6 |  |  | 3042 | 8 | 13835 | 0 | 16416 | 3092 | 0 | EL6021_M180 |  | BITVAL
VCN6103M2 | VEGA BUNKER PLC : AC CABINET (STULTZ) 103.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6103DC2 | HVAC07 | HVAC |  | 6 |  |  | 3042 | 9 | 13835 | 2 | 16416 | 3092 | 2 | EL6021_M180 |  | BITVAL
VCN6113M1 | VEGA BUNKER PLC : AC CABINET (STULTZ) 113.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6113DC1 | HVAC08 | HVAC |  | 6 |  |  | 3042 | 10 | 13835 | 4 | 16416 | 3092 | 4 | EL6021_M180 |  | BITVAL
VCN6113M2 | VEGA BUNKER PLC : AC CABINET (STULTZ) 113.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6113DC2 | HVAC08 | HVAC |  | 6 |  |  | 3042 | 11 | 13835 | 6 | 16416 | 3092 | 6 | EL6021_M180 |  | BITVAL
VCN6116M1 | VEGA BUNKER PLC : AC CABINET (STULTZ) 116.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6116DC1 | HVAC08 | HVAC |  | 6 |  |  | 3042 | 12 | 13835 | 8 | 16416 | 3093 | 0 | EL6021_M180 |  | BITVAL
VCN6116M2 | VEGA BUNKER PLC : AC CABINET (STULTZ) 116.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VCN6116DC2 | HVAC08 | HVAC |  | 6 |  |  | 3042 | 13 | 13835 | 10 | 16416 | 3093 | 2 | EL6021_M180 |  | BITVAL
SPASCR0588 | SPARE SER 0588 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3042 | 14 | 13835 | 12 | 16416 | 3093 | 4 | EL6021_M180 |  | BITVAL
SPASCR0589 | SPARE SER 0589 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3042 | 15 | 13835 | 14 | 16416 | 3093 | 6 | EL6021_M180 |  | BITVAL
VZC6126J11 | VEGA BUNKER PLC X80-1 : RUN PRIMARY | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01);HVAC01 | HVAC |  | 6 |  |  | 3043 | 0 | 13836 | 0 | 16416 | 3094 | 0 | EL6021_M180 |  | BITVAL
VZC6126J12 | VEGA BUNKER PLC X80-1 : RUN SECONDARY | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01);HVAC01 | HVAC |  | 6 |  |  | 3043 | 1 | 13836 | 2 | 16416 | 3094 | 2 | EL6021_M180 |  | BITVAL
VZC6126J21 | VEGA BUNKER PLC X80-2 : RUN PRIMARY | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01);HVAC01 | HVAC |  | 6 |  |  | 3043 | 2 | 13836 | 4 | 16416 | 3094 | 4 | EL6021_M180 |  | BITVAL
VZC6126J22 | VEGA BUNKER PLC X80-2 : RUN SECONDARY | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01);HVAC01 | HVAC |  | 6 |  |  | 3043 | 3 | 13836 | 6 | 16416 | 3094 | 6 | EL6021_M180 |  | BITVAL
SPASCR0590 | SPARE SER 0590 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 4 | 13836 | 8 | 16416 | 3095 | 0 | EL6021_M180 |  | BITVAL
SPASCR0591 | SPARE SER 0591 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 5 | 13836 | 10 | 16416 | 3095 | 2 | EL6021_M180 |  | BITVAL
SPASCR0592 | SPARE SER 0592 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 6 | 13836 | 12 | 16416 | 3095 | 4 | EL6021_M180 |  | BITVAL
SPASCR0593 | SPARE SER 0593 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 7 | 13836 | 14 | 16416 | 3095 | 6 | EL6021_M180 |  | BITVAL
SPASCR0594 | SPARE SER 0594 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 8 | 13837 | 0 | 16416 | 3096 | 0 | EL6021_M180 |  | BITVAL
SPASCR0595 | SPARE SER 0595 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 9 | 13837 | 2 | 16416 | 3096 | 2 | EL6021_M180 |  | BITVAL
SPASCR0596 | SPARE SER 0596 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 10 | 13837 | 4 | 16416 | 3096 | 4 | EL6021_M180 |  | BITVAL
SPASCR0597 | SPARE SER 0597 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 11 | 13837 | 6 | 16416 | 3096 | 6 | EL6021_M180 |  | BITVAL
SPASCR0598 | SPARE SER 0598 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 12 | 13837 | 8 | 16416 | 3097 | 0 | EL6021_M180 |  | BITVAL
SPASCR0599 | SPARE SER 0599 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 13 | 13837 | 10 | 16416 | 3097 | 2 | EL6021_M180 |  | BITVAL
SPASCR0600 | SPARE SER 0600 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 14 | 13837 | 12 | 16416 | 3097 | 4 | EL6021_M180 |  | BITVAL
SPASCR0601 | SPARE SER 0601 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3043 | 15 | 13837 | 14 | 16416 | 3097 | 6 | EL6021_M180 |  | BITVAL
SPASCR0602 | SPARE SER 0602 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 0 | 13838 | 0 | 16416 | 3098 | 0 | EL6021_M180 |  | BITVAL
SPASCR0603 | SPARE SER 0603 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 1 | 13838 | 2 | 16416 | 3098 | 2 | EL6021_M180 |  | BITVAL
SPASCR0604 | SPARE SER 0604 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 2 | 13838 | 4 | 16416 | 3098 | 4 | EL6021_M180 |  | BITVAL
SPASCR0605 | SPARE SER 0605 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 3 | 13838 | 6 | 16416 | 3098 | 6 | EL6021_M180 |  | BITVAL
SPASCR0606 | SPARE SER 0606 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 4 | 13838 | 8 | 16416 | 3099 | 0 | EL6021_M180 |  | BITVAL
SPASCR0607 | SPARE SER 0607 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 5 | 13838 | 10 | 16416 | 3099 | 2 | EL6021_M180 |  | BITVAL
SPASCR0608 | SPARE SER 0608 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 6 | 13838 | 12 | 16416 | 3099 | 4 | EL6021_M180 |  | BITVAL
SPASCR0609 | SPARE SER 0609 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 7 | 13838 | 14 | 16416 | 3099 | 6 | EL6021_M180 |  | BITVAL
SPASCR0610 | SPARE SER 0610 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 8 | 13839 | 0 | 16416 | 3100 | 0 | EL6021_M180 |  | BITVAL
SPASCR0611 | SPARE SER 0611 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 9 | 13839 | 2 | 16416 | 3100 | 2 | EL6021_M180 |  | BITVAL
SPASCR0612 | SPARE SER 0612 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 10 | 13839 | 4 | 16416 | 3100 | 4 | EL6021_M180 |  | BITVAL
SPASCR0613 | SPARE SER 0613 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 11 | 13839 | 6 | 16416 | 3100 | 6 | EL6021_M180 |  | BITVAL
SPASCR0614 | SPARE SER 0614 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 12 | 13839 | 8 | 16416 | 3101 | 0 | EL6021_M180 |  | BITVAL
SPASCR0615 | SPARE SER 0615 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 13 | 13839 | 10 | 16416 | 3101 | 2 | EL6021_M180 |  | BITVAL
SPASCR0616 | SPARE SER 0616 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 14 | 13839 | 12 | 16416 | 3101 | 4 | EL6021_M180 |  | BITVAL
SPASCR0617 | SPARE SER 0617 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3044 | 15 | 13839 | 14 | 16416 | 3101 | 6 | EL6021_M180 |  | BITVAL
VVU6126K1 | VEGA BUNKER PLC : HVAC INSTALLATION MODE OPE OK | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3045 | 0 | 13840 | 0 | 16416 | 3102 | 0 | EL6021_M180 |  | BITVAL
VVU6126K2 | VEGA BUNKER PLC : HVAC INSTALLATION MODE ECO OK | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3045 | 1 | 13840 | 2 | 16416 | 3102 | 2 | EL6021_M180 |  | BITVAL
VVU6126M2 | VEGA BUNKER PLC : INTERNAL HVAC ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3045 | 2 | 13840 | 4 | 16416 | 3102 | 4 | EL6021_M180 |  | BITVAL
VVU6127M2 | VEGA BUNKER PLC : DISTANT FRESH AIR ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D |  |  |  | 6 |  |  | 3045 | 3 | 13840 | 6 | 16416 | 3102 | 6 | EL6021_M180 |  | BITVAL
VVU6106M | VEGA BUNKER PLC : INTERNAL HVAC (ROOM 106 : RELOCATION) ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 | VZC6126D | HVAC12 | HVAC |  | 6 |  |  | 3045 | 4 | 13840 | 8 | 16416 | 3103 | 0 | EL6021_M180 |  | BITVAL
VVU6126K3 | VEGA BUNKER PLC : HVAC INSTALLATION READY FOR GANTRY TRANSFER | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12;HVAC17 | HVAC |  | 6 |  |  | 3045 | 5 | 13840 | 10 | 16416 | 3103 | 2 | EL6021_M180 |  | BITVAL
VVU6126K4 | VEGA BUNKER PLC : HVAC INSTALLATION READY FOR LAUNCH | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6126D | HVAC12;HVAC17 | HVAC |  | 6 |  |  | 3045 | 6 | 13840 | 12 | 16416 | 3103 | 4 | EL6021_M180 |  | BITVAL
SPASCR0618 | SPARE SER 0618 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 7 | 13840 | 14 | 16416 | 3103 | 6 | EL6021_M180 |  | BITVAL
SPASCR0619 | SPARE SER 0619 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 8 | 13841 | 0 | 16416 | 3104 | 0 | EL6021_M180 |  | BITVAL
SPASCR0620 | SPARE SER 0620 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 9 | 13841 | 2 | 16416 | 3104 | 2 | EL6021_M180 |  | BITVAL
SPASCR0621 | SPARE SER 0621 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 10 | 13841 | 4 | 16416 | 3104 | 4 | EL6021_M180 |  | BITVAL
SPASCR0622 | SPARE SER 0622 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 11 | 13841 | 6 | 16416 | 3104 | 6 | EL6021_M180 |  | BITVAL
SPASCR0623 | SPARE SER 0623 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 12 | 13841 | 8 | 16416 | 3105 | 0 | EL6021_M180 |  | BITVAL
SPASCR0624 | SPARE SER 0624 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 13 | 13841 | 10 | 16416 | 3105 | 2 | EL6021_M180 |  | BITVAL
SPASCR0625 | SPARE SER 0625 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 14 | 13841 | 12 | 16416 | 3105 | 4 | EL6021_M180 |  | BITVAL
SPASCR0626 | SPARE SER 0626 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3045 | 15 | 13841 | 14 | 16416 | 3105 | 6 | EL6021_M180 |  | BITVAL
VVV6100M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 100.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3046 | 0 | 13842 | 0 | 16416 | 3106 | 0 | EL6021_M180 |  | BITVAL
VVV6002M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 002.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3046 | 1 | 13842 | 2 | 16416 | 3106 | 2 | EL6021_M180 |  | BITVAL
VVV6106M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3046 | 2 | 13842 | 4 | 16416 | 3106 | 4 | EL6021_M180 |  | BITVAL
VVV6004M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 004.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3046 | 3 | 13842 | 6 | 16416 | 3106 | 6 | EL6021_M180 |  | BITVAL
VVV6105M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 105.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3046 | 4 | 13842 | 8 | 16416 | 3107 | 0 | EL6021_M180 |  | BITVAL
VVV6106M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3046 | 5 | 13842 | 10 | 16416 | 3107 | 2 | EL6021_M180 |  | BITVAL
VVV6006M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 006.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3046 | 6 | 13842 | 12 | 16416 | 3107 | 4 | EL6021_M180 |  | BITVAL
VVV6108M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 108.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3046 | 7 | 13842 | 14 | 16416 | 3107 | 6 | EL6021_M180 |  | BITVAL
VVV6122M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 122.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3046 | 8 | 13843 | 0 | 16416 | 3108 | 0 | EL6021_M180 |  | BITVAL
VVV6115M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3046 | 9 | 13843 | 2 | 16416 | 3108 | 2 | EL6021_M180 |  | BITVAL
VVV6117M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 117.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3046 | 10 | 13843 | 4 | 16416 | 3108 | 4 | EL6021_M180 |  | BITVAL
VVV6115M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3046 | 11 | 13843 | 6 | 16416 | 3108 | 6 | EL6021_M180 |  | BITVAL
VVV6120M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 120.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3046 | 12 | 13843 | 8 | 16416 | 3109 | 0 | EL6021_M180 |  | BITVAL
VVV6121M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 121.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3046 | 13 | 13843 | 10 | 16416 | 3109 | 2 | EL6021_M180 |  | BITVAL
VVV6012M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 012.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3046 | 14 | 13843 | 12 | 16416 | 3109 | 4 | EL6021_M180 |  | BITVAL
VVV6126M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 126.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3046 | 15 | 13843 | 14 | 16416 | 3109 | 6 | EL6021_M180 |  | BITVAL
VVV6118M5 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.5 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 0 | 13844 | 0 | 16416 | 3110 | 0 | EL6021_M180 |  | BITVAL
VVV6118M4 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.4 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 1 | 13844 | 2 | 16416 | 3110 | 2 | EL6021_M180 |  | BITVAL
VVV6118M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 2 | 13844 | 4 | 16416 | 3110 | 4 | EL6021_M180 |  | BITVAL
VVV6121M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 121.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3047 | 3 | 13844 | 6 | 16416 | 3110 | 6 | EL6021_M180 |  | BITVAL
VVV6118M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 4 | 13844 | 8 | 16416 | 3111 | 0 | EL6021_M180 |  | BITVAL
VVV6118M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 118.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 5 | 13844 | 10 | 16416 | 3111 | 2 | EL6021_M180 |  | BITVAL
VVV6115M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 6 | 13844 | 12 | 16416 | 3111 | 4 | EL6021_M180 |  | BITVAL
VVV6115M4 | VEGA BUNKER PLC : FAN COIL (AERMEC) 115.4 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 7 | 13844 | 14 | 16416 | 3111 | 6 | EL6021_M180 |  | BITVAL
VVV6117M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 117.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 8 | 13845 | 0 | 16416 | 3112 | 0 | EL6021_M180 |  | BITVAL
VVV6112M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 112.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 9 | 13845 | 2 | 16416 | 3112 | 2 | EL6021_M180 |  | BITVAL
VVV6111M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 111.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 10 | 13845 | 4 | 16416 | 3112 | 4 | EL6021_M180 |  | BITVAL
VVV6108M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 108.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 11 | 13845 | 6 | 16416 | 3112 | 6 | EL6021_M180 |  | BITVAL
VVV6108M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 108.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 12 | 13845 | 8 | 16416 | 3113 | 0 | EL6021_M180 |  | BITVAL
VVV6107M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 107.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 13 | 13845 | 10 | 16416 | 3113 | 2 | EL6021_M180 |  | BITVAL
VVV6106M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 14 | 13845 | 12 | 16416 | 3113 | 4 | EL6021_M180 |  | BITVAL
VVV6106M4 | VEGA BUNKER PLC : FAN COIL (AERMEC) 106.4 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3047 | 15 | 13845 | 14 | 16416 | 3113 | 6 | EL6021_M180 |  | BITVAL
VVV6105M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 105.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 0 | 13846 | 0 | 16416 | 3114 | 0 | EL6021_M180 |  | BITVAL
VVV6121M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 121.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC09 | HVAC |  | 6 |  |  | 3048 | 1 | 13846 | 2 | 16416 | 3114 | 2 | EL6021_M180 |  | BITVAL
VVV6104M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 104.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 2 | 13846 | 4 | 16416 | 3114 | 4 | EL6021_M180 |  | BITVAL
VVV6100M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 100.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 3 | 13846 | 6 | 16416 | 3114 | 6 | EL6021_M180 |  | BITVAL
VVV6012M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 012.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 4 | 13846 | 8 | 16416 | 3115 | 0 | EL6021_M180 |  | BITVAL
VVV6004M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 004.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 5 | 13846 | 10 | 16416 | 3115 | 2 | EL6021_M180 |  | BITVAL
VVV6006M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 006.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 6 | 13846 | 12 | 16416 | 3115 | 4 | EL6021_M180 |  | BITVAL
VVV6006M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 006.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 7 | 13846 | 14 | 16416 | 3115 | 6 | EL6021_M180 |  | BITVAL
VVV6004M3 | VEGA BUNKER PLC : FAN COIL (AERMEC) 004.3 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 8 | 13847 | 0 | 16416 | 3116 | 0 | EL6021_M180 |  | BITVAL
VVV6002M2 | VEGA BUNKER PLC : FAN COIL (AERMEC) 002.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 9 | 13847 | 2 | 16416 | 3116 | 2 | EL6021_M180 |  | BITVAL
VVV6001M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 001.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 10 | 13847 | 4 | 16416 | 3116 | 4 | EL6021_M180 |  | BITVAL
VVV6008M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 008.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 11 | 13847 | 6 | 16416 | 3116 | 6 | EL6021_M180 |  | BITVAL
VVV6009M1 | VEGA BUNKER PLC : FAN COIL (AERMEC) 009.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3048 | 12 | 13847 | 8 | 16416 | 3117 | 0 | EL6021_M180 |  | BITVAL
SPASCR0627 | SPARE SER 0627 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3048 | 13 | 13847 | 10 | 16416 | 3117 | 2 | EL6021_M180 |  | BITVAL
SPASCR0628 | SPARE SER 0628 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3048 | 14 | 13847 | 12 | 16416 | 3117 | 4 | EL6021_M180 |  | BITVAL
SPASCR0629 | SPARE SER 0629 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3048 | 15 | 13847 | 14 | 16416 | 3117 | 6 | EL6021_M180 |  | BITVAL
SPASCR0711 | SPARE SER 0711 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3002 | 9 | 14127 | 2 | 16416 | 3676 | 2 | EL6021_M181 |  | BITVAL
SPASCR0712 | SPARE SER 0712 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 2 | 14130 | 4 | 16416 | 3682 | 4 | EL6021_M181 |  | BITVAL
SPASCR0713 | SPARE SER 0713 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 3 | 14130 | 6 | 16416 | 3682 | 6 | EL6021_M181 |  | BITVAL
SPASCR0714 | SPARE SER 0714 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 5 | 14130 | 10 | 16416 | 3683 | 2 | EL6021_M181 |  | BITVAL
SPASCR0715 | SPARE SER 0715 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 6 | 14130 | 12 | 16416 | 3683 | 4 | EL6021_M181 |  | BITVAL
SPASCR0716 | SPARE SER 0716 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 10 | 14131 | 4 | 16416 | 3684 | 4 | EL6021_M181 |  | BITVAL
SPASCR1048 | SPARE SER 0717 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 11 | 14131 | 6 | 16416 | 3684 | 6 | EL6021_M181 |  | BITVAL
SPASCR0717 | SPARE SER 0717 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3004 | 15 | 14131 | 14 | 16416 | 3685 | 6 | EL6021_M181 |  | BITVAL
SPASCR0718 | SPARE SER 0718 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 4 | 14132 | 8 | 16416 | 3687 | 0 | EL6021_M181 |  | BITVAL
SPASCR0719 | SPARE SER 0719 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 5 | 14132 | 10 | 16416 | 3687 | 2 | EL6021_M181 |  | BITVAL
SPASCR0720 | SPARE SER 0720 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 6 | 14132 | 12 | 16416 | 3687 | 4 | EL6021_M181 |  | BITVAL
SPASCR0721 | SPARE SER 0721 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 7 | 14132 | 14 | 16416 | 3687 | 6 | EL6021_M181 |  | BITVAL
SPASCR0722 | SPARE SER 0722 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 12 | 14133 | 8 | 16416 | 3689 | 0 | EL6021_M181 |  | BITVAL
SPASCR0723 | SPARE SER 0723 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 13 | 14133 | 10 | 16416 | 3689 | 2 | EL6021_M181 |  | BITVAL
SPASCR0724 | SPARE SER 0724 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 14 | 14133 | 12 | 16416 | 3689 | 4 | EL6021_M181 |  | BITVAL
SPASCR0725 | SPARE SER 0725 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3005 | 15 | 14133 | 14 | 16416 | 3689 | 6 | EL6021_M181 |  | BITVAL
SPASCR0726 | SPARE SER 0726 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 3 | 14134 | 6 | 16416 | 3690 | 6 | EL6021_M181 |  | BITVAL
SPASCR0727 | SPARE SER 0727 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 8 | 14135 | 0 | 16416 | 3692 | 0 | EL6021_M181 |  | BITVAL
SPASCR0728 | SPARE SER 0728 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 9 | 14135 | 2 | 16416 | 3692 | 2 | EL6021_M181 |  | BITVAL
SPASCR0729 | SPARE SER 0729 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 10 | 14135 | 4 | 16416 | 3692 | 4 | EL6021_M181 |  | BITVAL
SPASCR0730 | SPARE SER 0730 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 11 | 14135 | 6 | 16416 | 3692 | 6 | EL6021_M181 |  | BITVAL
SPASCR0731 | SPARE SER 0731 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 12 | 14135 | 8 | 16416 | 3693 | 0 | EL6021_M181 |  | BITVAL
SPASCR0732 | SPARE SER 0732 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 13 | 14135 | 10 | 16416 | 3693 | 2 | EL6021_M181 |  | BITVAL
SPASCR0733 | SPARE SER 0733 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 14 | 14135 | 12 | 16416 | 3693 | 4 | EL6021_M181 |  | BITVAL
SPASCR0734 | SPARE SER 0734 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3006 | 15 | 14135 | 14 | 16416 | 3693 | 6 | EL6021_M181 |  | BITVAL
SPASCR0735 | SPARE SER 0735 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 4 | 14136 | 8 | 16416 | 3695 | 0 | EL6021_M181 |  | BITVAL
SPASCR0736 | SPARE SER 0736 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 5 | 14136 | 10 | 16416 | 3695 | 2 | EL6021_M181 |  | BITVAL
SPASCR0737 | SPARE SER 0737 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 6 | 14136 | 12 | 16416 | 3695 | 4 | EL6021_M181 |  | BITVAL
SPASCR0738 | SPARE SER 0738 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 7 | 14136 | 14 | 16416 | 3695 | 6 | EL6021_M181 |  | BITVAL
SPASCR0739 | SPARE SER 0739 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 8 | 14137 | 0 | 16416 | 3696 | 0 | EL6021_M181 |  | BITVAL
SPASCR0740 | SPARE SER 0740 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 11 | 14137 | 6 | 16416 | 3696 | 6 | EL6021_M181 |  | BITVAL
SPASCR0741 | SPARE SER 0741 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 12 | 14137 | 8 | 16416 | 3697 | 0 | EL6021_M181 |  | BITVAL
SPASCR0742 | SPARE SER 0742 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 13 | 14137 | 10 | 16416 | 3697 | 2 | EL6021_M181 |  | BITVAL
SPASCR0743 | SPARE SER 0743 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 14 | 14137 | 12 | 16416 | 3697 | 4 | EL6021_M181 |  | BITVAL
SPASCR0744 | SPARE SER 0744 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3007 | 15 | 14137 | 14 | 16416 | 3697 | 6 | EL6021_M181 |  | BITVAL
SPASCR0745 | SPARE SER 0745 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 3 | 14138 | 6 | 16416 | 3698 | 6 | EL6021_M181 |  | BITVAL
SPASCR0746 | SPARE SER 0746 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 7 | 14138 | 14 | 16416 | 3699 | 6 | EL6021_M181 |  | BITVAL
SPASCR0747 | SPARE SER 0747 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 11 | 14139 | 6 | 16416 | 3700 | 6 | EL6021_M181 |  | BITVAL
SPASCR0748 | SPARE SER 0748 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 12 | 14139 | 8 | 16416 | 3701 | 0 | EL6021_M181 |  | BITVAL
SPASCR0749 | SPARE SER 0749 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 13 | 14139 | 10 | 16416 | 3701 | 2 | EL6021_M181 |  | BITVAL
SPASCR0750 | SPARE SER 0750 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 14 | 14139 | 12 | 16416 | 3701 | 4 | EL6021_M181 |  | BITVAL
SPASCR0751 | SPARE SER 0751 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3008 | 15 | 14139 | 14 | 16416 | 3701 | 6 | EL6021_M181 |  | BITVAL
SPASCR0752 | SPARE SER 0752 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 5 | 14140 | 10 | 16416 | 3703 | 2 | EL6021_M181 |  | BITVAL
SPASCR0753 | SPARE SER 0753 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 6 | 14140 | 12 | 16416 | 3703 | 4 | EL6021_M181 |  | BITVAL
SPASCR0754 | SPARE SER 0754 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 7 | 14140 | 14 | 16416 | 3703 | 6 | EL6021_M181 |  | BITVAL
SPASCR0755 | SPARE SER 0755 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 8 | 14141 | 0 | 16416 | 3704 | 0 | EL6021_M181 |  | BITVAL
SPASCR0756 | SPARE SER 0756 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 9 | 14141 | 2 | 16416 | 3704 | 2 | EL6021_M181 |  | BITVAL
SPASCR0757 | SPARE SER 0757 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 10 | 14141 | 4 | 16416 | 3704 | 4 | EL6021_M181 |  | BITVAL
SPASCR0758 | SPARE SER 0758 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 11 | 14141 | 6 | 16416 | 3704 | 6 | EL6021_M181 |  | BITVAL
SPASCR0759 | SPARE SER 0759 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 12 | 14141 | 8 | 16416 | 3705 | 0 | EL6021_M181 |  | BITVAL
SPASCR0760 | SPARE SER 0760 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 13 | 14141 | 10 | 16416 | 3705 | 2 | EL6021_M181 |  | BITVAL
SPASCR0761 | SPARE SER 0761 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 14 | 14141 | 12 | 16416 | 3705 | 4 | EL6021_M181 |  | BITVAL
SPASCR0762 | SPARE SER 0762 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3009 | 15 | 14141 | 14 | 16416 | 3705 | 6 | EL6021_M181 |  | BITVAL
SPASCR0763 | SPARE SER 0763 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3011 | 9 | 14144 | 2 | 16416 | 3710 | 2 | EL6021_M181 |  | BITVAL
SPASCR0764 | SPARE SER 0764 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3011 | 10 | 14144 | 4 | 16416 | 3710 | 4 | EL6021_M181 |  | BITVAL
SPASCR0765 | SPARE SER 0765 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3011 | 11 | 14144 | 6 | 16416 | 3710 | 6 | EL6021_M181 |  | BITVAL
SPASCR0766 | SPARE SER 0766 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3012 | 2 | 14145 | 4 | 16416 | 3712 | 4 | EL6021_M181 |  | BITVAL
SPASCR0767 | SPARE SER 0767 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3012 | 3 | 14145 | 6 | 16416 | 3712 | 6 | EL6021_M181 |  | BITVAL
SPASCR0768 | SPARE SER 0768 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3012 | 12 | 14146 | 8 | 16416 | 3715 | 0 | EL6021_M181 |  | BITVAL
SPASCR0769 | SPARE SER 0769 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3012 | 13 | 14146 | 10 | 16416 | 3715 | 2 | EL6021_M181 |  | BITVAL
SPASCR0770 | SPARE SER 0770 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3012 | 14 | 14146 | 12 | 16416 | 3715 | 4 | EL6021_M181 |  | BITVAL
SPASCR0771 | SPARE SER 0771 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3012 | 15 | 14146 | 14 | 16416 | 3715 | 6 | EL6021_M181 |  | BITVAL
SPASCR0772 | SPARE SER 0772 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 1 | 14147 | 2 | 16416 | 3716 | 2 | EL6021_M181 |  | BITVAL
SPASCR0773 | SPARE SER 0773 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 2 | 14147 | 4 | 16416 | 3716 | 4 | EL6021_M181 |  | BITVAL
SPASCR0774 | SPARE SER 0774 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 3 | 14147 | 6 | 16416 | 3716 | 6 | EL6021_M181 |  | BITVAL
SPASCR0775 | SPARE SER 0775 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 4 | 14147 | 8 | 16416 | 3717 | 0 | EL6021_M181 |  | BITVAL
SPASCR0776 | SPARE SER 0776 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 5 | 14147 | 10 | 16416 | 3717 | 2 | EL6021_M181 |  | BITVAL
SPASCR0777 | SPARE SER 0777 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 6 | 14147 | 12 | 16416 | 3717 | 4 | EL6021_M181 |  | BITVAL
SPASCR0778 | SPARE SER 0778 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 7 | 14147 | 14 | 16416 | 3717 | 6 | EL6021_M181 |  | BITVAL
SPASCR0779 | SPARE SER 0779 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 8 | 14148 | 0 | 16416 | 3718 | 0 | EL6021_M181 |  | BITVAL
SPASCR0780 | SPARE SER 0780 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 9 | 14148 | 2 | 16416 | 3718 | 2 | EL6021_M181 |  | BITVAL
SPASCR0781 | SPARE SER 0781 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 10 | 14148 | 4 | 16416 | 3718 | 4 | EL6021_M181 |  | BITVAL
SPASCR0782 | SPARE SER 0782 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 11 | 14148 | 6 | 16416 | 3718 | 6 | EL6021_M181 |  | BITVAL
SPASCR0783 | SPARE SER 0783 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 12 | 14148 | 8 | 16416 | 3719 | 0 | EL6021_M181 |  | BITVAL
SPASCR0784 | SPARE SER 0784 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 13 | 14148 | 10 | 16416 | 3719 | 2 | EL6021_M181 |  | BITVAL
SPASCR0785 | SPARE SER 0785 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 14 | 14148 | 12 | 16416 | 3719 | 4 | EL6021_M181 |  | BITVAL
SPASCR0786 | SPARE SER 0786 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3013 | 15 | 14148 | 14 | 16416 | 3719 | 6 | EL6021_M181 |  | BITVAL
SPASCR0888 | SPARE SER 0888 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 4 | 14155 | 8 | 16416 | 3733 | 0 | EL6021_M181 |  | BITVAL
SPASCR0787 | SPARE SER 0787 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 5 | 14155 | 10 | 16416 | 3733 | 2 | EL6021_M181 |  | BITVAL
SPASCR0788 | SPARE SER 0788 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 6 | 14155 | 12 | 16416 | 3733 | 4 | EL6021_M181 |  | BITVAL
SPASCR0789 | SPARE SER 0789 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 7 | 14155 | 14 | 16416 | 3733 | 6 | EL6021_M181 |  | BITVAL
SPASCR0790 | SPARE SER 0790 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 8 | 14156 | 0 | 16416 | 3734 | 0 | EL6021_M181 |  | BITVAL
SPASCR0791 | SPARE SER 0791 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 9 | 14156 | 2 | 16416 | 3734 | 2 | EL6021_M181 |  | BITVAL
SPASCR0792 | SPARE SER 0792 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 10 | 14156 | 4 | 16416 | 3734 | 4 | EL6021_M181 |  | BITVAL
SPASCR0793 | SPARE SER 0793 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 11 | 14156 | 6 | 16416 | 3734 | 6 | EL6021_M181 |  | BITVAL
SPASCR0794 | SPARE SER 0794 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 12 | 14156 | 8 | 16416 | 3735 | 0 | EL6021_M181 |  | BITVAL
SPASCR0795 | SPARE SER 0795 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 13 | 14156 | 10 | 16416 | 3735 | 2 | EL6021_M181 |  | BITVAL
SPASCR0796 | SPARE SER 0796 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 14 | 14156 | 12 | 16416 | 3735 | 4 | EL6021_M181 |  | BITVAL
SPASCR0797 | SPARE SER 0797 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3019 | 15 | 14156 | 14 | 16416 | 3735 | 6 | EL6021_M181 |  | BITVAL
VRP6401F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 401.1 (CTA 1) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13;HVAC14 | HVAC |  | 7 |  |  | 3025 | 0 | 14160 | 0 | 16416 | 3742 | 0 | EL6021_M181 |  | BITVAL
VRP6401O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 401.1 (CTA 1) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3025 | 1 | 14160 | 2 | 16416 | 3742 | 2 | EL6021_M181 |  | BITVAL
VRP6401F2 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 401.2 (CTA 1) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13;HVAC15 | HVAC |  | 7 |  |  | 3025 | 2 | 14160 | 4 | 16416 | 3742 | 4 | EL6021_M181 |  | BITVAL
VRP6401O2 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 401.2 (CTA 1) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 3 | 14160 | 6 | 16416 | 3742 | 6 | EL6021_M181 |  | BITVAL
VCT6401M1 | VEGA GANTRY PLC : FAN CTA P01 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3025 | 4 | 14160 | 8 | 16416 | 3743 | 0 | EL6021_M181 |  | BITVAL
VCT6102M | VEGA GANTRY PLC : FAN CTA P03 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3025 | 5 | 14160 | 10 | 16416 | 3743 | 2 | EL6021_M181 |  | BITVAL
VRP6102F5 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 102.5 (CTA 3) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14;HVAC15 | HVAC |  | 7 |  |  | 3025 | 6 | 14160 | 12 | 16416 | 3743 | 4 | EL6021_M181 |  | BITVAL
VRP6102O5 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 102.5 (CTA 3) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14;HVAC15 | HVAC |  | 7 |  |  | 3025 | 7 | 14160 | 14 | 16416 | 3743 | 6 | EL6021_M181 |  | BITVAL
VRP6601F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 601.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 8 | 14161 | 0 | 16416 | 3744 | 0 | EL6021_M181 |  | BITVAL
VRP6601O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 601.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 9 | 14161 | 2 | 16416 | 3744 | 2 | EL6021_M181 |  | BITVAL
VRP6701F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 701.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 10 | 14161 | 4 | 16416 | 3744 | 4 | EL6021_M181 |  | BITVAL
VRP6701O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 701.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 11 | 14161 | 6 | 16416 | 3744 | 6 | EL6021_M181 |  | BITVAL
VRP6101F21 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 101.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 12 | 14161 | 8 | 16416 | 3745 | 0 | EL6021_M181 |  | BITVAL
VRP6101O21 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 101.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 13 | 14161 | 10 | 16416 | 3745 | 2 | EL6021_M181 |  | BITVAL
VRP6201F3 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 201.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 14 | 14161 | 12 | 16416 | 3745 | 4 | EL6021_M181 |  | BITVAL
VRP6201O3 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 201.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3025 | 15 | 14161 | 14 | 16416 | 3745 | 6 | EL6021_M181 |  | BITVAL
VRP6502F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 502.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 0 | 14162 | 0 | 16416 | 3746 | 0 | EL6021_M181 |  | BITVAL
VRP6502O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 502.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 1 | 14162 | 2 | 16416 | 3746 | 2 | EL6021_M181 |  | BITVAL
VRP6601F2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 601.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 2 | 14162 | 4 | 16416 | 3746 | 4 | EL6021_M181 |  | BITVAL
VRP6601O2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 601.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 3 | 14162 | 6 | 16416 | 3746 | 6 | EL6021_M181 |  | BITVAL
VRP6701F2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 701.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 4 | 14162 | 8 | 16416 | 3747 | 0 | EL6021_M181 |  | BITVAL
VRP6701O2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 701.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 5 | 14162 | 10 | 16416 | 3747 | 2 | EL6021_M181 |  | BITVAL
VRP6999F2 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER HALL CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 6 | 14164 | 8 | 16416 | 3751 | 0 | EL6021_M181 |  | BITVAL
VRP6999O2 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER HALL OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 7 | 14162 | 14 | 16416 | 3747 | 6 | EL6021_M181 |  | BITVAL
VRP6101F22 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 101.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 8 | 14163 | 0 | 16416 | 3748 | 0 | EL6021_M181 |  | BITVAL
VRP6101O22 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 101.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 9 | 14163 | 2 | 16416 | 3748 | 2 | EL6021_M181 |  | BITVAL
VRP6201F2 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 201.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 10 | 14163 | 4 | 16416 | 3748 | 4 | EL6021_M181 |  | BITVAL
VRP6201O2 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 201.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 11 | 14163 | 6 | 16416 | 3748 | 6 | EL6021_M181 |  | BITVAL
VRP6502F2 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 502.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 12 | 14163 | 8 | 16416 | 3749 | 0 | EL6021_M181 |  | BITVAL
VRP6502O2 | VEGA GANTRY PLC : EXTRACT N2 MOTORISED DAMPER 502.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 13 | 14163 | 10 | 16416 | 3749 | 2 | EL6021_M181 |  | BITVAL
VCT6701M | VEGA GANTRY PLC : FAN EXTRACTOR P06 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 14 | 14163 | 12 | 16416 | 3749 | 4 | EL6021_M181 |  | BITVAL
VRP6701F3 | VEGA GANTRY PLC : HALL MOTORISED DAMPER 701.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3026 | 15 | 14163 | 14 | 16416 | 3749 | 6 | EL6021_M181 |  | BITVAL
VRP6701O3 | VEGA GANTRY PLC : HALL MOTORISED DAMPER 701.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 0 | 14164 | 0 | 16416 | 3750 | 0 | EL6021_M181 |  | BITVAL
VCT6601M | VEGA GANTRY PLC : FAN EXTRACTOR P07 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 1 | 14164 | 2 | 16416 | 3750 | 2 | EL6021_M181 |  | BITVAL
VRP6601F3 | VEGA GANTRY PLC : HALL MOTORISED DAMPER 601.3 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 2 | 14164 | 4 | 16416 | 3750 | 4 | EL6021_M181 |  | BITVAL
VRP6601O3 | VEGA GANTRY PLC : HALL MOTORISED DAMPER 601.3 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 3 | 14164 | 6 | 16416 | 3750 | 6 | EL6021_M181 |  | BITVAL
VRP6999F1 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER HALL CLOSED | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 4 | 14162 | 12 | 16416 | 3747 | 4 | EL6021_M181 |  | BITVAL
VRP6999O1 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER HALL OPEN | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 5 | 14164 | 10 | 16416 | 3751 | 2 | EL6021_M181 |  | BITVAL
VCT6999M | VEGA GANTRY PLC : FAN EXTRACTOR P08 ON | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 6 | 14164 | 12 | 16416 | 3751 | 4 | EL6021_M181 |  | BITVAL
VVU6101O2 | VEGA GANTRY PLC : DECONTAMINATION ROOM 101 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 7 | 14164 | 14 | 16416 | 3751 | 6 | EL6021_M181 |  | BITVAL
VVU6201O | VEGA GANTRY PLC : DECONTAMINATION ROOM 201 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 8 | 14165 | 0 | 16416 | 3752 | 0 | EL6021_M181 |  | BITVAL
VVU6502O | VEGA GANTRY PLC : DECONTAMINATION ROOM 502 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 9 | 14165 | 2 | 16416 | 3752 | 2 | EL6021_M181 |  | BITVAL
VVU6999O | VEGA GANTRY PLC : DECONTAMINATION HALL | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 10 | 14165 | 4 | 16416 | 3752 | 4 | EL6021_M181 |  | BITVAL
VZN6701O | VEGA GANTRY PLC : DUSTING N2O4 ROOM 701 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 11 | 14165 | 6 | 16416 | 3752 | 6 | EL6021_M181 |  | BITVAL
VZU6601O | VEGA GANTRY PLC : DUSTING UDMH ROOM 601 | CR |  | RES | 1 | C | [26 empty] | NOT | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3027 | 12 | 14165 | 8 | 16416 | 3753 | 0 | EL6021_M181 |  | BITVAL
SPASCR0798 | SPARE SER 0798 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3027 | 13 | 14165 | 10 | 16416 | 3753 | 2 | EL6021_M181 |  | BITVAL
SPASCR0799 | SPARE SER 0799 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3027 | 14 | 14165 | 12 | 16416 | 3753 | 4 | EL6021_M181 |  | BITVAL
SPASCR0800 | SPARE SER 0800 | CR | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 7 |  |  | 3027 | 15 | 14165 | 14 | 16416 | 3753 | 6 | EL6021_M181 |  | BITVAL
SPASCR0801 | SPARE SER 0801 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 0 | 14166 | 0 | 16416 | 3754 | 0 | EL6021_M181 |  | BITVAL
SPASCR0802 | SPARE SER 0802 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 1 | 14166 | 2 | 16416 | 3754 | 2 | EL6021_M181 |  | BITVAL
SPASCR0803 | SPARE SER 0803 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 2 | 14166 | 4 | 16416 | 3754 | 4 | EL6021_M181 |  | BITVAL
VRP6102O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 102.1 (CTA 3) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3028 | 3 | 14166 | 6 | 16416 | 3754 | 6 | EL6021_M181 |  | BITVAL
VRP6102F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 102.1 (CTA 3) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3028 | 4 | 14166 | 8 | 16416 | 3755 | 0 | EL6021_M181 |  | BITVAL
VRP6102O3 | VEGA GANTRY PLC : RETURN AIR MOTORISED DAMPER 102.3 (CTA 3) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3028 | 5 | 14166 | 10 | 16416 | 3755 | 2 | EL6021_M181 |  | BITVAL
VRP6102F3 | VEGA GANTRY PLC : RETURN AIR MOTORISED DAMPER 102.3 (CTA 3) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3028 | 6 | 14166 | 12 | 16416 | 3755 | 4 | EL6021_M181 |  | BITVAL
VPZ6999O | VEGA GANTRY PLC : DOOR HALL OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3028 | 7 | 14166 | 14 | 16416 | 3755 | 6 | EL6021_M181 |  | BITVAL
SPASCR0804 | SPARE SER 0804 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 8 | 14167 | 0 | 16416 | 3756 | 0 | EL6021_M181 |  | BITVAL
SPASCR0805 | SPARE SER 0805 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 9 | 14167 | 2 | 16416 | 3756 | 2 | EL6021_M181 |  | BITVAL
SPASCR0806 | SPARE SER 0806 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 10 | 14167 | 4 | 16416 | 3756 | 4 | EL6021_M181 |  | BITVAL
SPASCR0807 | SPARE SER 0807 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 11 | 14167 | 6 | 16416 | 3756 | 6 | EL6021_M181 |  | BITVAL
SPASCR0808 | SPARE SER 0808 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 12 | 14167 | 8 | 16416 | 3757 | 0 | EL6021_M181 |  | BITVAL
SPASCR0809 | SPARE SER 0809 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 13 | 14167 | 10 | 16416 | 3757 | 2 | EL6021_M181 |  | BITVAL
SPASCR0810 | SPARE SER 0810 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 14 | 14167 | 12 | 16416 | 3757 | 4 | EL6021_M181 |  | BITVAL
SPASCR0811 | SPARE SER 0811 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3028 | 15 | 14167 | 14 | 16416 | 3757 | 6 | EL6021_M181 |  | BITVAL
VVU6401RM1 | VEGA GANTRY PLC : COMMAND IN PROGRESS : STARTING HVAC INSTALLATION | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 0 | 14168 | 0 | 16416 | 3758 | 0 | EL6021_M181 |  | BITVAL
VVU6401RK | VEGA GANTRY PLC : COMMAND IN PROGRESS : OPERATING IN ECO MODE | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 1 | 14168 | 2 | 16416 | 3758 | 2 | EL6021_M181 |  | BITVAL
VPZ6999RO | VEGA GANTRY PLC : COMMAND IN PROGRESS : OPENNING HALL DOOR | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 2 | 14168 | 4 | 16416 | 3758 | 4 | EL6021_M181 |  | BITVAL
VZN6701RM | VEGA GANTRY PLC : COMMAND IN PROGRESS : FILLING N2O4 | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 3 | 14168 | 6 | 16416 | 3758 | 6 | EL6021_M181 |  | BITVAL
VZU6601RM | VEGA GANTRY PLC : COMMAND IN PROGRESS : FILLING UDMH | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 4 | 14168 | 8 | 16416 | 3759 | 0 | EL6021_M181 |  | BITVAL
VVU6401RV | VEGA GANTRY PLC : COMMAND IN PROGRESS : LOCKING CONFIGURATION (D-1) | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 5 | 14168 | 10 | 16416 | 3759 | 2 | EL6021_M181 |  | BITVAL
VVU6401RM2 | VEGA GANTRY PLC : COMMAND IN PROGRESS : STARTING INTERNAL HVAC | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3029 | 6 | 14168 | 12 | 16416 | 3759 | 4 | EL6021_M181 |  | BITVAL
SPASCR0812 | SPARE SER 0812 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 7 | 14168 | 14 | 16416 | 3759 | 6 | EL6021_M181 |  | BITVAL
SPASCR0813 | SPARE SER 0813 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 8 | 14169 | 0 | 16416 | 3760 | 0 | EL6021_M181 |  | BITVAL
SPASCR0814 | SPARE SER 0814 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 9 | 14169 | 2 | 16416 | 3760 | 2 | EL6021_M181 |  | BITVAL
SPASCR0815 | SPARE SER 0815 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 10 | 14169 | 4 | 16416 | 3760 | 4 | EL6021_M181 |  | BITVAL
SPASCR0816 | SPARE SER 0816 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 11 | 14169 | 6 | 16416 | 3760 | 6 | EL6021_M181 |  | BITVAL
SPASCR0817 | SPARE SER 0817 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 12 | 14169 | 8 | 16416 | 3761 | 0 | EL6021_M181 |  | BITVAL
SPASCR0818 | SPARE SER 0818 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 13 | 14169 | 10 | 16416 | 3761 | 2 | EL6021_M181 |  | BITVAL
SPASCR0819 | SPARE SER 0819 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 14 | 14169 | 12 | 16416 | 3761 | 4 | EL6021_M181 |  | BITVAL
SPASCR0820 | SPARE SER 0820 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3029 | 15 | 14169 | 14 | 16416 | 3761 | 6 | EL6021_M181 |  | BITVAL
VZC6401J11 | VEGA GANTRY PLC X80-1 : RUN PRIMARY | CR |  | RES | 1 | C;A | [26 empty] | POL | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01);HVAC01 | HVAC |  | 7 |  |  | 3030 | 0 | 14170 | 0 | 16416 | 3762 | 0 | EL6021_M181 |  | BITVAL
VZC6401J12 | VEGA GANTRY PLC X80-1 : RUN SECONDARY | CR |  | RES | 1 | C;A | [26 empty] | POL | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01);HVAC01 | HVAC |  | 7 |  |  | 3030 | 1 | 14170 | 2 | 16416 | 3762 | 2 | EL6021_M181 |  | BITVAL
VZC6401J21 | VEGA GANTRY PLC X80-2 : RUN PRIMARY | CR |  | RES | 1 | C;A | [26 empty] | POL | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01);HVAC01 | HVAC |  | 7 |  |  | 3030 | 2 | 14170 | 4 | 16416 | 3762 | 4 | EL6021_M181 |  | BITVAL
VZC6401J22 | VEGA GANTRY PLC X80-2 : RUN SECONDARY | CR |  | RES | 1 | C;A | [26 empty] | POL | 1000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01);HVAC01 | HVAC |  | 7 |  |  | 3030 | 3 | 14170 | 6 | 16416 | 3762 | 6 | EL6021_M181 |  | BITVAL
SPASCR0821 | SPARE SER 0821 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 4 | 14170 | 8 | 16416 | 3763 | 0 | EL6021_M181 |  | BITVAL
SPASCR0822 | SPARE SER 0822 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 5 | 14170 | 10 | 16416 | 3763 | 2 | EL6021_M181 |  | BITVAL
SPASCR0823 | SPARE SER 0823 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 6 | 14170 | 12 | 16416 | 3763 | 4 | EL6021_M181 |  | BITVAL
SPASCR0824 | SPARE SER 0824 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 7 | 14170 | 14 | 16416 | 3763 | 6 | EL6021_M181 |  | BITVAL
SPASCR0825 | SPARE SER 0825 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 8 | 14171 | 0 | 16416 | 3764 | 0 | EL6021_M181 |  | BITVAL
SPASCR0826 | SPARE SER 0826 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 9 | 14171 | 2 | 16416 | 3764 | 2 | EL6021_M181 |  | BITVAL
SPASCR0827 | SPARE SER 0827 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 10 | 14171 | 4 | 16416 | 3764 | 4 | EL6021_M181 |  | BITVAL
SPASCR0828 | SPARE SER 0828 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 11 | 14171 | 6 | 16416 | 3764 | 6 | EL6021_M181 |  | BITVAL
SPASCR0829 | SPARE SER 0829 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 12 | 14171 | 8 | 16416 | 3765 | 0 | EL6021_M181 |  | BITVAL
SPASCR0830 | SPARE SER 0830 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 13 | 14171 | 10 | 16416 | 3765 | 2 | EL6021_M181 |  | BITVAL
SPASCR0831 | SPARE SER 0831 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 14 | 14171 | 12 | 16416 | 3765 | 4 | EL6021_M181 |  | BITVAL
SPASCR0832 | SPARE SER 0832 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3030 | 15 | 14171 | 14 | 16416 | 3765 | 6 | EL6021_M181 |  | BITVAL
VVU6401K1 | VEGA GANTRY PLC : HVAC INSTALLATION MODE OPE OK | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3031 | 0 | 14172 | 0 | 16416 | 3766 | 0 | EL6021_M181 |  | BITVAL
VVU6401K2 | VEGA GANTRY PLC : HVAC INSTALLATION MODE ECO OK | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D | HVAC17 | HVAC |  | 7 |  |  | 3031 | 1 | 14172 | 2 | 16416 | 3766 | 2 | EL6021_M181 |  | BITVAL
VVU6401M2 | VEGA GANTRY PLC : INTERNAL HVAC ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VZC6401D |  |  |  | 7 |  |  | 3031 | 2 | 14172 | 4 | 16416 | 3766 | 4 | EL6021_M181 |  | BITVAL
SPASCR0833 | SPARE SER 0833 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 3 | 14172 | 6 | 16416 | 3766 | 6 | EL6021_M181 |  | BITVAL
SPASCR0834 | SPARE SER 0834 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 4 | 14172 | 8 | 16416 | 3767 | 0 | EL6021_M181 |  | BITVAL
SPASCR0835 | SPARE SER 0835 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 5 | 14172 | 10 | 16416 | 3767 | 2 | EL6021_M181 |  | BITVAL
SPASCR0836 | SPARE SER 0836 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 6 | 14172 | 12 | 16416 | 3767 | 4 | EL6021_M181 |  | BITVAL
SPASCR0837 | SPARE SER 0837 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 7 | 14172 | 14 | 16416 | 3767 | 6 | EL6021_M181 |  | BITVAL
SPASCR0838 | SPARE SER 0838 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 8 | 14173 | 0 | 16416 | 3768 | 0 | EL6021_M181 |  | BITVAL
SPASCR0839 | SPARE SER 0839 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 9 | 14173 | 2 | 16416 | 3768 | 2 | EL6021_M181 |  | BITVAL
SPASCR0840 | SPARE SER 0840 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 10 | 14173 | 4 | 16416 | 3768 | 4 | EL6021_M181 |  | BITVAL
SPASCR0841 | SPARE SER 0841 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 11 | 14173 | 6 | 16416 | 3768 | 6 | EL6021_M181 |  | BITVAL
SPASCR0842 | SPARE SER 0842 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 12 | 14173 | 8 | 16416 | 3769 | 0 | EL6021_M181 |  | BITVAL
SPASCR0843 | SPARE SER 0843 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 13 | 14173 | 10 | 16416 | 3769 | 2 | EL6021_M181 |  | BITVAL
SPASCR0844 | SPARE SER 0844 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 14 | 14173 | 12 | 16416 | 3769 | 4 | EL6021_M181 |  | BITVAL
SPASCR0845 | SPARE SER 0845 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3031 | 15 | 14173 | 14 | 16416 | 3769 | 6 | EL6021_M181 |  | BITVAL
VRP6401F3 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 401.3 (CTA 2) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3037 | 0 | 14179 | 0 | 16416 | 3780 | 0 | EL6021_M181 |  | BITVAL
VRP6401O3 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 401.3 (CTA 2) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3037 | 1 | 14179 | 2 | 16416 | 3780 | 2 | EL6021_M181 |  | BITVAL
VRP6401F4 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 401.4 (CTA 2) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13;HVAC15 | HVAC |  | 7 |  |  | 3037 | 2 | 14179 | 4 | 16416 | 3780 | 4 | EL6021_M181 |  | BITVAL
VRP6401O4 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 401.4 (CTA 2) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13;HVAC15 | HVAC |  | 7 |  |  | 3037 | 3 | 14179 | 6 | 16416 | 3780 | 6 | EL6021_M181 |  | BITVAL
VCT6401M2 | VEGA GANTRY PLC : FAN CTA P02 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3037 | 4 | 14179 | 8 | 16416 | 3781 | 0 | EL6021_M181 |  | BITVAL
VCT6202M | VEGA GANTRY PLC : FAN CTA P04 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3037 | 5 | 14179 | 10 | 16416 | 3781 | 2 | EL6021_M181 |  | BITVAL
VRP6201F5 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 201.5 (CTA 4) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14;HVAC15 | HVAC |  | 7 |  |  | 3037 | 6 | 14179 | 12 | 16416 | 3781 | 4 | EL6021_M181 |  | BITVAL
VRP6201O5 | VEGA GANTRY PLC : PULSE AIR MOTORISED DAMPER 201.5 (CTA 4) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14;HVAC15 | HVAC |  | 7 |  |  | 3037 | 7 | 14179 | 14 | 16416 | 3781 | 6 | EL6021_M181 |  | BITVAL
VRP6301O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 301.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 8 | 14180 | 0 | 16416 | 3782 | 0 | EL6021_M181 |  | BITVAL
VRP6301F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 301.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 9 | 14180 | 2 | 16416 | 3782 | 2 | EL6021_M181 |  | BITVAL
VRP6501O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 501.1 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 10 | 14180 | 4 | 16416 | 3782 | 4 | EL6021_M181 |  | BITVAL
VRP6501F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 501.1 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 11 | 14180 | 6 | 16416 | 3782 | 6 | EL6021_M181 |  | BITVAL
VRP6301F2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 301.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 12 | 14180 | 8 | 16416 | 3783 | 0 | EL6021_M181 |  | BITVAL
VRP6301O2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 301.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 13 | 14180 | 10 | 16416 | 3783 | 2 | EL6021_M181 |  | BITVAL
VRP6501F2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 501.2 CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 14 | 14180 | 12 | 16416 | 3783 | 4 | EL6021_M181 |  | BITVAL
VRP6501O2 | VEGA GANTRY PLC : EXTRACT AIR MOTORISED DAMPER 501.2 OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC15 | HVAC |  | 7 |  |  | 3037 | 15 | 14180 | 14 | 16416 | 3783 | 6 | EL6021_M181 |  | BITVAL
SPASCR0846 | SPARE SER 0846 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 0 | 14181 | 0 | 16416 | 3784 | 0 | EL6021_M181 |  | BITVAL
SPASCR0847 | SPARE SER 0847 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 1 | 14181 | 2 | 16416 | 3784 | 2 | EL6021_M181 |  | BITVAL
SPASCR0848 | SPARE SER 0848 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 2 | 14181 | 4 | 16416 | 3784 | 4 | EL6021_M181 |  | BITVAL
SPASCR0849 | SPARE SER 0849 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 3 | 14181 | 6 | 16416 | 3784 | 6 | EL6021_M181 |  | BITVAL
VRP6201O4 | VEGA GANTRY PLC : RETURN AIR MOTORISED DAMPER 201.4 (CTA 4) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3038 | 4 | 14181 | 8 | 16416 | 3785 | 0 | EL6021_M181 |  | BITVAL
VRP6201F4 | VEGA GANTRY PLC : RETURN AIR MOTORISED DAMPER 201.4 (CTA 4) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3038 | 5 | 14181 | 10 | 16416 | 3785 | 2 | EL6021_M181 |  | BITVAL
VRP6201O1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 201.1 (CTA 4) OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3038 | 6 | 14181 | 12 | 16416 | 3785 | 4 | EL6021_M181 |  | BITVAL
VRP6201F1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 201.1 (CTA 4) CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC14 | HVAC |  | 7 |  |  | 3038 | 7 | 14181 | 14 | 16416 | 3785 | 6 | EL6021_M181 |  | BITVAL
SPASCR0850 | SPARE SER 0850 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 8 | 14182 | 0 | 16416 | 3786 | 0 | EL6021_M181 |  | BITVAL
SPASCR0851 | SPARE SER 0851 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 9 | 14182 | 2 | 16416 | 3786 | 2 | EL6021_M181 |  | BITVAL
SPASCR0852 | SPARE SER 0852 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 10 | 14182 | 4 | 16416 | 3786 | 4 | EL6021_M181 |  | BITVAL
SPASCR0853 | SPARE SER 0853 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 11 | 14182 | 6 | 16416 | 3786 | 6 | EL6021_M181 |  | BITVAL
SPASCR0854 | SPARE SER 0854 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 12 | 14182 | 8 | 16416 | 3787 | 0 | EL6021_M181 |  | BITVAL
SPASCR0855 | SPARE SER 0855 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 13 | 14182 | 10 | 16416 | 3787 | 2 | EL6021_M181 |  | BITVAL
SPASCR0856 | SPARE SER 0856 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 14 | 14182 | 12 | 16416 | 3787 | 4 | EL6021_M181 |  | BITVAL
SPASCR0857 | SPARE SER 0857 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3038 | 15 | 14182 | 14 | 16416 | 3787 | 6 | EL6021_M181 |  | BITVAL
VVV6502M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 502.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 0 | 14183 | 0 | 16416 | 3788 | 0 | EL6021_M181 |  | BITVAL
VVV6401M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 401.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 1 | 14183 | 2 | 16416 | 3788 | 2 | EL6021_M181 |  | BITVAL
VVV6301M2 | VEGA GANTRY PLC : FAN COIL (CAREL) 301.2 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 2 | 14183 | 4 | 16416 | 3788 | 4 | EL6021_M181 |  | BITVAL
VVV6202M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 202.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 3 | 14183 | 6 | 16416 | 3788 | 6 | EL6021_M181 |  | BITVAL
VVV6102M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 102.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 4 | 14183 | 8 | 16416 | 3789 | 0 | EL6021_M181 |  | BITVAL
VVV6101M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 101.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 5 | 14183 | 10 | 16416 | 3789 | 2 | EL6021_M181 |  | BITVAL
VVV6501M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 501.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 6 | 14183 | 12 | 16416 | 3789 | 4 | EL6021_M181 |  | BITVAL
VVV6801M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 801.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 7 | 14183 | 14 | 16416 | 3789 | 6 | EL6021_M181 |  | BITVAL
VVV6301M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 301.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 8 | 14184 | 0 | 16416 | 3790 | 0 | EL6021_M181 |  | BITVAL
VVV6201M1 | VEGA GANTRY PLC : FAN COIL (CAREL) 201.1 ON | CR |  | RES | 1 | C | [26 empty] | POL | 1000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3039 | 9 | 14184 | 2 | 16416 | 3790 | 2 | EL6021_M181 |  | BITVAL
SPASCR0858 | SPARE SER 0858 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3039 | 10 | 14184 | 4 | 16416 | 3790 | 4 | EL6021_M181 |  | BITVAL
SPASCR0859 | SPARE SER 0859 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3039 | 11 | 14184 | 6 | 16416 | 3790 | 6 | EL6021_M181 |  | BITVAL
SPASCR0860 | SPARE SER 0860 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3039 | 12 | 14184 | 8 | 16416 | 3791 | 0 | EL6021_M181 |  | BITVAL
SPASCR0861 | SPARE SER 0861 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3039 | 13 | 14184 | 10 | 16416 | 3791 | 2 | EL6021_M181 |  | BITVAL
SPASCR0862 | SPARE SER 0862 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3039 | 14 | 14184 | 12 | 16416 | 3791 | 4 | EL6021_M181 |  | BITVAL
SPASCR0863 | SPARE SER 0863 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3039 | 15 | 14184 | 14 | 16416 | 3791 | 6 | EL6021_M181 |  | BITVAL
GVM6005F2 | VEGA GANTRY PLC : COLD WATER VALVE 5 SUPPLY GANTRY CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 0 | 14189 | 0 | 16416 | 3800 | 0 | EL6021_M181 |  | BITVAL
GVM6005O2 | VEGA GANTRY PLC : COLD WATER VALVE 5 SUPPLY GANTRY OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 1 | 14189 | 2 | 16416 | 3800 | 2 | EL6021_M181 |  | BITVAL
GVM6006F2 | VEGA GANTRY PLC : COLD WATER VALVE 6 RETURN GANTRY CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 2 | 14189 | 4 | 16416 | 3800 | 4 | EL6021_M181 |  | BITVAL
GVM6006O2 | VEGA GANTRY PLC : COLD WATER VALVE 6 RETURN GANTRY OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 3 | 14189 | 6 | 16416 | 3800 | 6 | EL6021_M181 |  | BITVAL
CVM6005F2 | VEGA GANTRY PLC : HOT WATER VALVE 5 SUPPLY GANTRY CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 4 | 14189 | 8 | 16416 | 3801 | 0 | EL6021_M181 |  | BITVAL
CVM6005O2 | VEGA GANTRY PLC : HOT WATER VALVE 5 SUPPLY GANTRY OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 5 | 14189 | 10 | 16416 | 3801 | 2 | EL6021_M181 |  | BITVAL
CVM6006F2 | VEGA GANTRY PLC : HOT WATER VALVE 6 RETURN GANTRY CLOSED | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 6 | 14189 | 12 | 16416 | 3801 | 4 | EL6021_M181 |  | BITVAL
CVM6006O2 | VEGA GANTRY PLC : HOT WATER VALVE 6 RETURN GANTRY OPEN | CR |  | RES | 1 | C | [26 empty] | POL | 1000 |  | HVAC03 | HVAC |  | 7 |  |  | 3044 | 7 | 14189 | 14 | 16416 | 3801 | 6 | EL6021_M181 |  | BITVAL
SPASCR0864 | SPARE SER 0864 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 8 | 14190 | 0 | 16416 | 3802 | 0 | EL6021_M181 |  | BITVAL
SPASCR0865 | SPARE SER 0865 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 9 | 14190 | 2 | 16416 | 3802 | 2 | EL6021_M181 |  | BITVAL
SPASCR0866 | SPARE SER 0866 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 10 | 14190 | 4 | 16416 | 3802 | 4 | EL6021_M181 |  | BITVAL
SPASCR0867 | SPARE SER 0867 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 11 | 14190 | 6 | 16416 | 3802 | 6 | EL6021_M181 |  | BITVAL
SPASCR0868 | SPARE SER 0868 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 12 | 14190 | 8 | 16416 | 3803 | 0 | EL6021_M181 |  | BITVAL
SPASCR0869 | SPARE SER 0869 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 13 | 14190 | 10 | 16416 | 3803 | 2 | EL6021_M181 |  | BITVAL
SPASCR0870 | SPARE SER 0870 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 14 | 14190 | 12 | 16416 | 3803 | 4 | EL6021_M181 |  | BITVAL
SPASCR0871 | SPARE SER 0871 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3044 | 15 | 14190 | 14 | 16416 | 3803 | 6 | EL6021_M181 |  | BITVAL
SPASCR0872 | SPARE SER 0872 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 0 | 14191 | 0 | 16416 | 3804 | 0 | EL6021_M181 |  | BITVAL
SPASCR0873 | SPARE SER 0873 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 1 | 14191 | 2 | 16416 | 3804 | 2 | EL6021_M181 |  | BITVAL
SPASCR0874 | SPARE SER 0874 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 2 | 14191 | 4 | 16416 | 3804 | 4 | EL6021_M181 |  | BITVAL
SPASCR0875 | SPARE SER 0875 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 3 | 14191 | 6 | 16416 | 3804 | 6 | EL6021_M181 |  | BITVAL
SPASCR0876 | SPARE SER 0876 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 4 | 14191 | 8 | 16416 | 3805 | 0 | EL6021_M181 |  | BITVAL
SPASCR0877 | SPARE SER 0877 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 5 | 14191 | 10 | 16416 | 3805 | 2 | EL6021_M181 |  | BITVAL
SPASCR0878 | SPARE SER 0878 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 6 | 14191 | 12 | 16416 | 3805 | 4 | EL6021_M181 |  | BITVAL
SPASCR0879 | SPARE SER 0879 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 7 | 14191 | 14 | 16416 | 3805 | 6 | EL6021_M181 |  | BITVAL
SPASCR0880 | SPARE SER 0880 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 8 | 14192 | 0 | 16416 | 3806 | 0 | EL6021_M181 |  | BITVAL
SPASCR0881 | SPARE SER 0881 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 9 | 14192 | 2 | 16416 | 3806 | 2 | EL6021_M181 |  | BITVAL
SPASCR0882 | SPARE SER 0882 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 10 | 14192 | 4 | 16416 | 3806 | 4 | EL6021_M181 |  | BITVAL
SPASCR0883 | SPARE SER 0883 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 11 | 14192 | 6 | 16416 | 3806 | 6 | EL6021_M181 |  | BITVAL
SPASCR0884 | SPARE SER 0884 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 12 | 14192 | 8 | 16416 | 3807 | 0 | EL6021_M181 |  | BITVAL
SPASCR0885 | SPARE SER 0885 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 13 | 14192 | 10 | 16416 | 3807 | 2 | EL6021_M181 |  | BITVAL
SPASCR0886 | SPARE SER 0886 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 14 | 14192 | 12 | 16416 | 3807 | 4 | EL6021_M181 |  | BITVAL
SPASCR0887 | SPARE SER 0887 | CR | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3045 | 15 | 14192 | 14 | 16416 | 3807 | 6 | EL6021_M181 |  | BITVAL
ZZZ6134M2 | VMC API Front-End etat du module EL1134_M2 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15000 | NA | 16416 | 5422 | NA | EL1134_M2 |  | UINT
ZZZ6134M3 | VMC API Front-End etat du module EL1134_M3 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15001 | NA | 16416 | 5424 | NA | EL1134_M3 |  | UINT
ZZZ6134M4 | VMC API Front-End etat du module EL1134_M4 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 2 (VMC01);Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15002 | NA | 16416 | 5426 | NA | EL1134_M4 |  | UINT
ZZZ6134M5 | VMC API Front-End etat du module EL1134_M5 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15003 | NA | 16416 | 5428 | NA | EL1134_M5 |  | UINT
ZZZ6134M6 | VMC API Front-End etat du module EL1134_M6 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 3 (VMC01);Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15004 | NA | 16416 | 5430 | NA | EL1134_M6 |  | UINT
ZZZ6134M7 | VMC API Front-End etat du module EL1134_M7 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15005 | NA | 16416 | 5432 | NA | EL1134_M7 |  | UINT
ZZZ6134M8 | VMC API Front-End etat du module EL1134_M8 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15006 | NA | 16416 | 5434 | NA | EL1134_M8 |  | UINT
ZZZ6134M9 | VMC API Front-End etat du module EL1134_M9 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15007 | NA | 16416 | 5436 | NA | EL1134_M9 |  | UINT
ZZZ6134M10 | VMC API Front-End etat du module EL1134_M10 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15008 | NA | 16416 | 5438 | NA | EL1134_M10 |  | UINT
ZZZ6134M11 | VMC API Front-End etat du module EL1134_M11 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 5 (VMC01);Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15009 | NA | 16416 | 5440 | NA | EL1134_M11 |  | UINT
ZZZ6134M13 | VMC API Front-End etat du module EL1134_M13 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 6 (VMC01);Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15010 | NA | 16416 | 5442 | NA | EL1134_M13 |  | UINT
ZZZ6134M14 | VMC API Front-End etat du module EL1134_M14 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15011 | NA | 16416 | 5444 | NA | EL1134_M14 |  | UINT
ZZZ6134M15 | VMC API Front-End etat du module EL1134_M15 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01);Infos Chaine 7 (VMC01);Infos Chaine 8 (VMC01) | VMC (Z) | [6 empty] | 15012 | NA | 16416 | 5446 | NA | EL1134_M15 |  | UINT
ZZZ6134M16 | VMC API Front-End etat du module EL1134_M16 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15013 | NA | 16416 | 5448 | NA | EL1134_M16 |  | UINT
ZZZ6134M17 | VMC API Front-End etat du module EL1134_M17 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15014 | NA | 16416 | 5450 | NA | EL1134_M17 |  | UINT
ZZZ6134M18 | VMC API Front-End etat du module EL1134_M18 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15015 | NA | 16416 | 5452 | NA | EL1134_M18 |  | UINT
ZZZ6134M19 | VMC API Front-End etat du module EL1134_M19 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15016 | NA | 16416 | 5454 | NA | EL1134_M19 |  | UINT
ZZZ6134M20 | VMC API Front-End etat du module EL1134_M20 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15017 | NA | 16416 | 5456 | NA | EL1134_M20 |  | UINT
ZZZ6134M21 | VMC API Front-End etat du module EL1134_M21 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15018 | NA | 16416 | 5458 | NA | EL1134_M21 |  | UINT
ZZZ6134M22 | VMC API Front-End etat du module EL1134_M22 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15019 | NA | 16416 | 5460 | NA | EL1134_M22 |  | UINT
ZZZ6134M24 | VMC API Front-End etat du module EL1134_M24 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15020 | NA | 16416 | 5462 | NA | EL1134_M24 |  | UINT
ZZZ6134M25 | VMC API Front-End etat du module EL1134_M25 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15021 | NA | 16416 | 5464 | NA | EL1134_M25 |  | UINT
ZZZ6134M26 | VMC API Front-End etat du module EL1134_M26 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15022 | NA | 16416 | 5466 | NA | EL1134_M26 |  | UINT
ZZZ6134M27 | VMC API Front-End etat du module EL1134_M27 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15023 | NA | 16416 | 5468 | NA | EL1134_M27 |  | UINT
ZZZ6134M28 | VMC API Front-End etat du module EL1134_M28 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15024 | NA | 16416 | 5470 | NA | EL1134_M28 |  | UINT
ZZZ6134M29 | VMC API Front-End etat du module EL1134_M29 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15025 | NA | 16416 | 5472 | NA | EL1134_M29 |  | UINT
ZZZ6134M30 | VMC API Front-End etat du module EL1134_M30 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15026 | NA | 16416 | 5474 | NA | EL1134_M30 |  | UINT
ZZZ6134M31 | VMC API Front-End etat du module EL1134_M31 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15027 | NA | 16416 | 5476 | NA | EL1134_M31 |  | UINT
ZZZ6134M32 | VMC API Front-End etat du module EL1134_M32 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15028 | NA | 16416 | 5478 | NA | EL1134_M32 |  | UINT
ZZZ6134M33 | VMC API Front-End etat du module EL1134_M33 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15029 | NA | 16416 | 5480 | NA | EL1134_M33 |  | UINT
ZZZ6134M35 | VMC API Front-End etat du module EL1134_M35 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15030 | NA | 16416 | 5482 | NA | EL1134_M35 |  | UINT
ZZZ6134M36 | VMC API Front-End etat du module EL1134_M36 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15031 | NA | 16416 | 5484 | NA | EL1134_M36 |  | UINT
ZZZ6134M37 | VMC API Front-End etat du module EL1134_M37 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15032 | NA | 16416 | 5486 | NA | EL1134_M37 |  | UINT
ZZZ6134M38 | VMC API Front-End etat du module EL1134_M38 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15033 | NA | 16416 | 5488 | NA | EL1134_M38 |  | UINT
ZZZ6134M39 | VMC API Front-End etat du module EL1134_M39 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15034 | NA | 16416 | 5490 | NA | EL1134_M39 |  | UINT
ZZZ6134M40 | VMC API Front-End etat du module EL1134_M40 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15035 | NA | 16416 | 5492 | NA | EL1134_M40 |  | UINT
ZZZ6134M41 | VMC API Front-End etat du module EL1134_M41 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15036 | NA | 16416 | 5494 | NA | EL1134_M41 |  | UINT
ZZZ6134M42 | VMC API Front-End etat du module EL1134_M42 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15037 | NA | 16416 | 5496 | NA | EL1134_M42 |  | UINT
ZZZ6134M43 | VMC API Front-End etat du module EL1134_M43 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15038 | NA | 16416 | 5498 | NA | EL1134_M43 |  | UINT
ZZZ6134M44 | VMC API Front-End etat du module EL1134_M44 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15039 | NA | 16416 | 5500 | NA | EL1134_M44 |  | UINT
ZZZ6134M46 | VMC API Front-End etat du module EL1134_M46 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15040 | NA | 16416 | 5502 | NA | EL1134_M46 |  | UINT
ZZZ6134M47 | VMC API Front-End etat du module EL1134_M47 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15041 | NA | 16416 | 5504 | NA | EL1134_M47 |  | UINT
ZZZ6134M48 | VMC API Front-End etat du module EL1134_M48 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15042 | NA | 16416 | 5506 | NA | EL1134_M48 |  | UINT
ZZZ6134M49 | VMC API Front-End etat du module EL1134_M49 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15043 | NA | 16416 | 5508 | NA | EL1134_M49 |  | UINT
ZZZ6134M50 | VMC API Front-End etat du module EL1134_M50 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15044 | NA | 16416 | 5510 | NA | EL1134_M50 |  | UINT
ZZZ6134M51 | VMC API Front-End etat du module EL1134_M51 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15045 | NA | 16416 | 5512 | NA | EL1134_M51 |  | UINT
ZZZ6134M52 | VMC API Front-End etat du module EL1134_M52 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15046 | NA | 16416 | 5514 | NA | EL1134_M52 |  | UINT
ZZZ6134M53 | VMC API Front-End etat du module EL1134_M53 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15047 | NA | 16416 | 5516 | NA | EL1134_M53 |  | UINT
ZZZ6134M54 | VMC API Front-End etat du module EL1134_M54 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15048 | NA | 16416 | 5518 | NA | EL1134_M54 |  | UINT
ZZZ6134M55 | VMC API Front-End etat du module EL1134_M55 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15049 | NA | 16416 | 5520 | NA | EL1134_M55 |  | UINT
ZZZ6134M57 | VMC API Front-End etat du module EL1134_M57 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15050 | NA | 16416 | 5522 | NA | EL1134_M57 |  | UINT
ZZZ6134M58 | VMC API Front-End etat du module EL1134_M58 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15051 | NA | 16416 | 5524 | NA | EL1134_M58 |  | UINT
ZZZ6134M59 | VMC API Front-End etat du module EL1134_M59 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15052 | NA | 16416 | 5526 | NA | EL1134_M59 |  | UINT
ZZZ6134M60 | VMC API Front-End etat du module EL1134_M60 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15053 | NA | 16416 | 5528 | NA | EL1134_M60 |  | UINT
ZZZ6134M61 | VMC API Front-End etat du module EL1134_M61 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15054 | NA | 16416 | 5530 | NA | EL1134_M61 |  | UINT
ZZZ6134M62 | VMC API Front-End etat du module EL1134_M62 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15055 | NA | 16416 | 5532 | NA | EL1134_M62 |  | UINT
ZZZ6134M63 | VMC API Front-End etat du module EL1134_M63 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15056 | NA | 16416 | 5534 | NA | EL1134_M63 |  | UINT
ZZZ6134M64 | VMC API Front-End etat du module EL1134_M64 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15057 | NA | 16416 | 5536 | NA | EL1134_M64 |  | UINT
ZZZ6134M65 | VMC API Front-End etat du module EL1134_M65 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15058 | NA | 16416 | 5538 | NA | EL1134_M65 |  | UINT
ZZZ6134M66 | VMC API Front-End etat du module EL1134_M66 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15059 | NA | 16416 | 5540 | NA | EL1134_M66 |  | UINT
ZZZ6134M68 | VMC API Front-End etat du module EL1134_M68 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15060 | NA | 16416 | 5542 | NA | EL1134_M68 |  | UINT
ZZZ6134M69 | VMC API Front-End etat du module EL1134_M69 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15061 | NA | 16416 | 5544 | NA | EL1134_M69 |  | UINT
ZZZ6134M70 | VMC API Front-End etat du module EL1134_M70 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15062 | NA | 16416 | 5546 | NA | EL1134_M70 |  | UINT
ZZZ6134M71 | VMC API Front-End etat du module EL1134_M71 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15063 | NA | 16416 | 5548 | NA | EL1134_M71 |  | UINT
ZZZ6134M72 | VMC API Front-End etat du module EL1134_M72 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15064 | NA | 16416 | 5550 | NA | EL1134_M72 |  | UINT
ZZZ6134M73 | VMC API Front-End etat du module EL1134_M73 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15065 | NA | 16416 | 5552 | NA | EL1134_M73 |  | UINT
ZZZ6134M74 | VMC API Front-End etat du module EL1134_M74 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15066 | NA | 16416 | 5554 | NA | EL1134_M74 |  | UINT
ZZZ6134M75 | VMC API Front-End etat du module EL1134_M75 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15067 | NA | 16416 | 5556 | NA | EL1134_M75 |  | UINT
ZZZ6134M76 | VMC API Front-End etat du module EL1134_M76 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15068 | NA | 16416 | 5558 | NA | EL1134_M76 |  | UINT
ZZZ6134M77 | VMC API Front-End etat du module EL1134_M77 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15069 | NA | 16416 | 5560 | NA | EL1134_M77 |  | UINT
ZZZ6134M79 | VMC API Front-End etat du module EL1134_M79 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15070 | NA | 16416 | 5562 | NA | EL1134_M79 |  | UINT
ZZZ6134M80 | VMC API Front-End etat du module EL1134_M80 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15071 | NA | 16416 | 5564 | NA | EL1134_M80 |  | UINT
ZZZ6134M81 | VMC API Front-End etat du module EL1134_M81 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15072 | NA | 16416 | 5566 | NA | EL1134_M81 |  | UINT
ZZZ6134M82 | VMC API Front-End etat du module EL1134_M82 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15073 | NA | 16416 | 5568 | NA | EL1134_M82 |  | UINT
ZZZ6134M83 | VMC API Front-End etat du module EL1134_M83 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15074 | NA | 16416 | 5570 | NA | EL1134_M83 |  | UINT
ZZZ6134M84 | VMC API Front-End etat du module EL1134_M84 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15075 | NA | 16416 | 5572 | NA | EL1134_M84 |  | UINT
ZZZ6134M85 | VMC API Front-End etat du module EL1134_M85 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15076 | NA | 16416 | 5574 | NA | EL1134_M85 |  | UINT
ZZZ6134M86 | VMC API Front-End etat du module EL1134_M86 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15077 | NA | 16416 | 5576 | NA | EL1134_M86 |  | UINT
ZZZ6134M87 | VMC API Front-End etat du module EL1134_M87 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15078 | NA | 16416 | 5578 | NA | EL1134_M87 |  | UINT
ZZZ6134M88 | VMC API Front-End etat du module EL1134_M88 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15079 | NA | 16416 | 5580 | NA | EL1134_M88 |  | UINT
ZZZ6134M90 | VMC API Front-End etat du module EL1134_M90 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15080 | NA | 16416 | 5582 | NA | EL1134_M90 |  | UINT
ZZZ6134M91 | VMC API Front-End etat du module EL1134_M91 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15081 | NA | 16416 | 5584 | NA | EL1134_M91 |  | UINT
ZZZ6134M92 | VMC API Front-End etat du module EL1134_M92 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15082 | NA | 16416 | 5586 | NA | EL1134_M92 |  | UINT
ZZZ6134M93 | VMC API Front-End etat du module EL1134_M93 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15083 | NA | 16416 | 5588 | NA | EL1134_M93 |  | UINT
ZZZ6134M94 | VMC API Front-End etat du module EL1134_M94 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15084 | NA | 16416 | 5590 | NA | EL1134_M94 |  | UINT
ZZZ6134M95 | VMC API Front-End etat du module EL1134_M95 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15085 | NA | 16416 | 5592 | NA | EL1134_M95 |  | UINT
ZZZ6134M96 | VMC API Front-End etat du module EL1134_M96 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15086 | NA | 16416 | 5594 | NA | EL1134_M96 |  | UINT
ZZZ6134M97 | VMC API Front-End etat du module EL1134_M97 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15087 | NA | 16416 | 5596 | NA | EL1134_M97 |  | UINT
ZZZ6134M98 | VMC API Front-End etat du module EL1134_M98 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15088 | NA | 16416 | 5598 | NA | EL1134_M98 |  | UINT
ZZZ6134M99 | VMC API Front-End etat du module EL1134_M99 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15089 | NA | 16416 | 5600 | NA | EL1134_M99 |  | UINT
ZZZ6134M101 | VMC API Front-End etat du module EL1134_M101 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15090 | NA | 16416 | 5602 | NA | EL1134_M101 |  | UINT
ZZZ6134M102 | VMC API Front-End etat du module EL1134_M102 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15091 | NA | 16416 | 5604 | NA | EL1134_M102 |  | UINT
ZZZ6134M103 | VMC API Front-End etat du module EL1134_M103 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15092 | NA | 16416 | 5606 | NA | EL1134_M103 |  | UINT
ZZZ6134M104 | VMC API Front-End etat du module EL1134_M104 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15093 | NA | 16416 | 5608 | NA | EL1134_M104 |  | UINT
ZZZ6134M105 | VMC API Front-End etat du module EL1134_M105 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15094 | NA | 16416 | 5610 | NA | EL1134_M105 |  | UINT
ZZZ6134M106 | VMC API Front-End etat du module EL1134_M106 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15095 | NA | 16416 | 5612 | NA | EL1134_M106 |  | UINT
ZZZ6134M107 | VMC API Front-End etat du module EL1134_M107 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15096 | NA | 16416 | 5614 | NA | EL1134_M107 |  | UINT
ZZZ6134M108 | VMC API Front-End etat du module EL1134_M108 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15097 | NA | 16416 | 5616 | NA | EL1134_M108 |  | UINT
ZZZ6134M109 | VMC API Front-End etat du module EL1134_M109 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15098 | NA | 16416 | 5618 | NA | EL1134_M109 |  | UINT
ZZZ6134M110 | VMC API Front-End etat du module EL1134_M110 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15099 | NA | 16416 | 5620 | NA | EL1134_M110 |  | UINT
ZZZ6134M112 | VMC API Front-End etat du module EL1134_M112 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15100 | NA | 16416 | 5622 | NA | EL1134_M112 |  | UINT
ZZZ6134M113 | VMC API Front-End etat du module EL1134_M113 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15101 | NA | 16416 | 5624 | NA | EL1134_M113 |  | UINT
ZZZ6134M114 | VMC API Front-End etat du module EL1134_M114 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15102 | NA | 16416 | 5626 | NA | EL1134_M114 |  | UINT
ZZZ6134M115 | VMC API Front-End etat du module EL1134_M115 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15103 | NA | 16416 | 5628 | NA | EL1134_M115 |  | UINT
ZZZ6134M116 | VMC API Front-End etat du module EL1134_M116 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15104 | NA | 16416 | 5630 | NA | EL1134_M116 |  | UINT
ZZZ6134M117 | VMC API Front-End etat du module EL1134_M117 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15105 | NA | 16416 | 5632 | NA | EL1134_M117 |  | UINT
ZZZ6134M118 | VMC API Front-End etat du module EL1134_M118 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15106 | NA | 16416 | 5634 | NA | EL1134_M118 |  | UINT
ZZZ6134M119 | VMC API Front-End etat du module EL1134_M119 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15107 | NA | 16416 | 5636 | NA | EL1134_M119 |  | UINT
ZZZ6134M120 | VMC API Front-End etat du module EL1134_M120 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15108 | NA | 16416 | 5638 | NA | EL1134_M120 |  | UINT
ZZZ6134M121 | VMC API Front-End etat du module EL1134_M121 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15109 | NA | 16416 | 5640 | NA | EL1134_M121 |  | UINT
ZZZ6134M123 | VMC API Front-End etat du module EL1134_M123 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15110 | NA | 16416 | 5642 | NA | EL1134_M123 |  | UINT
ZZZ6134M124 | VMC API Front-End etat du module EL1134_M124 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15111 | NA | 16416 | 5644 | NA | EL1134_M124 |  | UINT
ZZZ6134M125 | VMC API Front-End etat du module EL1134_M125 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15112 | NA | 16416 | 5646 | NA | EL1134_M125 |  | UINT
ZZZ6134M126 | VMC API Front-End etat du module EL1134_M126 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15113 | NA | 16416 | 5648 | NA | EL1134_M126 |  | UINT
ZZZ6134M127 | VMC API Front-End etat du module EL1134_M127 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15114 | NA | 16416 | 5650 | NA | EL1134_M127 |  | UINT
ZZZ6134M128 | VMC API Front-End etat du module EL1134_M128 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15115 | NA | 16416 | 5652 | NA | EL1134_M128 |  | UINT
ZZZ6134M129 | VMC API Front-End etat du module EL1134_M129 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15116 | NA | 16416 | 5654 | NA | EL1134_M129 |  | UINT
ZZZ6134M130 | VMC API Front-End etat du module EL1134_M130 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15117 | NA | 16416 | 5656 | NA | EL1134_M130 |  | UINT
ZZZ6134M131 | VMC API Front-End etat du module EL1134_M131 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15118 | NA | 16416 | 5658 | NA | EL1134_M131 |  | UINT
ZZZ6134M132 | VMC API Front-End etat du module EL1134_M132 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15119 | NA | 16416 | 5660 | NA | EL1134_M132 |  | UINT
ZZZ6134M134 | VMC API Front-End etat du module EL1134_M134 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15120 | NA | 16416 | 5662 | NA | EL1134_M134 |  | UINT
ZZZ6134M135 | VMC API Front-End etat du module EL1134_M135 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15121 | NA | 16416 | 5664 | NA | EL1134_M135 |  | UINT
ZZZ6134M136 | VMC API Front-End etat du module EL1134_M136 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15122 | NA | 16416 | 5666 | NA | EL1134_M136 |  | UINT
ZZZ6134M137 | VMC API Front-End etat du module EL1134_M137 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15123 | NA | 16416 | 5668 | NA | EL1134_M137 |  | UINT
ZZZ6134M138 | VMC API Front-End etat du module EL1134_M138 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15124 | NA | 16416 | 5670 | NA | EL1134_M138 |  | UINT
ZZZ6134M139 | VMC API Front-End etat du module EL1134_M139 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15125 | NA | 16416 | 5672 | NA | EL1134_M139 |  | UINT
ZZZ6134M140 | VMC API Front-End etat du module EL1134_M140 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15126 | NA | 16416 | 5674 | NA | EL1134_M140 |  | UINT
ZZZ6134M141 | VMC API Front-End etat du module EL1134_M141 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15127 | NA | 16416 | 5676 | NA | EL1134_M141 |  | UINT
ZZZ6134M142 | VMC API Front-End etat du module EL1134_M142 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15128 | NA | 16416 | 5678 | NA | EL1134_M142 |  | UINT
ZZZ6134M143 | VMC API Front-End etat du module EL1134_M143 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15129 | NA | 16416 | 5680 | NA | EL1134_M143 |  | UINT
ZZZ6134M145 | VMC API Front-End etat du module EL1134_M145 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15130 | NA | 16416 | 5682 | NA | EL1134_M145 |  | UINT
ZZZ6134M146 | VMC API Front-End etat du module EL1134_M146 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15131 | NA | 16416 | 5684 | NA | EL1134_M146 |  | UINT
ZZZ6134M147 | VMC API Front-End etat du module EL1134_M147 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15132 | NA | 16416 | 5686 | NA | EL1134_M147 |  | UINT
ZZZ6134M148 | VMC API Front-End etat du module EL1134_M148 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15133 | NA | 16416 | 5688 | NA | EL1134_M148 |  | UINT
ZZZ6134M149 | VMC API Front-End etat du module EL1134_M149 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15134 | NA | 16416 | 5690 | NA | EL1134_M149 |  | UINT
ZZZ6134M150 | VMC API Front-End etat du module EL1134_M150 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15135 | NA | 16416 | 5692 | NA | EL1134_M150 |  | UINT
ZZZ6134M151 | VMC API Front-End etat du module EL1134_M151 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15136 | NA | 16416 | 5694 | NA | EL1134_M151 |  | UINT
ZZZ6134M152 | VMC API Front-End etat du module EL1134_M152 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15137 | NA | 16416 | 5696 | NA | EL1134_M152 |  | UINT
ZZZ6134M153 | VMC API Front-End etat du module EL1134_M153 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15138 | NA | 16416 | 5698 | NA | EL1134_M153 |  | UINT
ZZZ6134M154 | VMC API Front-End etat du module EL1134_M154 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15139 | NA | 16416 | 5700 | NA | EL1134_M154 |  | UINT
ZZZ6134M156 | VMC API Front-End etat du module EL1134_M156 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 8 (VMC01) | VMC (Z) | [6 empty] | 15140 | NA | 16416 | 5702 | NA | EL1134_M156 |  | UINT
ZZZ6134M157 | VMC API Front-End etat du module EL1134_M157 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 8 (VMC01) | VMC (Z) | [6 empty] | 15141 | NA | 16416 | 5704 | NA | EL1134_M157 |  | UINT
ZZZ6134M158 | VMC API Front-End etat du module EL1134_M158 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 8 (VMC01) | VMC (Z) | [6 empty] | 15142 | NA | 16416 | 5706 | NA | EL1134_M158 |  | UINT
ZZZ6134M159 | VMC API Front-End etat du module EL1134_M159 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 8 (VMC01) | VMC (Z) | [6 empty] | 15143 | NA | 16416 | 5708 | NA | EL1134_M159 |  | UINT
ZZZ6289M187 | VMC API Front-End etat du module EL 2809_M187 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 0 (VMC01) | VMC (Z) | [6 empty] | 15144 | NA | 16416 | 5710 | NA | EL2809_M187 |  | UINT
ZZZ6289M160 | VMC API Front-End etat du module EL 2809_M160 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15145 | NA | 16416 | 5712 | NA | EL2809_M160 |  | UINT
ZZZ6289M161 | VMC API Front-End etat du module EL 2809_M161 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15146 | NA | 16416 | 5714 | NA | EL2809_M161 |  | UINT
ZZZ6289M162 | VMC API Front-End etat du module EL 2809_M162 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15147 | NA | 16416 | 5716 | NA | EL2809_M162 |  | UINT
ZZZ6289M163 | VMC API Front-End etat du module EL 2809_M163 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15148 | NA | 16416 | 5718 | NA | EL2809_M163 |  | UINT
ZZZ6289M164 | VMC API Front-End etat du module EL 2809_M164 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15149 | NA | 16416 | 5720 | NA | EL2809_M164 |  | UINT
ZZZ6289M165 | VMC API Front-End etat du module EL 2809_M165 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15150 | NA | 16416 | 5722 | NA | EL2809_M165 |  | UINT
ZZZ6289M166 | VMC API Front-End etat du module EL 2809_M166 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15151 | NA | 16416 | 5724 | NA | EL2809_M166 |  | UINT
ZZZ6289M167 | VMC API Front-End etat du module EL 2809_M167 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15152 | NA | 16416 | 5726 | NA | EL2809_M167 |  | UINT
ZZZ6289M168 | VMC API Front-End etat du module EL 2809_M168 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15153 | NA | 16416 | 5728 | NA | EL2809_M168 |  | UINT
ZZZ6289M169 | VMC API Front-End etat du module EL 2809_M169 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15154 | NA | 16416 | 5730 | NA | EL2809_M169 |  | UINT
ZZZ6289M170 | VMC API Front-End etat du module EL 2809_M170 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15155 | NA | 16416 | 5732 | NA | EL2809_M170 |  | UINT
ZZZ6289M171 | VMC API Front-End etat du module EL 2809_M171 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15156 | NA | 16416 | 5734 | NA | EL2809_M171 |  | UINT
ZZZ6621M176 | VMC API Front-End etat du module EL6021_M176 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15157 | NA | 16416 | 5736 | NA | EL6021_M176 |  | UINT
ZZZ6621M177 | VMC API Front-End etat du module EL6021_M177 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15158 | NA | 16416 | 5738 | NA | EL6021_M177 |  | UINT
ZZZ6621M178 | VMC API Front-End etat du module EL6021_M178 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15159 | NA | 16416 | 5740 | NA | EL6021_M178 |  | UINT
ZZZ6621M179 | VMC API Front-End etat du module EL6021_M179 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15160 | NA | 16416 | 5742 | NA | EL6021_M179 |  | UINT
ZZZ6621M180 | VMC API Front-End etat du module EL6021_M180 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15161 | NA | 16416 | 5744 | NA | EL6021_M180 |  | UINT
ZZZ6621M181 | VMC API Front-End etat du module EL6021_M181 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15162 | NA | 16416 | 5746 | NA | EL6021_M181 |  | UINT
ZZZ6621M182 | VMC API Front-End etat du module EL6021_M182 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15163 | NA | 16416 | 5748 | NA | EL6021_M182 |  | UINT
ZZZ6621M183 | VMC API Front-End etat du module EL6021_M183 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15164 | NA | 16416 | 5750 | NA | EL6021_M183 |  | UINT
ZZZ6621M184 | VMC API Front-End etat du module EL6021_M184 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15165 | NA | 16416 | 5752 | NA | EL6021_M184 |  | UINT
ZZZ6621M185 | VMC API Front-End etat du module EL6021_M185 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15166 | NA | 16416 | 5754 | NA | EL6021_M185 |  | UINT
ZZZ6189M186 | VMC API Front-End etat du module EL1809_M186 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 0 (VMC01) | VMC (Z) | [6 empty] | 15167 | NA | 16416 | 5756 | NA | EL1809_M186 |  | UINT
ZZZ6670M188 | VMC API Front-End etat du module EL6070_M188 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 0 (VMC01) | VMC (Z) | [6 empty] | 15168 | NA | 16416 | 5758 | NA | EL6070_M188 |  | UINT
ZZZ6110EC0 | VMC Front-End etat du module EK1110_EC0 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 0 (VMC01) | VMC (Z) | [6 empty] | 15169 | NA | 16416 | 5760 | NA | EK1110_EC0 |  | UINT
ZZZ6100EC1 | VMC Front-End etat du module EK1100_EC1 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 1 (VMC01) | VMC (Z) | [6 empty] | 15170 | NA | 16416 | 5762 | NA | EK1100_EC1 |  | UINT
ZZZ6100EC2 | VMC Front-End etat du module EK1100_EC2 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 2 (VMC01) | VMC (Z) | [6 empty] | 15171 | NA | 16416 | 5764 | NA | EK1100_EC2 |  | UINT
ZZZ6100EC3 | VMC Front-End etat du module EK1100_EC3 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 3 (VMC01) | VMC (Z) | [6 empty] | 15172 | NA | 16416 | 5766 | NA | EK1100_EC3 |  | UINT
ZZZ6100EC4 | VMC Front-End etat du module EK1100_EC4 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 4 (VMC01) | VMC (Z) | [6 empty] | 15173 | NA | 16416 | 5768 | NA | EK1100_EC4 |  | UINT
ZZZ6100EC5 | VMC Front-End etat du module EK1100_EC5 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 5 (VMC01) | VMC (Z) | [6 empty] | 15174 | NA | 16416 | 5770 | NA | EK1100_EC5 |  | UINT
ZZZ6100EC6 | VMC Front-End etat du module EK1100_EC6 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 6 (VMC01) | VMC (Z) | [6 empty] | 15175 | NA | 16416 | 5772 | NA | EK1100_EC6 |  | UINT
ZZZ6100EC7 | VMC Front-End etat du module EK1100_EC7 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 7 (VMC01) | VMC (Z) | [6 empty] | 15176 | NA | 16416 | 5774 | NA | EK1100_EC7 |  | UINT
ZZZ6100EC8 | VMC Front-End etat du module EK1100_EC8 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 8 (VMC01) | VMC (Z) | [6 empty] | 15177 | NA | 16416 | 5776 | NA | EK1100_EC8 |  | UINT
ZZZ6100EC9 | VMC Front-End etat du module EK1100_EC9 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15178 | NA | 16416 | 5778 | NA | EK1100_EC9 |  | UINT
ZZZ6941M174 | VMC Front-End etat du module EL9410_M174 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15180 | NA | 16416 | 5782 | NA | EL9410_M174 |  | UINT
ZZZ6324M172 | VMC Front-End etat du module EL3124_M172 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15183 | NA | 16416 | 5788 | NA | EL3124_M172 |  | UINT
ZZZ6324M173 | VMC Front-End etat du module EL3124_M173 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15184 | NA | 16416 | 5790 | NA | EL3124_M173 |  | UINT
ZZZ6324M175 | VMC Front-End etat du module EL3124_M175 | CR | N | INT | 0 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 9 (VMC01) | VMC (Z) | [6 empty] | 15186 | NA | 16416 | 5792 | NA | EL3124_M175 |  | UINT
QKO6000 | CR Marche Arret acquisition de capteurs SHM | CR | N | TIP | 1 | H | [26 empty] | SHM |  |  | SHM60; | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 11 | [8 empty] | I16
OVM6318DI | Vanne OVM6318 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6318F;OVM6318O |  |  |  |  | MG61;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6306DI | Vanne OVM6306 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6306F;OVM6306O |  |  |  |  | MG61;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6323DI | Vanne OVM6323 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6323F;OVM6323O |  |  |  |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6324DI | Vanne OVM6324 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6324F;OVM6324O |  |  |  |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6325DI | Vanne OVM6325 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6325F;OVM6325O |  |  |  |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6301DI | Vanne OVM6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6301F;OVM6301O |  |  |  |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6314DI | Vanne OVM6314 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6314F;OVM6314O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6315DI | Vanne OVP6315 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6315F;OVP6315O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6311DI | Vanne OVP6311 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6311F;OVP6311O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6310DI | Vanne OVP6310 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6310F;OVP6310O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6309DI | Vanne OVP6309 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6309F;OVP6309O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6308DI | Vanne OVP6308 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6308F;OVP6308O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6307DI | Vanne OVP6307 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6307F;OVP6307O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6306DI | Vanne OVP6306 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6306F;OVP6306O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6312DI | Vanne OVM6312 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6312F;OVM6312O |  |  |  |  | MG63 | Moyens Generaux (MG)
OVM6308DI | Vanne OVM6308 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6308F;OVM6308O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6390DI | Vanne OVM6390 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6390F;OVM6390O |  |  |  |  | MG63 | Moyens Generaux (MG)
OVM6313DI | Vanne OVM6313 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6313F;OVM6313O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6311DI | Vanne OVM6311 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6311F;OVM6311O |  |  |  |  | MG63;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6310DI | Vanne OVM6310 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6310F;OVM6310O |  |  |  |  | MG63;VG01;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6309DI | Vanne OVM6309 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6309F;OVM6309O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6305DI | Vanne OVP6305 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6305F;OVP6305O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6304DI | Vanne OVP6304 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6304F;OVP6304O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6303DI | Vanne OVP6303 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6303F;OVP6303O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6302DI | Vanne OVP6302 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6302F;OVP6302O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6301DI | Vanne OVP6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6301F;OVP6301O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6317DI | Vanne OVM6317 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6317F;OVM6317O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6312DI | Vanne OVP6312 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6312F;OVP6312O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6313DI | Vanne OVP6313 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6313F;OVP6313O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6314DI | Vanne OVP6314 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6314F;OVP6314O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6344DI | Vanne OVM6344 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6344F;OVM6344O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6356DI | Vanne OVM6356 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6356F;OVM6356O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6334DI | Vanne OVM6334 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6334F;OVM6334O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6332DI | Vanne OVM6332 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6332F;OVM6332O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6333DI | Vanne OVM6333 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6333F;OVM6333O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6330DI | Vanne OVM6330 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6330F;OVM6330O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6331DI | Vanne OVM6331 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6331F;OVM6331O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6355DI | Vanne OVM6355 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6355F;OVM6355O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OPP6301DI | Pompe OPP6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OPP6301A;OPP6301M |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OPP6302DI | Pompe OPP6302 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OPP6302A;OPP6302M |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6386DI | Vanne OVM6386 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6386F;OVM6386O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6387DI | Vanne OVM6387 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6387F;OVM6387O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6388DI | Vanne OVM6388 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6388F;OVM6388O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6382DI | Vanne OVM6382 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6382F;OVM6382O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6376DI | Vanne OVM6376 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6376F;OVM6376O |  |  |  |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6377DI | Vanne OVM6377 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6377F;OVM6377O |  |  |  |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6378DI | Vanne OVM6378 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6378F;OVM6378O |  |  |  |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6372DI | Vanne OVM6372 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6372F;OVM6372O |  |  |  |  | MG67;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NPP6001DI | Pompe NPP6001 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NPP6001A;NPP6001M |  |  |  |  | MG67 | Moyens Generaux (MG)
UVM6303DI | Vanne UVM6303 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6303F;UVM6303O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6304DI | Vanne UVM6304 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6304F;UVM6304O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6305DI | Vanne UVM6305 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6305F;UVM6305O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6302DI | Vanne UVM6302 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6302F;UVM6302O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6301DI | Vanne UVM6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6301F;UVM6301O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6306DI | Vanne UVM6306 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6306F;UVM6306O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6307DI | Vanne UVM6307 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UVM6307F;UVM6307O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UPP6301DI | Pompe UPP6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | UPP6301A;UPP6301M |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6303DI | Vanne NVM6303 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6303F;NVM6303O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6304DI | Vanne NVM6304 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6304F;NVM6304O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6305DI | Vanne NVM6305 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6305F;NVM6305O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6302DI | Vanne NVM6302 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6302F;NVM6302O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6301DI | Vanne NVM6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6301F;NVM6301O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6306DI | Vanne NVM6306 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6306F;NVM6306O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6307DI | Vanne NVM6307 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NVM6307F;NVM6307O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NPP6301DI | Pompe NPP6301 Discordance | CR | N | CAL | 1 | F | [22 empty] | AND |  | NPP6301A;NPP6301M |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
EQMT6002AE | IM Arrivee CAT II 1D60: Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQM6002O ; EQM6002F ;
EQMT6001AE | IM Arrivee CAT I 1D60: Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQM6001O ; EQM6001F ;
EQF6950AE | Disjoncteur Type 2 QF7950 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQF6950O; EQF6950F ; EQF6950D ; EQF6950DE | [5 empty] | E62 | Energie TGBT et UPS VEGA (E)
EQF6951AE | Disjoncteur Type 2 QF7951 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQF6951O; EQF6951F ; EQF6951D ; EQF6951DE | [5 empty] | E62 | Energie TGBT et UPS VEGA (E)
EQF6952AE | Disjoncteur Type 2 QF7952 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQF6952O; EQF6952F ; EQF6952D ; EQF6952DE | [5 empty] | E62 | Energie TGBT et UPS VEGA (E)
EQF6001AE | Disjoncteur Type 2 QF7001 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQF6001O ; EQF6001F ; EQF6001D ; EQF6001DE | [5 empty] | E61 | Energie TGBT et UPS VEGA (E)
EQF6002AE | Disjoncteur Type 2 QF7002 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQF6002O ; EQF6002F ; EQF6002D ; EQF6002DE | [5 empty] | E61 | Energie TGBT et UPS VEGA (E)
EQF6003AE | Disjoncteur Type 2 QF7003 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | EQF6003O ; EQF6003F ; EQF6003D ; EQF6003DE | [5 empty] | E61 | Energie TGBT et UPS VEGA (E)
ESA6030AE | Interrupteur SA7030 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6030O ; ESA6030F | [5 empty] | E64 | Energie TGBT et UPS VEGA (E)
ESA6031AE | Interrupteur SA7031 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6031O ; ESA6031F | [5 empty] | E64 | Energie TGBT et UPS VEGA (E)
ESA6032AE | Interrupteur SA7032 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6032O ; ESA6032F | [5 empty] | E64 | Energie TGBT et UPS VEGA (E)
ESA6033AE | Interrupteur SA7033 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6033O ; ESA6033F | [5 empty] | E64 | Energie TGBT et UPS VEGA (E)
ESA6009AE | Interrupteur SA7009 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6009O ; ESA6009F | [5 empty] | E65 | Energie TGBT et UPS VEGA (E)
ESA6010AE | Interrupteur SA7010 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6010O ; ESA6010F | [5 empty] | E65 | Energie TGBT et UPS VEGA (E)
ESA6005AE | Interrupteur SA7005 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6005O ; ESA6005F | [5 empty] | E70 | Energie TGBT et UPS VEGA (E)
ESA6006AE | Interrupteur SA7006 Aucun Etat | CR | N | CAL | 1 | E | [22 empty] | NOR | ESA6006O ; ESA6006F | [5 empty] | E70 | Energie TGBT et UPS VEGA (E)
SSP6001QA | Sirene ZLV SSP6001 Arret | CR | N | CAL | 1 | S | [22 empty] | NOR | SSP6001QC ; SSP6001QM | SSP6001QM;SSP6001QC |  |  |  |  | MG71 | Moyens Generaux (MG)
OSY6370 | Synthese vannes manuelles de purges fermees | CR | N | CAL | 1 | F | [22 empty] | AND | OVM6373F ; OVM6374F ; OVM6375F ; OVM6379F | OVM6373F;OVM6374F;OVM6375F;OVM6379F |  |  |  |  | MG67 | Moyens Generaux (MG)
OSY6380 | Synthese vannes manuelles de purges fermees | CR | N | CAL | 1 | F | [22 empty] | AND | OVM6383F ; OVM6384F ; OVM6385F ; OVM6389F | OVM6383F;OVM6384F;OVM6385F;OVM6389F |  |  |  |  | MG66 | Moyens Generaux (MG)
ZNC6628NH1 | ETAT CONNEXION MODULE SCSI HLCS-1 | CR | N | INT | 0 | Z | [26 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | Boolean
ZNC6629NH1 | FAULT SYNCHRONISATION MODULE SCSI HLCS-1 | CR | N | INT | 0 | Z | [26 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | Boolean
ZNT6100 | NOM COMMUNICATION NTP SERVER | CR | N | INT | 0 | Z | [26 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | STRING
ZNT6631 | ETAT COMMUNICATION NTP SERVER | CR | N | INT | 0 | Z | [26 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | U8
ZNT6632 | TSS TU DISTRIBUTION MODE | CR | N | INT | 0 | Z | [26 empty] | MTCP |  |  | VMC03 | VMC (Z) | NEW | [12 empty] | U8
QIM6201XY | Axe inclinaison MAX MG niveau 21200, faisceau 1 est | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6201 >=5000 | QIM6201 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6202XY | Axe inclinaison MAX MG niveau 21200, faisceau 2 ouest | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6202 >=5000 | QIM6202 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6203XY | Axe inclinaison MAX MG niveau 26600, faisceau 1 est | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6203 >=5000 | QIM6203 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6204XY | Axe inclinaison MAX MG niveau 26600, faisceau 2 ouest | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6204 >=5000 | QIM6204 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6205XY | Axe inclinaison MAX MG niveau 31800, faisceau 1 est | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6205 >=5000 | QIM6205 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6206XY | Axe inclinaison MAX MG niveau 31800, faisceau 2 ouest | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6206 >=5000 | QIM6206 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6207XY | Axe inclinaison MAX MG niveau 39600, faisceau 1 est | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6207 >=5000 | QIM6207 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6208XY | Axe inclinaison MAX MG niveau 39600, faisceau 2 ouest | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6208 >=5000 | QIM6208 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6209XY | Axe inclinaison MAX MG niveau 47400, faisceau 1 est | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6209 >=5000 | QIM6209 |  |  |  |  | SHM65MG | Structural Health Monitoring (SHM)
QIM6210XY | Axe inclinaison MAX MG niveau 47400, faisceau 2 ouest | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6210 >=5000 | QIM6210 |  |  |  |  | SHM65MG | Structural Health Monitoring (SHM)
QIM6211XY | Axe inclinaison MAX MG niveau 54000, faisceau 1 est | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6211 >=5000 | QIM6211 |  |  |  |  | SHM67MG | Structural Health Monitoring (SHM)
QIM6212XY | Axe inclinaison MAX MG niveau 54000, faisceau 2 ouest | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6212 >=5000 | QIM6212 |  |  |  |  | SHM67MG | Structural Health Monitoring (SHM)
QIM6713XY | Axe inclinaison MAX MAST niveau 21200, façade nord | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6713 >=5000 | QIM6713 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6714XY | Axe inclinaison MAX MAST niveau 29200, façade nord | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6714 >=5000 | QIM6714 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6715XY | Axe inclinaison MAX MAST niveau 37000, façade nord | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6715 >=5000 | QIM6715 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6716XY | Axe inclinaison MAX MAST niveau 44800, façade nord | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6716 >=5000 | QIM6716 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6117XY | Axe inclinaison MAX BUNKER des pipes R100-1_P1, panneau O 800-3 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6117 >=5000 | QIM6117 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6118XY | Axe inclinaison MAX BUNKER des pipes R100-1_P2, panneau HA 600-1 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6118 >=5000 | QIM6118 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6119XY | Axe inclinaison MAX BUNKER des pipes R100-1_P3, panneau R 700-3 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6119 >=5000 | QIM6119 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6120XY | Axe inclinaison MAX BUNKER des pipes R100-1_P4, panneau R 700-4 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6120 >=5000 | QIM6120 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6121XY | Axe inclinaison MAX BUNKER des pipes R100-1_P5, panneau R 700-4 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6121 >=5000 | QIM6121 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6122XY | Axe inclinaison MAX BUNKER mur, R100-1_WALL | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6122 >=5000 | QIM6122 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6123XY | Axe inclinaison MAX BUNKER R100-1_PILLAR | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6123 >=5000 | QIM6123 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6124XY | Axe inclinaison MAX BUNKER armoire électrique R103, rack1 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6124 >=5000 | QIM6124 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6125XY | Axe inclinaison MAX BUNKER armoire électrique R103, rack2 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6125 >=5000 | QIM6125 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6126XY | Axe inclinaison MAX BUNKER armoire électrique R103, rack3 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6126 >=5000 | QIM6126 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6127XY | Axe inclinaison MAX BUNKER armoire électrique R103, rack 4 nord | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6127 >=5000 | QIM6127 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6128XY | Axe inclinaison MAX BUNKER armoire électrique R103, rack 4 au sud | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6128 >=5000 | QIM6128 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6129XY | Axe inclinaison MAX BUNKER mur 1, R103 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6129 >=5000 | QIM6129 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6130XY | Axe inclinaison MAX BUNKER mur 2, R103 | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6130 >=5000 | QIM6130 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6231XY | Axe inclinaison MAX MG CRANE TCMS faisceau SE | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6231 >=5000 | QIM6231 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
QIM6232XY | Axe inclinaison MAX MG CRANE TCMS faisceau SW | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6232 >=5000 | QIM6232 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
QIM6233XY | Axe inclinaison MAX MG CRANE TCMS faisceau NE | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6233 >=5000 | QIM6233 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
QIM6234XY | Axe inclinaison MAX MG CRANE TCMS faisceau NW | CR | N | CAL | 1 | H | [22 empty] | FORM | QIM6234 >=5000 | QIM6234 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
OVM6318AE | Vanne OVM6318 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6318F;OVM6318O |  |  |  |  | MG61;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6306AE | Vanne OVM6306 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6306F;OVM6306O |  |  |  |  | MG61;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6323AE | Vanne OVM6323 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6323F;OVM6323O |  |  |  |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6324AE | Vanne OVM6324 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6324F;OVM6324O |  |  |  |  | MG61;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6325AE | Vanne OVM6325 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6325F;OVM6325O |  |  |  |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6301AE | Vanne OVM6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6301F;OVM6301O |  |  |  |  | MG61;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6314AE | Vanne OVM6314 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6314F;OVM6314O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6315AE | Vanne OVP6315 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6315F;OVP6315O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6311AE | Vanne OVP6311 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6311F;OVP6311O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6310AE | Vanne OVP6310 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6310F;OVP6310O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6309AE | Vanne OVP6309 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6309F;OVP6309O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6308AE | Vanne OVP6308 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6308F;OVP6308O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6307AE | Vanne OVP6307 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6307F;OVP6307O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6306AE | Vanne OVP6306 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6306F;OVP6306O |  |  |  |  | MG62;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6312AE | Vanne OVM6312 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6312F;OVM6312O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6308AE | Vanne OVM6308 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6308F;OVM6308O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6390AE | Vanne OVM6390 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6390F;OVM6390O |  |  |  |  | MG63 | Moyens Generaux (MG)
OVM6313AE | Vanne OVM6313 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6313F;OVM6313O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6311AE | Vanne OVM6311 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6311F;OVM6311O |  |  |  |  | MG63;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6310AE | Vanne OVM6310 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6310F;OVM6310O |  |  |  |  | MG63;VG01 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6309AE | Vanne OVM6309 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6309F;OVM6309O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6305AE | Vanne OVP6305 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6305F;OVP6305O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6304AE | Vanne OVP6304 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6304F;OVP6304O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6303AE | Vanne OVP6303 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6303F;OVP6303O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6302AE | Vanne OVP6302 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6302F;OVP6302O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6301AE | Vanne OVP6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6301F;OVP6301O |  |  |  |  | MG63;VG02 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6317AE | Vanne OVM6317 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6317F;OVM6317O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6312AE | Vanne OVP6312 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6312F;OVP6312O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6313AE | Vanne OVP6313 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6313F;OVP6313O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVP6314AE | Vanne OVP6314 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6314F;OVP6314O |  |  |  |  | MG64;VG03 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6344AE | Vanne OVM6344 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6344F;OVM6344O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6356AE | Vanne OVM6356 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6356F;OVM6356O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6334AE | Vanne OVM6334 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6334F;OVM6334O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6332AE | Vanne OVM6332 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6332F;OVM6332O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6333AE | Vanne OVM6333 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6333F;OVM6333O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6330AE | Vanne OVM6330 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6330F;OVM6330O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6331AE | Vanne OVM6331 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6331F;OVM6331O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6355AE | Vanne OVM6355 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6355F;OVM6355O |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OPP6301AE | Pompe OPP6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OPP6301A;OPP6301M |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OPP6302AE | Pompe OPP6302 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OPP6302A;OPP6302M |  |  |  |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6386AE | Vanne OVM6386 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6386F;OVM6386O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6387AE | Vanne OVM6387 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6387F;OVM6387O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6388AE | Vanne OVM6388 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6388F;OVM6388O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6382AE | Vanne OVM6382 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6382F;OVM6382O |  |  |  |  | MG66;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6376AE | Vanne OVM6376 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6376F;OVM6376O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6377AE | Vanne OVM6377 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6377F;OVM6377O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6378AE | Vanne OVM6378 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6378F;OVM6378O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
OVM6372AE | Vanne OVM6372 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6372F;OVM6372O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NPP6001AE | Pompe NPP6001 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NPP6001A;NPP6001M |  |  |  |  | MG67 | Moyens Generaux (MG)
UVM6303AE | Vanne UVM6303 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6303F;UVM6303O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6304AE | Vanne UVM6304 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6304F;UVM6304O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6305AE | Vanne UVM6305 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6305F;UVM6305O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6302AE | Vanne UVM6302 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6302F;UVM6302O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6301AE | Vanne UVM6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6301F;UVM6301O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6306AE | Vanne UVM6306 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6306F;UVM6306O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UVM6307AE | Vanne UVM6307 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UVM6307F;UVM6307O |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
UPP6301AE | Pompe UPP6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | UPP6301A;UPP6301M |  |  |  |  | MG69;VG05 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6303AE | Vanne NVM6303 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6303F;NVM6303O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6304AE | Vanne NVM6304 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6304F;NVM6304O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6305AE | Vanne NVM6305 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6305F;NVM6305O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6302AE | Vanne NVM6302 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6302F;NVM6302O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6301AE | Vanne NVM6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6301F;NVM6301O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6306AE | Vanne NVM6306 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6306F;NVM6306O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NVM6307AE | Vanne NVM6307 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NVM6307F;NVM6307O |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
NPP6301AE | Pompe NPP6301 Aucun Etat | CR | N | CAL | 1 | F | [22 empty] | NOR |  | NPP6301A;NPP6301M |  |  |  |  | MG70;VG06 | Moyens Generaux (MG); Process Fluide et Energie General (VG)
GVM6004DI2 | Vanne GVM6004 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | GVM6004O2 ; GVM6004F2 |  |  |  |  | HVAC03 | HVAC
GVM6003DI2 | Vanne GVM6003 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | GVM6003O2 ; GVM6003F2 |  |  |  |  | HVAC03 | HVAC
GVM6002DI2 | Vanne GVM6002 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | GVM6002O2 ; GVM6002F2 |  |  |  |  | HVAC03 | HVAC
CVM6002DI2 | Vanne CVM6002 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6002O2 ; CVM6002F2 |  |  |  |  | HVAC03 | HVAC
GVM6001DI2 | Vanne GVM6001 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | GVM6001O2 ; GVM6001F2 |  |  |  |  | HVAC03 | HVAC
CVM6001DI2 | Vanne CVM6001 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6001O2 ; CVM6001F2 |  |  |  |  | HVAC03 | HVAC
GVM6005DI2 | Vanne GVM6005 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | GVM6005O2 ; GVM6005F2 |  |  |  |  | HVAC03 | HVAC
GVM6006DI2 | Vanne GVM6006 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | GVM6006O2 ; GVM6006F2 |  |  |  |  | HVAC03 | HVAC
CVM6005DI2 | Vanne CVM6005 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6005O2 ; CVM6005F2 |  |  |  |  | HVAC03 | HVAC
CVM6006DI2 | Vanne CVM6006 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6006O2 ; CVM6006F2 |  |  |  |  | HVAC03 | HVAC
CVM6004DI2 | Vanne CVM6004 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6004O2 ; CVM6004F2 |  |  |  |  | HVAC03 | HVAC
CVM6003DI2 | Vanne CVM6003 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6003O2 ; CVM6003F2 |  |  |  |  | HVAC03 | HVAC
CVM6001DI | Vanne CVM6001 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6001O ; CVM6001F |  |  |  |  | HVAC03 | HVAC
CVM6002DI | Vanne CVM6002 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6002O ; CVM6002F |  |  |  |  | HVAC03 | HVAC
CVM6003DI | Vanne CVM6003 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | CVM6003O ; CVM6003F |  |  |  |  | HVAC03 | HVAC
VRP6127DI2 | Registre VRP6127 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6127O2 ; VRP6127F2 |  |  |  |  | HVAC04 | HVAC
VRP6127DI1 | Registre VRP6127 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6127O1 ; VRP6127F1 |  |  |  |  | HVAC04 | HVAC
VRP6118DI3 | Registre VRP6118 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6118O3 ; VRP6118F3 |  |  |  |  | HVAC04 | HVAC
VRP6118DI1 | Registre VRP6118 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6118O1 ; VRP6118F1 |  |  |  |  | HVAC04 | HVAC
VRP6118DI2 | Registre VRP6118 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6118O2 ; VRP6118F2 |  |  |  |  | HVAC04;HVAC05;HVAC06 | HVAC
VRP6118DI4 | Registre VRP6118 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6118O4 ; VRP6118F4 |  |  |  |  | HVAC04;HVAC05;HVAC06 | HVAC
VRP6004DI1 | Registre VRP6004 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6004O1 ; VRP6004F1 |  |  |  |  | HVAC05 | HVAC
VRP6004DI2 | Registre VRP6004 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6004O2 ; VRP6004F2 |  |  |  |  | HVAC05 | HVAC
VRP6007DI1 | Registre VRP6007 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6007O1 ; VRP6007F1 |  |  |  |  | HVAC05 | HVAC
VRP6007DI2 | Registre VRP6007 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6007O2 ; VRP6007F2 |  |  |  |  | HVAC05 | HVAC
VRP6008DI1 | Registre VRP6008 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6008O1 ; VRP6008F1 |  |  |  |  | HVAC05 | HVAC
VRP6008DI2 | Registre VRP6008 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6008O2 ; VRP6008F2 |  |  |  |  | HVAC05 | HVAC
VRP6009DI1 | Registre VRP6009 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6009O1 ; VRP6009F1 |  |  |  |  | HVAC05 | HVAC
VRP6009DI2 | Registre VRP6009 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6009O2 ; VRP6009F2 |  |  |  |  | HVAC05 | HVAC
VRP6002DI1 | Registre VRP6002 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6002O1 ; VRP6002F1 |  |  |  |  | HVAC05 | HVAC
VRP6013DI1 | Registre VRP6013 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6013O1 ; VRP6013F1 |  |  |  |  | HVAC05 | HVAC
VRP6002DI2 | Registre VRP6002 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6002O2 ; VRP6002F2 |  |  |  |  | HVAC05 | HVAC
VRP6101DI11 | Registre VRP6101 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6101O11 ; VRP6101F11 |  |  |  |  | HVAC05 | HVAC
VRP6101DI12 | Registre VRP6101 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6101O12 ; VRP6101F12 |  |  |  |  | HVAC05 | HVAC
VRP6103DI1 | Registre VRP6103 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6103O1 ; VRP6103F1 |  |  |  |  | HVAC05 | HVAC
VRP6103DI2 | Registre VRP6103 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6103O2 ; VRP6103F2 |  |  |  |  | HVAC05 | HVAC
VRP6111DI1 | Registre VRP6111 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6111O1 ; VRP6111F1 |  |  |  |  | HVAC05 | HVAC
VRP6111DI2 | Registre VRP6111 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6111O2 ; VRP6111F2 |  |  |  |  | HVAC05 | HVAC
VRP6112DI1 | Registre VRP6112 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6112O1 ; VRP6112F1 |  |  |  |  | HVAC05 | HVAC
VRP6112DI2 | Registre VRP6112 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6112O2 ; VRP6112F2 |  |  |  |  | HVAC05 | HVAC
VRP6113DI1 | Registre VRP6113 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6113O1 ; VRP6113F1 |  |  |  |  | HVAC05 | HVAC
VRP6113DI2 | Registre VRP6113 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6113O2 ; VRP6113F2 |  |  |  |  | HVAC05 | HVAC
VRP6115DI1 | Registre VRP6115 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6115O1 ; VRP6115F1 |  |  |  |  | HVAC05 | HVAC
VRP6115DI2 | Registre VRP6115 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6115O2 ; VRP6115F2 |  |  |  |  | HVAC05 | HVAC
VRP6116DI1 | Registre VRP6116 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6116O1 ; VRP6116F1 |  |  |  |  | HVAC06 | HVAC
VRP6116DI2 | Registre VRP6116 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6116O2 ; VRP6116F2 |  |  |  |  | HVAC06 | HVAC
VRP6106DI1 | Registre VRP6106 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6106O1 ; VRP6106F1 |  |  |  |  | HVAC06 | HVAC
VRP6100DI2 | Registre VRP6100 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6100O2 ; VRP6100F2 |  |  |  |  | HVAC06 | HVAC
VRP6104DI1 | Registre VRP6104 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6104O1 ; VRP6104F1 |  |  |  |  | HVAC06 | HVAC
VRP6104DI2 | Registre VRP6104 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6104O2 ; VRP6104F2 |  |  |  |  | HVAC06 | HVAC
VRP6107DI1 | Registre VRP6107 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6107O1 ; VRP6107F1 |  |  |  |  | HVAC06 | HVAC
VRP6107DI2 | Registre VRP6107 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6107O2 ; VRP6107F2 |  |  |  |  | HVAC06 | HVAC
VRP6117DI1 | Registre VRP6117 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6117O1 ; VRP6117F1 |  |  |  |  | HVAC06 | HVAC
VRP6012DI1 | Registre VRP6012 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6012O1 ; VRP6012F1 |  |  |  |  | HVAC06 | HVAC
VRP6012DI2 | Registre VRP6012 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6012O2 ; VRP6012F2 |  |  |  |  | HVAC06 | HVAC
VCF6003DI1 | Clapet coupe feu VCF6003 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6003O1 ; VCF6003F1 |  |  |  |  | HVAC10 | HVAC
VCF6004DI1 | Clapet coupe feu VCF6004 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6004O1 ; VCF6004F1 |  |  |  |  | HVAC10 | HVAC
VCF6006DI1 | Clapet coupe feu VCF6006 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6006O1 ; VCF6006F1 |  |  |  |  | HVAC10 | HVAC
VCF6012DI1 | Clapet coupe feu VCF6012 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6012O1 ; VCF6012F1 |  |  |  |  | HVAC10 | HVAC
VCF6012DI3 | Clapet coupe feu VCF6012 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6012O3 ; VCF6012F3 |  |  |  |  | HVAC10 | HVAC
VCF6013DI3 | Clapet coupe feu VCF6013 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6013O3 ; VCF6013F3 |  |  |  |  | HVAC10 | HVAC
VCF6100DI1 | Clapet coupe feu VCF6100 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6100O1 ; VCF6100F1 |  |  |  |  | HVAC10 | HVAC
VCF6103DI1 | Clapet coupe feu VCF6103 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6103O1 ; VCF6103F1 |  |  |  |  | HVAC10 | HVAC
VCF6103DI2 | Clapet coupe feu VCF6103 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6103O2 ; VCF6103F2 |  |  |  |  | HVAC10 | HVAC
VCF6111DI1 | Clapet coupe feu VCF6111 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6111O1 ; VCF6111F1 |  |  |  |  | HVAC10 | HVAC
VCF6117DI2 | Clapet coupe feu VCF6117 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6117O2 ; VCF6117F2 |  |  |  |  | HVAC10 | HVAC
VCF6117DI1 | Clapet coupe feu VCF6117 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6117O1 ; VCF6117F1 |  |  |  |  | HVAC10 | HVAC
VCF6118DI1 | Clapet coupe feu VCF6118 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6118O1 ; VCF6118F1 |  |  |  |  | HVAC10 | HVAC
VCF6001DI1 | Clapet coupe feu VCF6001 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6001O1 ; VCF6001F1 |  |  |  |  | HVAC10 | HVAC
VCF6003DI3 | Clapet coupe feu VCF6003 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6003O3 ; VCF6003F3 |  |  |  |  | HVAC10 | HVAC
VCF6003DI2 | Clapet coupe feu VCF6003 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6003O2 ; VCF6003F2 |  |  |  |  | HVAC10 | HVAC
VCF6006DI2 | Clapet coupe feu VCF6006 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6006O2 ; VCF6006F2 |  |  |  |  | HVAC10 | HVAC
VCF6007DI1 | Clapet coupe feu VCF6007 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6007O1 ; VCF6007F1 |  |  |  |  | HVAC10 | HVAC
VCF6007DI2 | Clapet coupe feu VCF6007 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6007O2 ; VCF6007F2 |  |  |  |  | HVAC10 | HVAC
VCF6008DI1 | Clapet coupe feu VCF6008 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6008O1 ; VCF6008F1 |  |  |  |  | HVAC10 | HVAC
VCF6008DI2 | Clapet coupe feu VCF6008 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6008O2 ; VCF6008F2 |  |  |  |  | HVAC10 | HVAC
VCF6009DI1 | Clapet coupe feu VCF6009 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6009O1 ; VCF6009F1 |  |  |  |  | HVAC10 | HVAC
VCF6012DI2 | Clapet coupe feu VCF6012 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6012O2 ; VCF6012F2 |  |  |  |  | HVAC10 | HVAC
VCF6013DI1 | Clapet coupe feu VCF6013 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6013O1 ; VCF6013F1 |  |  |  |  | HVAC10 | HVAC
VCF6013DI2 | Clapet coupe feu VCF6013 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6013O2 ; VCF6013F2 |  |  |  |  | HVAC10 | HVAC
VCF6100DI2 | Clapet coupe feu VCF6100 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6100O2 ; VCF6100F2 |  |  |  |  | HVAC10 | HVAC
VCF6106DI1 | Clapet coupe feu VCF6106 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6106O1 ; VCF6106F1 |  |  |  |  | HVAC10 | HVAC
VCF6108DI1 | Clapet coupe feu VCF6108 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6108O1 ; VCF6108F1 |  |  |  |  | HVAC10 | HVAC
VCF6111DI2 | Clapet coupe feu VCF6111 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6111O2 ; VCF6111F2 |  |  |  |  | HVAC10 | HVAC
VCF6112DI1 | Clapet coupe feu VCF6112 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6112O1 ; VCF6112F1 |  |  |  |  | HVAC10 | HVAC
VCF6113DI1 | Clapet coupe feu VCF6113 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6113O1 ; VCF6113F1 |  |  |  |  | HVAC10 | HVAC
VCF6115DI1 | Clapet coupe feu VCF6115 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6115O1 ; VCF6115F1 |  |  |  |  | HVAC10 | HVAC
VCF6115DI2 | Clapet coupe feu VCF6115 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6115O2 ; VCF6115F2 |  |  |  |  | HVAC10 | HVAC
VCF6115DI3 | Clapet coupe feu VCF6115 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6115O3 ; VCF6115F3 |  |  |  |  | HVAC10 | HVAC
VCF6116DI1 | Clapet coupe feu VCF6116 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6116O1 ; VCF6116F1 |  |  |  |  | HVAC10 | HVAC
VCF6118DI2 | Clapet coupe feu VCF6118 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6118O2 ; VCF6118F2 |  |  |  |  | HVAC10 | HVAC
VCF6126DI1 | Clapet coupe feu VCF6126 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VCF6126O1 ; VCF6126F1 |  |  |  |  | HVAC10 | HVAC
VRP6401DI1 | Registre VRP6401 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6401O1 ; VRP6401F1 |  |  |  |  | HVAC13 | HVAC
VRP6401DI2 | Registre VRP6401 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6401O2 ; VRP6401F2 |  |  |  |  | HVAC13;HVAC15 | HVAC
VRP6401DI3 | Registre VRP6401 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6401O3 ; VRP6401F3 |  |  |  |  | HVAC13 | HVAC
VRP6401DI4 | Registre VRP6401 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6401O4 ; VRP6401F4 |  |  |  |  | HVAC13;HVAC15 | HVAC
VRP6201DI1 | Registre VRP6201 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6201O1 ; VRP6201F1 |  |  |  |  | HVAC14 | HVAC
VRP6201DI5 | Registre VRP6201 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6201O5 ; VRP6201F5 |  |  |  |  | HVAC14;HVAC15 | HVAC
VRP6201DI4 | Registre VRP6201 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6201O4 ; VRP6201F4 |  |  |  |  | HVAC14 | HVAC
VRP6102DI3 | Registre VRP6102 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6102O3 ; VRP6102F3 |  |  |  |  | HVAC14 | HVAC
VRP6102DI1 | Registre VRP6102 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6102O1 ; VRP6102F1 |  |  |  |  | HVAC14 | HVAC
VRP6102DI5 | Registre VRP6102 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6102O5 ; VRP6102F5 |  |  |  |  | HVAC14;HVAC15 | HVAC
VRP6502DI1 | Registre VRP6502 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6502O1 ; VRP6502F1 |  |  |  |  | HVAC15 | HVAC
VRP6502DI2 | Registre VRP6502 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6502O2 ; VRP6502F2 |  |  |  |  | HVAC15 | HVAC
VRP6201DI3 | Registre VRP6201 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6201O3 ; VRP6201F3 |  |  |  |  | HVAC15 | HVAC
VRP6201DI2 | Registre VRP6201 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6201O2 ; VRP6201F2 |  |  |  |  | HVAC15 | HVAC
VRP6101DI21 | Registre VRP6101 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6101O21 ; VRP6101F21 |  |  |  |  | HVAC15 | HVAC
VRP6101DI22 | Registre VRP6101 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6101O22 ; VRP6101F22 |  |  |  |  | HVAC15 | HVAC
VRP6501DI1 | Registre VRP6501 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6501O1 ; VRP6501F1 |  |  |  |  | HVAC15 | HVAC
VRP6501DI2 | Registre VRP6501 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6501O2 ; VRP6501F2 |  |  |  |  | HVAC15 | HVAC
VRP6301DI1 | Registre VRP6301 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6301O1 ; VRP6301F1 |  |  |  |  | HVAC15 | HVAC
VRP6301DI2 | Registre VRP6301 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6301O2 ; VRP6301F2 |  |  |  |  | HVAC15 | HVAC
VRP6999DI1 | Registre VRP6999 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6999O1 ; VRP6999F1 |  |  |  |  | HVAC15 | HVAC
VRP6999DI2 | Registre VRP6999 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6999O2 ; VRP6999F2 |  |  |  |  | HVAC15 | HVAC
VRP6701DI1 | Registre VRP6701 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6701O1 ; VRP6701F1 |  |  |  |  | HVAC15 | HVAC
VRP6701DI2 | Registre VRP6701 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6701O2 ; VRP6701F2 |  |  |  |  | HVAC15 | HVAC
VRP6701DI3 | Registre VRP6701 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6701O3 ; VRP6701F3 |  |  |  |  | HVAC15 | HVAC
VRP6601DI1 | Registre VRP6601 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6601O1 ; VRP6601F1 |  |  |  |  | HVAC15 | HVAC
VRP6601DI2 | Registre VRP6601 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6601O2 ; VRP6601F2 |  |  |  |  | HVAC15 | HVAC
VRP6601DI3 | Registre VRP6601 Discordance | CR | N | CAL | 1 | C | [22 empty] | AND |  | VRP6601O3 ; VRP6601F3 |  |  |  |  | HVAC15 | HVAC
GVM6004AE2 | Vanne GVM6004 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | GVM6004O2 ; GVM6004F2 |  |  |  |  | HVAC03 | HVAC
GVM6003AE2 | Vanne GVM6003 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | GVM6003O2 ; GVM6003F2 |  |  |  |  | HVAC03 | HVAC
GVM6002AE2 | Vanne GVM6002 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | GVM6002O2 ; GVM6002F2 |  |  |  |  | HVAC03 | HVAC
CVM6002AE2 | Vanne CVM6002 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6002O2 ; CVM6002F2 |  |  |  |  | HVAC03 | HVAC
GVM6001AE2 | Vanne GVM6001 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | GVM6001O2 ; GVM6001F2 |  |  |  |  | HVAC03 | HVAC
CVM6001AE2 | Vanne CVM6001 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6001O2 ; CVM6001F2 |  |  |  |  | HVAC03 | HVAC
GVM6005AE2 | Vanne GVM6005 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | GVM6005O2 ; GVM6005F2 |  |  |  |  | HVAC03 | HVAC
GVM6006AE2 | Vanne GVM6006 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | GVM6006O2 ; GVM6006F2 |  |  |  |  | HVAC03 | HVAC
CVM6005AE2 | Vanne CVM6005 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6005O2 ; CVM6005F2 |  |  |  |  | HVAC03 | HVAC
CVM6006AE2 | Vanne CVM6006 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6006O2 ; CVM6006F2 |  |  |  |  | HVAC03 | HVAC
CVM6004AE2 | Vanne CVM6004 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6004O2 ; CVM6004F2 |  |  |  |  | HVAC03 | HVAC
CVM6003AE2 | Vanne CVM6003 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6003O2 ; CVM6003F2 |  |  |  |  | HVAC03 | HVAC
CVM6001AE | Vanne CVM6001 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6001O ; CVM6001F |  |  |  |  | HVAC03 | HVAC
CVM6002AE | Vanne CVM6002 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6002O ; CVM6002F |  |  |  |  | HVAC03 | HVAC
CVM6003AE | Vanne CVM6003 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | CVM6003O ; CVM6003F |  |  |  |  | HVAC03 | HVAC
VRP6127AE2 | Registre VRP6127 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6127O2 ; VRP6127F2 |  |  |  |  | HVAC04 | HVAC
VRP6127AE1 | Registre VRP6127 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6127O1 ; VRP6127F1 |  |  |  |  | HVAC04 | HVAC
VRP6118AE3 | Registre VRP6118 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6118O3 ; VRP6118F3 |  |  |  |  | HVAC04 | HVAC
VRP6118AE1 | Registre VRP6118 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6118O1 ; VRP6118F1 |  |  |  |  | HVAC04 | HVAC
VRP6118AE2 | Registre VRP6118 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6118O2 ; VRP6118F2 |  |  |  |  | HVAC04;HVAC05;HVAC06 | HVAC
VRP6118AE4 | Registre VRP6118 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6118O4 ; VRP6118F4 |  |  |  |  | HVAC04;HVAC05;HVAC06 | HVAC
VRP6004AE1 | Registre VRP6004 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6004O1 ; VRP6004F1 |  |  |  |  | HVAC05 | HVAC
VRP6004AE2 | Registre VRP6004 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6004O2 ; VRP6004F2 |  |  |  |  | HVAC05 | HVAC
VRP6007AE1 | Registre VRP6007 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6007O1 ; VRP6007F1 |  |  |  |  | HVAC05 | HVAC
VRP6007AE2 | Registre VRP6007 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6007O2 ; VRP6007F2 |  |  |  |  | HVAC05 | HVAC
VRP6008AE1 | Registre VRP6008 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6008O1 ; VRP6008F1 |  |  |  |  | HVAC05 | HVAC
VRP6008AE2 | Registre VRP6008 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6008O2 ; VRP6008F2 |  |  |  |  | HVAC05 | HVAC
VRP6009AE1 | Registre VRP6009 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6009O1 ; VRP6009F1 |  |  |  |  | HVAC05 | HVAC
VRP6009AE2 | Registre VRP6009 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6009O2 ; VRP6009F2 |  |  |  |  | HVAC05 | HVAC
VRP6002AE1 | Registre VRP6002 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6002O1 ; VRP6002F1 |  |  |  |  | HVAC05 | HVAC
VRP6013AE1 | Registre VRP6013 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6013O1 ; VRP6013F1 |  |  |  |  | HVAC05 | HVAC
VRP6002AE2 | Registre VRP6002 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6002O2 ; VRP6002F2 |  |  |  |  | HVAC05 | HVAC
VRP6101AE11 | Registre VRP6101 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6101O11 ; VRP6101F11 |  |  |  |  | HVAC05 | HVAC
VRP6101AE12 | Registre VRP6101 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6101O12 ; VRP6101F12 |  |  |  |  | HVAC05 | HVAC
VRP6103AE1 | Registre VRP6103 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6103O1 ; VRP6103F1 |  |  |  |  | HVAC05 | HVAC
VRP6103AE2 | Registre VRP6103 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6103O2 ; VRP6103F2 |  |  |  |  | HVAC05 | HVAC
VRP6111AE1 | Registre VRP6111 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6111O1 ; VRP6111F1 |  |  |  |  | HVAC05 | HVAC
VRP6111AE2 | Registre VRP6111 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6111O2 ; VRP6111F2 |  |  |  |  | HVAC05 | HVAC
VRP6112AE1 | Registre VRP6112 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6112O1 ; VRP6112F1 |  |  |  |  | HVAC05 | HVAC
VRP6112AE2 | Registre VRP6112 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6112O2 ; VRP6112F2 |  |  |  |  | HVAC05 | HVAC
VRP6113AE1 | Registre VRP6113 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6113O1 ; VRP6113F1 |  |  |  |  | HVAC05 | HVAC
VRP6113AE2 | Registre VRP6113 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6113O2 ; VRP6113F2 |  |  |  |  | HVAC05 | HVAC
VRP6115AE1 | Registre VRP6115 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6115O1 ; VRP6115F1 |  |  |  |  | HVAC05 | HVAC
VRP6115AE2 | Registre VRP6115 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6115O2 ; VRP6115F2 |  |  |  |  | HVAC05 | HVAC
VRP6116AE1 | Registre VRP6116 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6116O1 ; VRP6116F1 |  |  |  |  | HVAC06 | HVAC
VRP6116AE2 | Registre VRP6116 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6116O2 ; VRP6116F2 |  |  |  |  | HVAC06 | HVAC
VRP6106AE1 | Registre VRP6106 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6106O1 ; VRP6106F1 |  |  |  |  | HVAC06 | HVAC
VRP6100AE2 | Registre VRP6100 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6100O2 ; VRP6100F2 |  |  |  |  | HVAC06 | HVAC
VRP6104AE1 | Registre VRP6104 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6104O1 ; VRP6104F1 |  |  |  |  | HVAC06 | HVAC
VRP6104AE2 | Registre VRP6104 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6104O2 ; VRP6104F2 |  |  |  |  | HVAC06 | HVAC
VRP6107AE1 | Registre VRP6107 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6107O1 ; VRP6107F1 |  |  |  |  | HVAC06 | HVAC
VRP6107AE2 | Registre VRP6107 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6107O2 ; VRP6107F2 |  |  |  |  | HVAC06 | HVAC
VRP6117AE1 | Registre VRP6117 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6117O1 ; VRP6117F1 |  |  |  |  | HVAC06 | HVAC
VRP6012AE1 | Registre VRP6012 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6012O1 ; VRP6012F1 |  |  |  |  | HVAC06 | HVAC
VRP6012AE2 | Registre VRP6012 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6012O2 ; VRP6012F2 |  |  |  |  | HVAC06 | HVAC
VCF6003AE1 | Clapet coupe feu VCF6003 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6003O1 ; VCF6003F1 |  |  |  |  | HVAC10 | HVAC
VCF6004AE1 | Clapet coupe feu VCF6004 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6004O1 ; VCF6004F1 |  |  |  |  | HVAC10 | HVAC
VCF6006AE1 | Clapet coupe feu VCF6006 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6006O1 ; VCF6006F1 |  |  |  |  | HVAC10 | HVAC
VCF6012AE1 | Clapet coupe feu VCF6012 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6012O1 ; VCF6012F1 |  |  |  |  | HVAC10 | HVAC
VCF6012AE3 | Clapet coupe feu VCF6012 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6012O3 ; VCF6012F3 |  |  |  |  | HVAC10 | HVAC
VCF6013AE3 | Clapet coupe feu VCF6013 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6013O3 ; VCF6013F3 |  |  |  |  | HVAC10 | HVAC
VCF6100AE1 | Clapet coupe feu VCF6100 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6100O1 ; VCF6100F1 |  |  |  |  | HVAC10 | HVAC
VCF6103AE1 | Clapet coupe feu VCF6103 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6103O1 ; VCF6103F1 |  |  |  |  | HVAC10 | HVAC
VCF6103AE2 | Clapet coupe feu VCF6103 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6103O2 ; VCF6103F2 |  |  |  |  | HVAC10 | HVAC
VCF6111AE1 | Clapet coupe feu VCF6111 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6111O1 ; VCF6111F1 |  |  |  |  | HVAC10 | HVAC
VCF6117AE2 | Clapet coupe feu VCF6117 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6117O2 ; VCF6117F2 |  |  |  |  | HVAC10 | HVAC
VCF6117AE1 | Clapet coupe feu VCF6117 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6117O1 ; VCF6117F1 |  |  |  |  | HVAC10 | HVAC
VCF6118AE1 | Clapet coupe feu VCF6118 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6118O1 ; VCF6118F1 |  |  |  |  | HVAC10 | HVAC
VCF6001AE1 | Clapet coupe feu VCF6001 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6001O1 ; VCF6001F1 |  |  |  |  | HVAC10 | HVAC
VCF6003AE3 | Clapet coupe feu VCF6003 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6003O3 ; VCF6003F3 |  |  |  |  | HVAC10 | HVAC
VCF6003AE2 | Clapet coupe feu VCF6003 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6003O2 ; VCF6003F2 |  |  |  |  | HVAC10 | HVAC
VCF6006AE2 | Clapet coupe feu VCF6006 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6006O2 ; VCF6006F2 |  |  |  |  | HVAC10 | HVAC
VCF6007AE1 | Clapet coupe feu VCF6007 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6007O1 ; VCF6007F1 |  |  |  |  | HVAC10 | HVAC
VCF6007AE2 | Clapet coupe feu VCF6007 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6007O2 ; VCF6007F2 |  |  |  |  | HVAC10 | HVAC
VCF6008AE1 | Clapet coupe feu VCF6008 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6008O1 ; VCF6008F1 |  |  |  |  | HVAC10 | HVAC
VCF6008AE2 | Clapet coupe feu VCF6008 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6008O2 ; VCF6008F2 |  |  |  |  | HVAC10 | HVAC
VCF6009AE1 | Clapet coupe feu VCF6009 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6009O1 ; VCF6009F1 |  |  |  |  | HVAC10 | HVAC
VCF6012AE2 | Clapet coupe feu VCF6012 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6012O2 ; VCF6012F2 |  |  |  |  | HVAC10 | HVAC
VCF6013AE1 | Clapet coupe feu VCF6013 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6013O1 ; VCF6013F1 |  |  |  |  | HVAC10 | HVAC
VCF6013AE2 | Clapet coupe feu VCF6013 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6013O2 ; VCF6013F2 |  |  |  |  | HVAC10 | HVAC
VCF6100AE2 | Clapet coupe feu VCF6100 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6100O2 ; VCF6100F2 |  |  |  |  | HVAC10 | HVAC
VCF6106AE1 | Clapet coupe feu VCF6106 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6106O1 ; VCF6106F1 |  |  |  |  | HVAC10 | HVAC
VCF6108AE1 | Clapet coupe feu VCF6108 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6108O1 ; VCF6108F1 |  |  |  |  | HVAC10 | HVAC
VCF6111AE2 | Clapet coupe feu VCF6111 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6111O2 ; VCF6111F2 |  |  |  |  | HVAC10 | HVAC
VCF6112AE1 | Clapet coupe feu VCF6112 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6112O1 ; VCF6112F1 |  |  |  |  | HVAC10 | HVAC
VCF6113AE1 | Clapet coupe feu VCF6113 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6113O1 ; VCF6113F1 |  |  |  |  | HVAC10 | HVAC
VCF6115AE1 | Clapet coupe feu VCF6115 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6115O1 ; VCF6115F1 |  |  |  |  | HVAC10 | HVAC
VCF6115AE2 | Clapet coupe feu VCF6115 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6115O2 ; VCF6115F2 |  |  |  |  | HVAC10 | HVAC
VCF6115AE3 | Clapet coupe feu VCF6115 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6115O3 ; VCF6115F3 |  |  |  |  | HVAC10 | HVAC
VCF6116AE1 | Clapet coupe feu VCF6116 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6116O1 ; VCF6116F1 |  |  |  |  | HVAC10 | HVAC
VCF6118AE2 | Clapet coupe feu VCF6118 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6118O2 ; VCF6118F2 |  |  |  |  | HVAC10 | HVAC
VCF6126AE1 | Clapet coupe feu VCF6126 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VCF6126O1 ; VCF6126F1 |  |  |  |  | HVAC10 | HVAC
VRP6401AE1 | Registre VRP6401 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6401O1 ; VRP6401F1 |  |  |  |  | HVAC13 | HVAC
VRP6401AE2 | Registre VRP6401 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6401O2 ; VRP6401F2 |  |  |  |  | HVAC13;HVAC15 | HVAC
VRP6401AE3 | Registre VRP6401 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6401O3 ; VRP6401F3 |  |  |  |  | HVAC13 | HVAC
VRP6401AE4 | Registre VRP6401 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6401O4 ; VRP6401F4 |  |  |  |  | HVAC13;HVAC15 | HVAC
VRP6201AE1 | Registre VRP6201 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6201O1 ; VRP6201F1 |  |  |  |  | HVAC14 | HVAC
VRP6201AE5 | Registre VRP6201 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6201O5 ; VRP6201F5 |  |  |  |  | HVAC14;HVAC15 | HVAC
VRP6201AE4 | Registre VRP6201 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6201O4 ; VRP6201F4 |  |  |  |  | HVAC14 | HVAC
VRP6102AE3 | Registre VRP6102 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6102O3 ; VRP6102F3 |  |  |  |  | HVAC14 | HVAC
VRP6102AE1 | Registre VRP6102 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6102O1 ; VRP6102F1 |  |  |  |  | HVAC14 | HVAC
VRP6102AE5 | Registre VRP6102 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6102O5 ; VRP6102F5 |  |  |  |  | HVAC14;HVAC15 | HVAC
VRP6502AE1 | Registre VRP6502 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6502O1 ; VRP6502F1 |  |  |  |  | HVAC15 | HVAC
VRP6502AE2 | Registre VRP6502 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6502O2 ; VRP6502F2 |  |  |  |  | HVAC15 | HVAC
VRP6201AE3 | Registre VRP6201 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6201O3 ; VRP6201F3 |  |  |  |  | HVAC15 | HVAC
VRP6201AE2 | Registre VRP6201 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6201O2 ; VRP6201F2 |  |  |  |  | HVAC15 | HVAC
VRP6101AE21 | Registre VRP6101 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6101O21 ; VRP6101F21 |  |  |  |  | HVAC15 | HVAC
VRP6101AE22 | Registre VRP6101 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6101O22 ; VRP6101F22 |  |  |  |  | HVAC15 | HVAC
VRP6501AE1 | Registre VRP6501 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6501O1 ; VRP6501F1 |  |  |  |  | HVAC15 | HVAC
VRP6501AE2 | Registre VRP6501 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6501O2 ; VRP6501F2 |  |  |  |  | HVAC15 | HVAC
VRP6301AE1 | Registre VRP6301 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6301O1 ; VRP6301F1 |  |  |  |  | HVAC15 | HVAC
VRP6301AE2 | Registre VRP6301 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6301O2 ; VRP6301F2 |  |  |  |  | HVAC15 | HVAC
VRP6999AE1 | Registre VRP6999 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6999O1 ; VRP6999F1 |  |  |  |  | HVAC15 | HVAC
VRP6999AE2 | Registre VRP6999 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6999O2 ; VRP6999F2 |  |  |  |  | HVAC15 | HVAC
VRP6701AE1 | Registre VRP6701 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6701O1 ; VRP6701F1 |  |  |  |  | HVAC15 | HVAC
VRP6701AE2 | Registre VRP6701 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6701O2 ; VRP6701F2 |  |  |  |  | HVAC15 | HVAC
VRP6701AE3 | Registre VRP6701 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6701O3 ; VRP6701F3 |  |  |  |  | HVAC15 | HVAC
VRP6601AE1 | Registre VRP6601 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6601O1 ; VRP6601F1 |  |  |  |  | HVAC15 | HVAC
VRP6601AE2 | Registre VRP6601 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6601O2 ; VRP6601F2 |  |  |  |  | HVAC15 | HVAC
VRP6601AE3 | Registre VRP6601 Aucun Etat | CR | N | CAL | 1 | C | [22 empty] | NOR |  | VRP6601O3 ; VRP6601F3 |  |  |  |  | HVAC15 | HVAC
SPAFCR0222 | SPARE FIL 0222 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 4 | 16416 | 1240 | 4 | EL1134_M153 | 4 | BITVAL
SPAFCR0223 | SPARE FIL 0223 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 6 | 16416 | 1240 | 6 | EL1134_M153 | 8 | BITVAL
SPAFCR0224 | SPARE FIL 0224 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 8 | 16416 | 1241 | 0 | EL1134_M154 | 1 | BITVAL
SPAFCR0225 | SPARE FIL 0225 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 10 | 16416 | 1241 | 2 | EL1134_M154 | 5 | BITVAL
SPAFCR0226 | SPARE FIL 0226 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 12 | 16416 | 1241 | 4 | EL1134_M154 | 4 | BITVAL
SPAFCR0227 | SPARE FIL 0227 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12909 | 14 | 16416 | 1241 | 6 | EL1134_M154 | 8 | BITVAL
SPAFCR0228 | SPARE FIL 0228 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12910 | 0 | 16416 | 1242 | 0 | EL1134_M156 |  | BITVAL
SPAFCR0229 | SPARE FIL 0229 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12910 | 8 | 16416 | 1243 | 0 | EL1134_M157 |  | BITVAL
SPAFCR0230 | SPARE FIL 0230 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12911 | 0 | 16416 | 1244 | 0 | EL1134_M158 |  | BITVAL
SPAFCR0231 | SPARE FIL 0231 | CR | N | FIL | [28 empty] | POL | 10000 | [9 empty] | 12911 | 8 | 16416 | 1245 | 0 | EL1134_M159 |  | BITVAL
VFN7013S1 | SMOKE EXTRACTION SALLE 13 LAGRANGE POSITION SECURITE | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1012 | 2 | [7 empty] | BITVAL
VFN7013S2 | SMOKE EXTRACTION SALLE 13 LAGRANGE Fan Motor Circuit breaker ON | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1012 | 4 | [7 empty] | BITVAL
VFN7013S3 | **SMOKE EXTRACTION SALLE 13 LAGRANGE DAMPER Ouvert | CR | O | FIL | 2 | E | [10 empty] | 0 | [15 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1012 | 6 | [7 empty] | BITVAL
VFN7013S4 | SMOKE EXTRACTION SALLE 13 LAGRANGE POSITION ATTENTE | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1012 | 8 | [7 empty] | BITVAL
VCD7014S2 | ACID BATTERY EVAC SALLE 14 LAGRANGE Fan Motor Circuit breaker ON | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1012 | 14 | [7 empty] | BITVAL
VCF7014O1 | ACID BATTERY EVAC SALLE 14 LAGRANGE CLAPET 184.CCF.14.1 ETAT OUVERT | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC 22 | HVAC (C) | LGRNG | 9 |  |  | 1013 | 0 | [7 empty] | BITVAL
VCF7014F1 | ACID BATTERY EVAC SALLE 14 LAGRANGE CLAPET 184.CCF.14.1 ETAT FERME | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC 22 | HVAC (C) | LGRNG | 9 |  |  | 1013 | 2 | [7 empty] | BITVAL
VCD7014S5 | **ACID BATTERY EVAC SALLE 14 LAGRANGE EXTRACTEUR IN MARCHE | CR | O | FIL | 2 | E | [10 empty] | 0 | [15 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1013 | 4 | [7 empty] | BITVAL
VFN7010S1 | SMOKE EXTRACTION SALLE 10 LAGRANGE POSITION SECURITE | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1013 | 8 | [7 empty] | BITVAL
VFN7010S2 | SMOKE EXTRACTION SALLE 10 LAGRANGE Fan Motor Circuit breaker ON | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1013 | 10 | [7 empty] | BITVAL
VFN7010S3 | **SMOKE EXTRACTION SALLE 10 LAGRANGE DAMPER Ouvert | CR | O | FIL | 2 | E | [10 empty] | 0 | [15 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1013 | 12 | [7 empty] | BITVAL
VFN7010S4 | SMOKE EXTRACTION SALLE 10 LAGRANGE POSITION ATTENTE | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1013 | 14 | [7 empty] | BITVAL
VFN7005S1 | SMOKE EXTRACTION SALLE 05 LAGRANGE POSITION SECURITE | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1014 | 2 | [7 empty] | BITVAL
EUL7071M | Lagrange UPS A UPS MARCHE / ARRET | CR | N | RES | 2 | E | [26 empty] | MTCP | 2000 |  | E73 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1021 | 0 | [7 empty] | BITVAL
EKM7071F | Lagrange UPS A Operation on static switch | CR | N | RES | 2 | E | [26 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1021 | 2 | [7 empty] | BITVAL
EUL7072M | Lagrange UPS B UPS MARCHE / ARRET | CR | N | RES | 2 | E | [26 empty] | MTCP | 2000 |  | E73 | Energy Lagrange (E) | LGRNG | 9 |  |  | 1023 | 0 | [7 empty] | BITVAL
EKM7072F | Lagrange UPS B Operation on static switch | CR | N | RES | 2 | E | [26 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1023 | 2 | [7 empty] | BITVAL
SZI7001D | Defaut Lagrange Hall RDC 0000 ZAD01 - ZONE 1 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1032 | 0 | [7 empty] | BITVAL
SZI7002D | Defaut Lagrange Aisle 0000 ZDA02 - ZONE 2 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1032 | 4 | [7 empty] | BITVAL
SZI7003D | Defaut Lagrange Meeting room 0001 ZDA03 - ZONE 3 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1032 | 8 | [7 empty] | BITVAL
SZI7004D | Defaut Lagrange Technical room 0005 ZDA04 Z1 - ZONE 4 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1032 | 12 | [7 empty] | BITVAL
SZI7005D | Defaut Lagrange Technical room 0005 ZDA05 Z2 - ZONE 5 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1033 | 0 | [7 empty] | BITVAL
SZI7006D | Defaut Lagrange COPV/PLANIF 0006 ZDA06 - ZONE 6 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1033 | 4 | [7 empty] | BITVAL
SZI7007D | Defaut Lagrange Control room 0007 ZDA07 - ZONE 7 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1033 | 8 | [7 empty] | BITVAL
SZI7008D | Defaut Lagrange DAS Room 0008 ZDA08 - ZONE 8 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1033 | 12 | [7 empty] | BITVAL
SZI7009D | Defaut Lagrange Local Telecom 0009 ZDA09 - ZONE 9 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 0 | [7 empty] | BITVAL
SZI7010D | Defaut Lagrange Launch range room 0010 ZDA10 Z1 - ZONE 10 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 4 | [7 empty] | BITVAL
SZI7011D | Defaut Lagrange Launch range room 0010 ZDA10 Z2 - ZONE 11 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 8 | [7 empty] | BITVAL
SZI7012D | Defaut Lagrange Office 0011 ZDA11 - ZONE 12 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI73 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1034 | 12 | [7 empty] | BITVAL
SZI7013D | Defaut Lagrange Crisis room 0012 ZDA12 - ZONE 13 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1035 | 0 | [7 empty] | BITVAL
SZI7014D | Defaut Lagrange UPS room 0013 ZDA13 Z1 - ZONE 14 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1035 | 4 | [7 empty] | BITVAL
SZI7015D | Defaut Lagrange UPS room 0013 ZDA13 Z2 - ZONE 15 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1035 | 8 | [7 empty] | BITVAL
SZI7016D | Defaut Lagrange Battery room 0014 ZDA14 Z1 - ZONE 16 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1035 | 12 | [7 empty] | BITVAL
SZI7017D | Defaut Lagrange Battery room 0014 ZDA14 Z2 - ZONE 17 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group); E77 (EXTIN Lagrange Group) | Detection Incendie (DI); Extinction Incendie (EI) | LGRNG | 9 |  |  | 1036 | 0 | [7 empty] | BITVAL
SZI7018D | Defaut Lagrange Local clim RDC 0020 ZDA15 - ZONE 18 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1036 | 4 | [7 empty] | BITVAL
SZI7019D | Defaut Lagrange Local de repos 0025 ZDA16 - ZONE 19 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1036 | 8 | [7 empty] | BITVAL
SZI7020D | Defaut Lagrange Local imprimerie 0048 ZDA17 - ZONE 20 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1036 | 12 | [7 empty] | BITVAL
SZI7021D | Defaut Lagrange Couloir étage 0100 ZDA18 - ZONE 21 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 0 | [7 empty] | BITVAL
SZI7022D | DM rdc Defaut Lagrange ZDM19 - ZONE 22 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 4 | [7 empty] | BITVAL
SZI7023D | DM 1°étage Defaut Lagrange ZDM20 - ZONE 23 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 8 | [7 empty] | BITVAL
SZI7024D | Defaut Lagrange DEFAUT PORTE OUVERTE - ZONE 24 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1037 | 12 | [7 empty] | BITVAL
SZI7025D | Defaut Lagrange DEFAUT PARAFOUDRE 230V - ZONE 25 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1038 | 0 | [7 empty] | BITVAL
SZI7026D | Defaut Lagrange DEFAUT UGA - ZONE 26 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI74 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1038 | 4 | [7 empty] | BITVAL
VFN7005S2 | SMOKE EXTRACTION SALLE 05 LAGRANGE Fan Motor Circuit breaker ON | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1014 | 4 | [7 empty] | BITVAL
VFN7005S3 | **SMOKE EXTRACTION SALLE 05 LAGRANGE DAMPER Ouvert | CR | O | FIL | 2 | E | [10 empty] | 0 | [15 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1014 | 6 | [7 empty] | BITVAL
VFN7005S4 | SMOKE EXTRACTION SALLE 05 LAGRANGE POSITION ATTENTE | CR | O | FIL | 2 | E | [26 empty] | MTCP | 500 |  | E75 | Smoke Extraction (E) | LGRNG | 9 |  |  | 1014 | 8 | [7 empty] | BITVAL
VCF7001O1 | CLAPET AIR NEUF 184.CCF.01.1 SALLE 01 LAGRANGE ETAT OUVERT | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC22 | HVAC (C) | LGRNG | 9 |  |  | 1014 | 10 | [7 empty] | BITVAL
VCF7001F1 | CLAPET AIR NEUF 184.CCF.01.1 SALLE 01 LAGRANGE ETAT FERME | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC22 | HVAC (C) | LGRNG | 9 |  |  | 1014 | 12 | [7 empty] | BITVAL
VCF7014O2 | CLAPET AIR NEUF 184.CCF.14.2 SALLE 14 LAGRANGE ETAT OUVERT | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC22 | HVAC (C) | LGRNG | 9 |  |  | 1014 | 14 | [7 empty] | BITVAL
VCF7014F2 | CLAPET AIR NEUF 184.CCF.14.2 SALLE 14 LAGRANGE ETAT FERME | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC22 | HVAC (C) | LGRNG | 9 |  |  | 1015 | 0 | [7 empty] | BITVAL
VCF7020O1 | CLAPET PULSION AIR NEUF 184.CCF.20.1 CTA SALLE 20 LAGRANGE ETAT OUVERT | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC22 | HVAC (C) | LGRNG | 9 |  |  | 1015 | 2 | [7 empty] | BITVAL
VCF7020F1 | CLAPET PULSION AIR NEUF 184.CCF.20.1 CTA SALLE 20 LAGRANGE ETAT FERME | CR | O | FIL | 2 | C | [26 empty] | MTCP | 500 |  | HVAC22 | HVAC (C) | LGRNG | 9 |  |  | 1015 | 4 | [7 empty] | BITVAL
SZI7101D | Defaut HA Lagrange Hall 0001 ZDA01 - ZONE HA 1 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 0 | [7 empty] | BITVAL
SZI7102D | Defaut HA Lagrange Hall stockage S.E.P 0001b ZDA02 - ZONE HA 2 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 4 | [7 empty] | BITVAL
SZI7103D | Defaut HA Lagrange Stock mat spéci lanceur 0002 ZDA03 - ZONE HA 3 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 8 | [7 empty] | BITVAL
SZI7104D | Defaut HA Lagrange Local électrique 0003 ZDA04 - ZONE HA 4 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 12 | [7 empty] | BITVAL
SZI7105D | Defaut HA Lagrange Local climatisation 0004 ZDA05 - ZONE HA 5 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 0 | [7 empty] | BITVAL
SZI7106D | Defaut HA Lagrange Atelier mécanique 0005a ZDA06 - ZONE HA 6 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 4 | [7 empty] | BITVAL
SZI7107D | Defaut HA Lagrange Sas atelier mécanique 0005bZDA07 - ZONE HA 7 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 8 | [7 empty] | BITVAL
SZI7108D | Defaut HA Lagrange Local 0005c ZDA08 - ZONE HA 8 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 12 | [7 empty] | BITVAL
SZI7110D | Defaut HA Lagrange Magasin SPPI 0006b ZDA10 - ZONE HA 10 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 0 | [7 empty] | BITVAL
SZI7109D | Defaut HA Lagrange Vestiaires S.E.P 0006a ZDA09 - ZONE HA 9 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 4 | [7 empty] | BITVAL
SZI7111D | Defaut HA Lagrange Vestiares 0007 ZDA11 - ZONE HA 11 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 8 | [7 empty] | BITVAL
SZI7112D | Defaut HA Lagrange Local batteries 0010 ZDA12 - ZONE HA 12 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 12 | [7 empty] | BITVAL
SZI7113D | Defaut HA Lagrange Couloir Nord Est 0011 ZDA13 - ZONE HA 13 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 0 | [7 empty] | BITVAL
SZI7114D | Defaut HA Lagrange Local telecom 0012 ZDA14 - ZONE HA 14 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 4 | [7 empty] | BITVAL
SZI7115D | Defaut HA Lagrange Vestiares 0013 ZDA15 - ZONE HA 15 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 8 | [7 empty] | BITVAL
SZI7116D | Defaut HA Lagrange Magasin 0015 ZDA16 - ZONE HA 16 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 12 | [7 empty] | BITVAL
SZI7117D | Defaut HA Lagrange Magasin AR4/5 0016 ZDA17 - ZONE HA 17 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 0 | [7 empty] | BITVAL
SZI7118D | Defaut HA Lagrange Couloir Nord Ouest 0017 ZDA18 - ZONE HA 18 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 4 | [7 empty] | BITVAL
SZI7119D | Defaut HA Lagrange Zone prépartion 0018a ZDA19 - ZONE HA 19 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 8 | [7 empty] | BITVAL
SZI7120D | Defaut HA Lagrange Zone prépartion 0018b ZDA20 - ZONE HA 20 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 12 | [7 empty] | BITVAL
SZI7121D | Defaut HA Lagrange Atelier Nord Clim 0019 ZDA21 - ZONE HA 21 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 0 | [7 empty] | BITVAL
SZI7122D | Defaut HA Lagrange Local onduleur babar 0020 ZDA22 - ZONE HA 22 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 4 | [7 empty] | BITVAL
SZI7123D | Defaut HA Lagrange Atelier charge batterie 0020 ZDA23 - ZONE HA 23 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 8 | [7 empty] | BITVAL
SZI7124D | Defaut HA Lagrange Bureau 0021 ZDA24 - ZONE HA 24 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 12 | [7 empty] | BITVAL
SZI7125D | Defaut HA Lagrange SPPM AR4/5 0022 ZDA25 - ZONE HA 25 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 0 | [7 empty] | BITVAL
SZI7126D | Defaut HA Lagrange Labo électrique 0023aZDA26 - ZONE HA 26 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 4 | [7 empty] | BITVAL
SZI7127D | Defaut HA Lagrange Bureau logistique AR4/5 0023bZDA27 - ZONE HA 27 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 8 | [7 empty] | BITVAL
SZI7128D | Defaut HA Lagrange Magasin AR4 0024 ZDA28 - ZONE HA 28 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 12 | [7 empty] | BITVAL
SZI7129D | Defaut HA Lagrange Magasin ST/EX 0026 ZDA29 - ZONE HA 29 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 0 | [7 empty] | BITVAL
SZI7130D | Defaut HA Lagrange Magasin A.E produit toxique 0027 ZDA30 - ZONE HA 30 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 4 | [7 empty] | BITVAL
SZI7131D | Defaut HA Lagrange Plannification AR4/5 0039 ZDA31 - ZONE HA 31 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 8 | [7 empty] | BITVAL
SZI7132D | Defaut HA Lagrange Bureau SPPI 0040a ZDA32 - ZONE HA 32 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 12 | [7 empty] | BITVAL
SZI7133D | Defaut HA Lagrange Salle préparation AR4 0040b -ZDA33 - ZONE HA 33 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 0 | [7 empty] | BITVAL
SZI7134D | Defaut HA Lagrange Salle préparation AR5 0041 ZDA34 - ZONE HA 34 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 4 | [7 empty] | BITVAL
SZI7135D | Defaut HA Lagrange Zone arrivée depart magasin 0042 ZDA35 - ZONE HA 35 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 8 | [7 empty] | BITVAL
SZI7136D | Defaut HA Lagrange Laboratoire analyseur 0043a ZDA36 - ZONE HA 36 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 12 | [7 empty] | BITVAL
SZI7137D | Defaut HA Lagrange Salle chaude 0043b ZDA37 - ZONE HA 37 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 0 | [7 empty] | BITVAL
SZI7138D | Defaut HA Lagrange Sas salle chaude 0043c ZDA38 - ZONE HA 38 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 4 | [7 empty] | BITVAL
SZI7139D | Defaut HA Lagrange Local 0043d ZDA39 - ZONE HA 39 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 8 | [7 empty] | BITVAL
SZI7140D | Defaut HA Lagrange Atelier maintenance 0044 ZDA40 - ZONE HA 40 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 12 | [7 empty] | BITVAL
SZI7141D | Defaut HA Lagrange Bureau atelier 0044b ZDA41 - ZONE HA 41 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 0 | [7 empty] | BITVAL
SZI7142D | Defaut HA Lagrange Vestiaires 0047 ZDA42 - ZONE HA 42 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 4 | [7 empty] | BITVAL
SZI7143D | Defaut HA Lagrange MAGASIN A.E MATERIEL LOURD 0048 ZDA43 - ZONE HA 43 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 8 | [7 empty] | BITVAL
SZI7144D | Defaut HA Lagrange Magasin pièce detaché SOGAL 0049 ZDA44 - ZONE HA 44 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 12 | [7 empty] | BITVAL
SZI7145D | Defaut HA Lagrange Local relumix 0050 ZDA45 - ZONE HA 45 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 0 | [7 empty] | BITVAL
SZI7146D | Defaut HA Lagrange Salle déshabillage 0051 ZDA46 - ZONE HA 46 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 4 | [7 empty] | BITVAL
SZI7147D | Defaut HA Lagrange Salle d'habillage 0057 ZDA47 - ZONE HA 47 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 8 | [7 empty] | BITVAL
SZI7148D | Defaut HA Lagrange Salle pollué 0059 ZDA48 - ZONE HA 48 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 12 | [7 empty] | BITVAL
SZI7149D | Defaut HA Lagrange Couloir 0029 ZDA49 - ZONE HA 49 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1113 | 0 | [7 empty] | BITVAL
SZI7150D | Defaut HA Lagrange Couloir 0031 ZDA50 - ZONE HA 50 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1113 | 4 | [7 empty] | BITVAL
SZI7151D | Defaut HA Lagrange Combles ZDA51 - ZONE HA 51 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1113 | 8 | [7 empty] | BITVAL
SZI7155D | Defaut HA Lagrange Extension HA 0028 ZDA49 - ZONE HA 55 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1114 | 8 | [7 empty] | BITVAL
VCF7001DI1 | CLAPET AIR NEUF 184.CCF.01.1 SALLE 01 LAGRANGE DISCORDANCE | CR | N | CAL | 2 | C | [22 empty] | AND |  | VCF7001O1; VCF7001F1 |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7001AE1 | CLAPET AIR NEUF 184.CCF.01.1 SALLE 01 LAGRANGE AUCUN ETAT | CR | N | CAL | 2 | C | [22 empty] | OR |  | VCF7001O1; VCF7001F1 |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7014DI1 | CLAPET AIR NEUF 184.CCF.14.1 SALLE 14 LAGRANGE DISCORDANCE | CR | N | CAL | 2 | C | [22 empty] | AND |  | VCF7014F1 ; VCF7014O2; |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7014AE1 | CLAPET AIR NEUF 184.CCF.14.1 SALLE 14 LAGRANGE AUCUN ETAT | CR | N | CAL | 2 | C | [22 empty] | OR |  | VCF7014F1 ; VCF7014O2; |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7014DI2 | CLAPET AIR NEUF 184.CCF.14.2 SALLE 14 LAGRANGE DISCORDANCE | CR | N | CAL | 2 | C | [22 empty] | AND |  | VCF7014F2; VCF7014O2; |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7014AE2 | CLAPET AIR NEUF 184.CCF.14.2 SALLE 14 LAGRANGE AUCUN ETAT | CR | N | CAL | 2 | C | [22 empty] | OR |  | VCF7014F2; VCF7014O2; |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7020DI1 | CLAPET PULSION AIR NEUF 184.CCF.20.1 CTA SALLE 20 LAGRANGE DISCORDANCE | CR | N | CAL | 2 | C | [22 empty] | AND |  | VCF7020F1 ; VCF7020O1 |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
VCF7020AE1 | CLAPET PULSION AIR NEUF 184.CCF.20.1 CTA SALLE 20 LAGRANGE AUCUN ETAT | CR | N | CAL | 2 | C | [22 empty] | OR |  | VCF7020F1 ; VCF7020O1 |  | MTCP |  |  | HVAC22 | HVAC (C) | LGRNG | 9
LZA7000A | LAGRANGE PLC A PRIMARY | CR | N | RES | 2 | Z | [26 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 903 | 12 | [7 empty] | BIT
LZA7000B | LAGRANGE PLC B PRIMARY | CR | N | RES | 2 | Z | [26 empty] | MTCP | 2000 |  | VMC05 | VMC (Z) | LGRNG | 9 |  |  | 903 | 13 | [7 empty] | BIT
SZI7156D | Defaut HA Lagrange Salle de Repos 0014 ZDA52 - ZONE HA 56 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1114 | 12 | [7 empty] | BITVAL
SCG7000DH | LAGRANGE DETG CENTRAL COMMON ALARM HIGH RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 6 | [7 empty] | BITVAL
SCG7000D | LAGRANGE DETG CENTRAL COMMON FAULT RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 8 | [7 empty] | BITVAL
SCG7001DB | LAGRANGE DETG CENTRAL CHANNEL 1 ALARM LOW RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 10 | [7 empty] | BITVAL
SCG7001DH | LAGRANGE DETG CENTRAL CHANNEL 1 ALARM HIGH RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 12 | [7 empty] | BITVAL
SCG7002DB | LAGRANGE DETG CENTRAL CHANNEL 2 ALARM LOW RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1047 | 14 | [7 empty] | BITVAL
SCG7002DH | LAGRANGE DETG CENTRAL CHANNEL 2 ALARM HIGH RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1048 | 0 | [7 empty] | BITVAL
SCG7003DB | LAGRANGE DETG CENTRAL CHANNEL 3 ALARM LOW RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1048 | 2 | [7 empty] | BITVAL
SCG7003DH | LAGRANGE DETG CENTRAL CHANNEL 3 ALARM HIGH RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1048 | 4 | [7 empty] | BITVAL
SCG7004DB | LAGRANGE DETG CENTRAL CHANNEL 4 ALARM LOW RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1048 | 6 | [7 empty] | BITVAL
SCG7004DH | LAGRANGE DETG CENTRAL CHANNEL 4 ALARM HIGH RELAY COIL OPEN CIRCUIT FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1048 | 8 | [7 empty] | BITVAL
SDO7001W1 | LAGRANGE DETG CENTRAL CHANNEL1 ALARM 1 | AL | N | RES | 2 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1051 | 0 | [7 empty] | BITVAL
SDO7001W2 | LAGRANGE DETG CENTRAL CHANNEL1 ALARM 2 | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1051 | 2 | [7 empty] | BITVAL
SDO7001N | LAGRANGE DETG CENTRAL CHANNEL1 INHIBIT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1051 | 4 | [7 empty] | BITVAL
SDO7001D | LAGRANGE DETG CENTRAL CHANNEL1 FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1051 | 6 | [7 empty] | BITVAL
SDO7002W1 | LAGRANGE DETG CENTRAL CHANNEL2 ALARM 1 | AL | N | RES | 2 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1052 | 0 | [7 empty] | BITVAL
SDO7002W2 | LAGRANGE DETG CENTRAL CHANNEL2 ALARM 2 | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1052 | 2 | [7 empty] | BITVAL
SDO7002N | LAGRANGE DETG CENTRAL CHANNEL2 INHIBIT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1052 | 4 | [7 empty] | BITVAL
SDO7002D | LAGRANGE DETG CENTRAL CHANNEL2 FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1052 | 6 | [7 empty] | BITVAL
SDO7003W1 | LAGRANGE DETG CENTRAL CHANNEL3 ALARM 1 | AL | N | RES | 2 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1057 | 0 | [7 empty] | BITVAL
SDO7003W2 | LAGRANGE DETG CENTRAL CHANNEL3 ALARM 2 | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1057 | 2 | [7 empty] | BITVAL
SDO7003N | LAGRANGE DETG CENTRAL CHANNEL3 INHIBIT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1057 | 4 | [7 empty] | BITVAL
SDO7003D | LAGRANGE DETG CENTRAL CHANNEL3 FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1057 | 6 | [7 empty] | BITVAL
SDO7004W1 | LAGRANGE DETG CENTRAL CHANNEL4 ALARM 1 | AL | N | RES | 2 | S;F;D | PCP | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1058 | 0 | [7 empty] | BITVAL
SDO7004W2 | LAGRANGE DETG CENTRAL CHANNEL4 ALARM 2 | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1058 | 2 | [7 empty] | BITVAL
SDO7004N | LAGRANGE DETG CENTRAL CHANNEL4 INHIBIT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1058 | 4 | [7 empty] | BITVAL
SDO7004D | LAGRANGE DETG CENTRAL CHANNEL4 FAULT | AL | N | RES | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 2000 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1058 | 6 | [7 empty] | BITVAL
SCG7000DA | LAGRANGE DETG CENTRAL GENERAL FAULT | AL | O | FIL | 2 | S;F;D |  | V | [10 empty] | S;F;D | [13 empty] | MTCP | 500 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1067 | 0 | [7 empty] | BITVAL
SCX7001GE | **LAGRANGE EXTI UPS BATT CYCLE TRIGGER | AL | O | FIL | 2 | S | [12 empty] | S | [9 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 6 | [7 empty] | BITVAL
SBT7001O | **LAGRANGE EXTI UPS BATT N2 SPREADING | AL | O | FIL | 2 | S | PCP | [11 empty] | S | [9 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 8 | [7 empty] | BITVAL
SWE7001F | LAGRANGE EXTI UPS BATT 3WAY VALVE POS | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 12 | [7 empty] | BITVAL
SWE7001O | LAGRANGE EXTI UPS BATT 3WAY VALVE POS TO VENT | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 14 | [7 empty] | BITVAL
SCX7002GE | **LAGRANGE EXTI TECH LAU CYCLE TRIGGER | AL | O | FIL | 2 | S | [12 empty] | S | [9 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 6 | [7 empty] | BITVAL
SBT7002O | **LAGRANGE EXTI TECH LAU N2 SPREADING | AL | O | FIL | 2 | S | PCP | [11 empty] | S | [9 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 8 | [7 empty] | BITVAL
SWE7002F1 | LAGRANGE EXTI TECH LAU 3WAY VALVE POS S1 | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 12 | [7 empty] | BITVAL
SWE7002O1 | LAGRANGE EXTI TECH LAU 3WAY VALVE POS TO VENT S1 | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 14 | [7 empty] | BITVAL
SWE7002F2 | LAGRANGE EXTI TECH LAU 3WAY VALVE POS S2 | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1070 | 2 | [7 empty] | BITVAL
SWE7002O2 | LAGRANGE EXTI TECH LAU 3WAY VALVE POS TO VENT S2 | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1070 | 4 | [7 empty] | BITVAL
ZZP7001D | SONO SOUND SYSTEM FAULT AM MASSIF | AL | O | FIL | 2 | S | [9 empty] | x==1 |  |  | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1072 | 0 | [7 empty] | BITVAL
ZZP7002D | SONO SOUND SYSTEM MONITORING LINE FAULT MASSIF | AL | O | FIL | 2 | S | [9 empty] | x==1 |  |  | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1072 | 2 | [7 empty] | BITVAL
SCE7003D | COPV PLATINE ACTIVATION ALERT EVACUATION ALARM | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1073 | 0 | [7 empty] | BITVAL
SCE7004D | COPV PLATINE ACTIVATION ALERT REPLI ALARM | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1073 | 2 | [7 empty] | BITVAL
SCE7005D | PRS PLATINE ACTIVATION ALERT EVACUATION ALARM | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1073 | 4 | [7 empty] | BITVAL
SCE7006D | PRS PLATINE ACTIVATION ALERT REPLI ALARM | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1073 | 6 | [7 empty] | BITVAL
SCE7007D | PANDORA PLATINE ACTIVATION ALERT EVACUATION ALARM | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1073 | 8 | [7 empty] | BITVAL
SCE7008D | PANDORA PLATINE ACTIVATION ALERT REPLI ALARM | AL | O | FIL | 2 | S | [12 empty] | S | [13 empty] | MTCP | 500 |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 1073 | 10 | [7 empty] | BITVAL
SZI7101W | Alarme Feu HA Lagrange Hall 0001 ZDA01 - ZONE HA 1 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 2 | [7 empty] | BITVAL
SZI7102W | Alarme Feu HA Lagrange Hall stockage S.E.P 0001b ZDA02 - ZONE HA 2 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 6 | [7 empty] | BITVAL
SZI7103W | Alarme Feu HA Lagrange Stock mat spéci lanceur 0002 ZDA03 - ZONE HA 3 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 10 | [7 empty] | BITVAL
SZI7104W | Alarme Feu HA Lagrange Local électrique 0003 ZDA04 - ZONE HA 4 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1101 | 14 | [7 empty] | BITVAL
SZI7105W | Alarme Feu HA Lagrange Local climatisation 0004 ZDA05 - ZONE HA 5 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 2 | [7 empty] | BITVAL
SZI7106W | Alarme Feu HA Lagrange Atelier mécanique 0005a ZDA06 - ZONE HA 6 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 6 | [7 empty] | BITVAL
SZI7107W | Alarme Feu HA Lagrange Sas atelier mécanique 0005bZDA07 - ZONE HA 7 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 10 | [7 empty] | BITVAL
SZI7108W | Alarme Feu HA Lagrange Local 0005c ZDA08 - ZONE HA 8 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1102 | 14 | [7 empty] | BITVAL
SZI7110W | Alarme Feu HA Lagrange Magasin SPPI 0006b ZDA10 - ZONE HA 10 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 2 | [7 empty] | BITVAL
SZI7109W | Alarme Feu HA Lagrange Vestiaires S.E.P 0006a ZDA09 - ZONE HA 9 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 6 | [7 empty] | BITVAL
SZI7111W | Alarme Feu HA Lagrange Vestiares 0007 ZDA11 - ZONE HA 11 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 10 | [7 empty] | BITVAL
SZI7112W | Alarme Feu HA Lagrange Local batteries 0010 ZDA12 - ZONE HA 12 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1103 | 14 | [7 empty] | BITVAL
SZI7113W | Alarme Feu HA Lagrange Couloir Nord Est 0011 ZDA13 - ZONE HA 13 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 2 | [7 empty] | BITVAL
SZI7114W | Alarme Feu HA Lagrange Local telecom 0012 ZDA14 - ZONE HA 14 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 6 | [7 empty] | BITVAL
SZI7115W | Alarme Feu HA Lagrange Vestiares 0013 ZDA15 - ZONE HA 15 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 10 | [7 empty] | BITVAL
SZI7116W | Alarme Feu HA Lagrange Magasin 0015 ZDA16 - ZONE HA 16 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1104 | 14 | [7 empty] | BITVAL
SZI7117W | Alarme Feu HA Lagrange Magasin AR4/5 0016 ZDA17 - ZONE HA 17 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 2 | [7 empty] | BITVAL
SZI7118W | Alarme Feu HA Lagrange Couloir Nord Ouest 0017 ZDA18 - ZONE HA 18 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 6 | [7 empty] | BITVAL
SZI7119W | Alarme Feu HA Lagrange Zone prépartion 0018a ZDA19 - ZONE HA 19 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 10 | [7 empty] | BITVAL
SZI7120W | Alarme Feu HA Lagrange Zone prépartion 0018b ZDA20 - ZONE HA 20 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1105 | 14 | [7 empty] | BITVAL
SZI7121W | Alarme Feu HA Lagrange Atelier Nord Clim 0019 ZDA21 - ZONE HA 21 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 2 | [7 empty] | BITVAL
SZI7122W | Alarme Feu HA Lagrange Local onduleur babar 0020 ZDA22 - ZONE HA 22 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 6 | [7 empty] | BITVAL
SZI7123W | Alarme Feu HA Lagrange Atelier charge batterie 0020 ZDA23 - ZONE HA 23 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 10 | [7 empty] | BITVAL
SZI7124W | Alarme Feu HA Lagrange Bureau 0021 ZDA24 - ZONE HA 24 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1106 | 14 | [7 empty] | BITVAL
SZI7125W | Alarme Feu HA Lagrange SPPM AR4/5 0022 ZDA25 - ZONE HA 25 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 2 | [7 empty] | BITVAL
SZI7126W | Alarme Feu HA Lagrange Labo électrique 0023aZDA26 - ZONE HA 26 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 6 | [7 empty] | BITVAL
SZI7127W | Alarme Feu HA Lagrange Bureau logistique AR4/5 0023bZDA27 - ZONE HA 27 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 10 | [7 empty] | BITVAL
SZI7128W | Alarme Feu HA Lagrange Magasin AR4 0024 ZDA28 - ZONE HA 28 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1107 | 14 | [7 empty] | BITVAL
SZI7129W | Alarme Feu HA Lagrange Magasin ST/EX 0026 ZDA29 - ZONE HA 29 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 2 | [7 empty] | BITVAL
SZI7130W | Alarme Feu HA Lagrange Magasin A.E produit toxique 0027 ZDA30 - ZONE HA 30 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 6 | [7 empty] | BITVAL
SZI7131W | Alarme Feu HA Lagrange Plannification AR4/5 0039 ZDA31 - ZONE HA 31 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI75 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 10 | [7 empty] | BITVAL
SZI7132W | Alarme Feu HA Lagrange Bureau SPPI 0040a ZDA32 - ZONE HA 32 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1108 | 14 | [7 empty] | BITVAL
SZI7133W | Alarme Feu HA Lagrange Salle préparation AR4 0040b -ZDA33 - ZONE HA 33 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 2 | [7 empty] | BITVAL
SZI7134W | Alarme Feu HA Lagrange Salle préparation AR5 0041 ZDA34 - ZONE HA 34 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 6 | [7 empty] | BITVAL
SZI7135W | Alarme Feu HA Lagrange Zone arrivée depart magasin 0042 ZDA35 - ZONE HA 35 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 10 | [7 empty] | BITVAL
SZI7136W | Alarme Feu HA Lagrange Laboratoire analyseur 0043a ZDA36 - ZONE HA 36 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1109 | 14 | [7 empty] | BITVAL
SZI7137W | Alarme Feu HA Lagrange Salle chaude 0043b ZDA37 - ZONE HA 37 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 2 | [7 empty] | BITVAL
SZI7138W | Alarme Feu HA Lagrange Sas salle chaude 0043c ZDA38 - ZONE HA 38 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 6 | [7 empty] | BITVAL
SZI7139W | Alarme Feu HA Lagrange Local 0043d ZDA39 - ZONE HA 39 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 10 | [7 empty] | BITVAL
SZI7140W | Alarme Feu HA Lagrange Atelier maintenance 0044 ZDA40 - ZONE HA 40 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1110 | 14 | [7 empty] | BITVAL
SZI7141W | Alarme Feu HA Lagrange Bureau atelier 0044b ZDA41 - ZONE HA 41 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 2 | [7 empty] | BITVAL
SZI7142W | Alarme Feu HA Lagrange Vestiaires 0047 ZDA42 - ZONE HA 42 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 6 | [7 empty] | BITVAL
SZI7143W | Alarme Feu HA Lagrange MAGASIN A.E MATERIEL LOURD 0048 ZDA43 - ZONE HA 43 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 10 | [7 empty] | BITVAL
SZI7144W | Alarme Feu HA Lagrange Magasin pièce detaché SOGAL 0049 ZDA44 - ZONE HA 44 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI77 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1111 | 14 | [7 empty] | BITVAL
SZI7145W | Alarme Feu HA Lagrange Local relumix 0050 ZDA45 - ZONE HA 45 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 2 | [7 empty] | BITVAL
SZI7146W | Alarme Feu HA Lagrange Salle déshabillage 0051 ZDA46 - ZONE HA 46 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 6 | [7 empty] | BITVAL
SZI7147W | Alarme Feu HA Lagrange Salle d'habillage 0057 ZDA47 - ZONE HA 47 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 10 | [7 empty] | BITVAL
SZI7148W | Alarme Feu HA Lagrange Salle pollué 0059 ZDA48 - ZONE HA 48 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1112 | 14 | [7 empty] | BITVAL
SZI7149W | Alarme Feu HA Lagrange Couloir 0029 ZDA49 - ZONE HA 49 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1113 | 2 | [7 empty] | BITVAL
SZI7150W | Alarme Feu HA Lagrange Couloir 0031 ZDA50 - ZONE HA 50 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI78 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1113 | 6 | [7 empty] | BITVAL
SZI7151W | Alarme Feu HA Lagrange Combles ZDA51 - ZONE HA 51 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1113 | 10 | [7 empty] | BITVAL
SZI7155W | Alarme Feu HA Lagrange Extension HA 0028 ZDA49 - ZONE HA 55 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1114 | 10 | [7 empty] | BITVAL
SZI7156W | Alarme Feu HA Lagrange Salle de Repos 0014 ZDA52 - ZONE HA 56 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI76 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1114 | 14 | [7 empty] | BITVAL
VRP6401D1 | VEGA GANTRY PLC : FRESH AIR MOTORISED DAMPER 401.1 (CTA 1) DEFAULT | AL |  | RES | 1 | C | [12 empty] | C | [13 empty] | NOT | 1000 |  | HVAC13 | HVAC |  | 7 |  |  | 3000 | 0 | 14122 | 0 | 16416 | 3666 | 0 | EL6021_M181 |  | BITVAL
VCN7005CM201 | CMDE ECO/OPE AC 1 SALLE 05 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | 170 | 350 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3001 | NA | [7 empty] | INT | 250
VCN7005CA201 | CMDE ECO/OPE AC 1 SALLE 05 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | 170 | 350 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3001 | NA | [7 empty] | INT | 270
VCN7005CM101 | CMDE MARCHE/ARRET AC 1 SALLE 05 LAGRANGE - U16(4), MARCHE(1) / U16(4),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3002 | NA | [7 empty] | UINT | 1
VCN7005CA101 | CMDE MARCHE/ARRET AC 1 SALLE 05 LAGRANGE - U16(4), MARCHE(1) / U16(4),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3002 | NA | [7 empty] | UINT | 0
VVV7010CM201 | CMDE ECO/OPE VC 1 SALLE 10 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3003 | NA | [7 empty] | INT | 250
SCX7001G | LAGRANGE EXTI UPS BATT CU READY | CR | O | FIL | 2 | S | [26 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 0 | [7 empty] | BITVAL
SCX7001U | LAGRANGE EXTI UPS BATT POWER ON | CR | O | FIL | 2 | S | [26 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 2 | [7 empty] | BITVAL
SCX7001D | **LAGRANGE EXTI UPS BATT GENERAL FAULT | CR | O | FIL | 2 | S | [22 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 4 | [7 empty] | BITVAL
SPB7001 | **LAGRANGE EXTI UPS BATT BOTTLE PRESSURE BORA | CR | O | FIL | 2 | S | [22 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1068 | 10 | [7 empty] | BITVAL
SCX7002G | LAGRANGE EXTI TECH LAU CU READY | CR | O | FIL | 2 | S | [26 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 0 | [7 empty] | BITVAL
SCX7002U | LAGRANGE EXTI TECH LAU POWER ON | CR | O | FIL | 2 | S | [26 empty] | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 2 | [7 empty] | BITVAL
SCX7002D | **LAGRANGE EXTI TECH LAU GENERAL FAULT | CR | O | FIL | 2 | S | [22 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 4 | [7 empty] | BITVAL
SPB7002S1 | **LAGRANGE EXTI TECH LAU BOTTLE PRESSURE BORA S1 | CR | O | FIL | 2 | S | [22 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1069 | 10 | [7 empty] | BITVAL
SPB7002S2 | **LAGRANGE EXTI TECH LAU BOTTLE PRESSURE BORA S2 | CR | O | FIL | 2 | S | [22 empty] | NEQUAL |  |  |  | MTCP | 500 |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 1070 | 0 | [7 empty] | BITVAL
VVV7010CA201 | CMDE ECO/OPE VC 1 SALLE 10 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3003 | NA | [7 empty] | INT | 270
VVV7010CM101 | CMDE MARCHE/ARRET VC 1 SALLE 10 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3004 | NA | [7 empty] | INT | 5
VVV7010CA101 | CMDE MARCHE/ARRET VC 1 SALLE 10 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3004 | NA | [7 empty] | INT | 1
VVV7013CM201 | CMDE ECO/OPE VC 1 SALLE 13 LAGRANGE - I16(3),MODE ECO(27) / I16(3),MODE OPE(25) | CA | N | RES | 2 | C |  |  | °C | 1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3005 | NA | [7 empty] | INT | 250
VVV7013CA201 | CMDE ECO/OPE VC 1 SALLE 13 LAGRANGE - I16(3),MODE ECO(27) / I16(3),MODE OPE(25) | CA | N | RES | 2 | C |  |  | °C | 1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3005 | NA | [7 empty] | INT | 270
VVV7013CM101 | CMDE MARCHE/ARRET VC 1 SALLE 13 LAGRANGE - I16(3),MARCHE(1) / I16(3),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3006 | NA | [7 empty] | INT | 1
VVV7013CA101 | CMDE MARCHE/ARRET VC 1 SALLE 13 LAGRANGE - I16(3),MARCHE(1) / I16(3),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3006 | NA | [7 empty] | INT | 0
VVV7010CM202 | CMDE ECO/OPE VC 2 SALLE 10 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3009 | NA | [7 empty] | INT | 250
VVV7010CA202 | CMDE ECO/OPE VC 2 SALLE 10 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3009 | NA | [7 empty] | INT | 270
VVV7010CM102 | CMDE MARCHE/ARRET VC 2 SALLE 10 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3010 | NA | [7 empty] | INT | 5
VVV7010CA102 | CMDE MARCHE/ARRET VC 2 SALLE 10 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3010 | NA | [7 empty] | INT | 1
VVV7013CM202 | CMDE ECO/OPE VC 2 SALLE 13 LAGRANGE - I16(3),MODE ECO(27) / I16(3),MODE OPE(25) | CA | N | RES | 2 | C |  |  | °C | 1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3011 | NA | [7 empty] | INT | 25
VVV7013CA202 | CMDE ECO/OPE VC 2 SALLE 13 LAGRANGE - I16(3),MODE ECO(27) / I16(3),MODE OPE(25) | CA | N | RES | 2 | C |  |  | °C | 1 | 120 | 330 | [6 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3011 | NA | [7 empty] | INT | 27
VVV7013CM102 | CMDE MARCHE/ARRET VC 2 SALLE 13 LAGRANGE - I16(3),MARCHE(1) / I16(3),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3012 | NA | [7 empty] | INT | 1
VVV7013CA102 | CMDE MARCHE/ARRET VC 2 SALLE 13 LAGRANGE - I16(3),MARCHE(1) / I16(3),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3012 | NA | [7 empty] | INT | 0
VVV7006CM101 | CMDE MARCHE/ARRET VC 1 SALLE 06 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3013 | NA | [7 empty] | INT | 5
VVV7006CA101 | CMDE MARCHE/ARRET VC 1 SALLE 06 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3013 | NA | [7 empty] | INT | 1
VVV7008CM101 | CMDE MARCHE/ARRET VC 1 SALLE 08 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3014 | NA | [7 empty] | INT | 5
VVV7008CA101 | CMDE MARCHE/ARRET VC 1 SALLE 08 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3014 | NA | [7 empty] | INT | 1
VVV7007CM101 | CMDE MARCHE/ARRET VC 1 SALLE 07 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3015 | NA | [7 empty] | INT | 5
VVV7007CA101 | CMDE MARCHE/ARRET VC 1 SALLE 07 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3015 | NA | [7 empty] | INT | 1
VVV7007CM102 | CMDE MARCHE/ARRET VC 2 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3016 | NA | [7 empty] | INT | 5
VVV7007CA102 | CMDE MARCHE/ARRET VC 2 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3016 | NA | [7 empty] | INT | 1
VVV7007CM103 | CMDE MARCHE/ARRET VC 3 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3017 | NA | [7 empty] | INT | 5
VVV7007CA103 | CMDE MARCHE/ARRET VC 3 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3017 | NA | [7 empty] | INT | 1
VVV7007CM104 | CMDE MARCHE/ARRET VC 4 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3018 | NA | [7 empty] | INT | 5
VVV7007CA104 | CMDE MARCHE/ARRET VC 4 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3018 | NA | [7 empty] | INT | 1
VVV7007CM105 | CMDE MARCHE/ARRET VC 5 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3019 | NA | [7 empty] | INT | 5
VVV7007CA105 | CMDE MARCHE/ARRET VC 5 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3019 | NA | [7 empty] | INT | 1
VVV7007CM106 | CMDE MARCHE/ARRET VC 6 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3020 | NA | [7 empty] | INT | 5
VVV7007CA106 | CMDE MARCHE/ARRET VC 6 SALLE 07 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 3020 | NA | [7 empty] | INT | 1
VVV7011CM101 | CMDE MARCHE/ARRET VC 1 SALLE 11 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3021 | NA | [7 empty] | INT | 5
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12914 | 2 | 16416 | 1250 | 2 | EL2809_M161 | 2 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12914 | 3 | 16416 | 1250 | 3 | EL2809_M161 | 2 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12914 | 4 | 16416 | 1250 | 4 | EL2809_M161 | 3 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12914 | 5 | 16416 | 1250 | 5 | EL2809_M161 | 3 | U8 | 32
VVV7011CA101 | CMDE MARCHE/ARRET VC 1 SALLE 11 LAGRANGE - I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3021 | NA | [7 empty] | INT | 1
VVV7012CM101 | CMDE MARCHE/ARRET VC 1 SALLE 12 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3022 | NA | [7 empty] | INT | 5
VVV7012CA101 | CMDE MARCHE/ARRET VC 1 SALLE 12 LAGRANGE- I16(3), MARCHE(5) / I16(3),ARRET(1) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 3022 | NA | [7 empty] | INT | 1
VCN7005CM202 | CMDE ECO/OPE AC 2 SALLE 05 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | [8 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3007 | NA | [7 empty] | INT | 250
VCN7005CA202 | CMDE ECO/OPE AC 2 SALLE 05 LAGRANGE - I16(3),MODE ECO(270) / I16(3),MODE OPE(250) | CA | N | RES | 2 | C |  |  | °C | 0.1 | [8 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3007 | NA | [7 empty] | INT | 270
VCN7005CM102 | CMDE MARCHE/ARRET AC 2 SALLE 05 LAGRANGE - I16(3),MARCHE(1) / I16(3),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3008 | NA | [7 empty] | INT | 1
VCN7005CA102 | CMDE MARCHE/ARRET AC 2 SALLE 05 LAGRANGE - I16(3),MARCHE(1) / I16(3),ARRET(0) | CA | N | RES | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 3008 | NA | [7 empty] | INT | 0
SFE6101CM | CDE MARCHE ACCES LIBRE TANGARA - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12926 | 10 | 16416 | 1275 | 0 | EL2809_M167 | 9 | U8 | 4
SFE6101CA | CDE ARRET ACCES LIBRE TANGARA - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12926 | 11 | 16416 | 1275 | 0 | EL2809_M167 | 9 | U8 | 8
SFE6102CM | CDE MARCHE ACCES CONTROLE TANGARA - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12926 | 12 | 16416 | 1275 | 0 | EL2809_M167 | 10 | U8 | 16
SFE6102CA | CDE ARRET ACCES CONTROLE TANGARA - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12926 | 13 | 16416 | 1275 | 0 | EL2809_M167 | 10 | U8 | 32
SFE6103CM | CDE MARCHE ACCES LIMITE TANGARA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12926 | 14 | 16416 | 1275 | 0 | EL2809_M167 | 11 | U8 | 64
SFE6103CA | CDE ARRET ACCES LIMITE TANGARA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12926 | 15 | 16416 | 1275 | 0 | EL2809_M167 | 11 | U8 | 128
SFE6104CM | CDE MARCHE ALERT EVAC TANGARA - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12927 | 0 | 16416 | 1276 | 0 | EL2809_M167 | 12 | U8 | 1
SFE6104CA | CDE ARRET ALERT EVAC TANGARA - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12927 | 1 | 16416 | 1276 | 0 | EL2809_M167 | 12 | U8 | 2
SFE6105CM | CDE MARCHE ALERT REPLI TANGARA - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12927 | 2 | 16416 | 1276 | 0 | EL2809_M167 | 13 | U8 | 4
SFE6105CA | CDE ARRET ALERT REPLI TANGARA - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12927 | 3 | 16416 | 1276 | 0 | EL2809_M167 | 13 | U8 | 8
SCE6100D | ** DEFAUT SYNTHESE ZONE TANGARA | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12863 | 8 | 16416 | 1149 | 0 | EL1134_M53 | 1 | BITVAL
SCE6101 | ** DECLENCHEMENT LOCAL ZONE TANGARA | AL | O | FIL | 1 | S | [10 empty] | 0 |  | S | [13 empty] | NOT | 1000 |  | MG71 | Moyens Generaux (MG) | CCS | [5 empty] | 12863 | 10 | 16416 | 1149 | 2 | EL1134_M53 | 5 | BITVAL
VFN6002S2 | Desenfumage 002 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 1 | 13120 | 2 | 16416 | 1662 | 2 | EL6021_M178 |  | BITVAL
VFN6004S2 | Desenfumage 004 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 5 | 13120 | 10 | 16416 | 1663 | 2 | EL6021_M178 |  | BITVAL
VFN6007S2 | Desenfumage 007 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 9 | 13121 | 2 | 16416 | 1664 | 2 | EL6021_M178 |  | BITVAL
VFN6008S2 | Desenfumage 008 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3050 | 13 | 13121 | 10 | 16416 | 1665 | 2 | EL6021_M178 |  | BITVAL
VFN6009S2 | Desenfumage 009 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 1 | 13122 | 2 | 16416 | 1666 | 2 | EL6021_M178 |  | BITVAL
VFN6010S2 | Desenfumage 010 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 5 | 13122 | 10 | 16416 | 1667 | 2 | EL6021_M178 |  | BITVAL
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 0 | 16416 | 1254 | 0 | EL2809_M162 | 1 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 1 | 16416 | 1254 | 1 | EL2809_M162 | 1 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 2 | 16416 | 1254 | 2 | EL2809_M162 | 2 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 3 | 16416 | 1254 | 3 | EL2809_M162 | 2 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 4 | 16416 | 1254 | 4 | EL2809_M162 | 3 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 5 | 16416 | 1254 | 5 | EL2809_M162 | 3 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 6 | 16416 | 1254 | 6 | EL2809_M162 | 4 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 7 | 16416 | 1254 | 7 | EL2809_M162 | 4 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 8 | 16416 | 1255 | 0 | EL2809_M162 | 5 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 9 | 16416 | 1255 | 1 | EL2809_M162 | 5 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 10 | 16416 | 1255 | 2 | EL2809_M162 | 6 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 11 | 16416 | 1255 | 3 | EL2809_M162 | 6 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 12 | 16416 | 1255 | 4 | EL2809_M162 | 7 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 13 | 16416 | 1255 | 5 | EL2809_M162 | 7 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 14 | 16416 | 1255 | 6 | EL2809_M162 | 8 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12916 | 15 | 16416 | 1255 | 7 | EL2809_M162 | 8 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 0 | 16416 | 1256 | 0 | EL2809_M162 | 9 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 1 | 16416 | 1256 | 1 | EL2809_M162 | 9 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 2 | 16416 | 1256 | 2 | EL2809_M162 | 10 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 3 | 16416 | 1256 | 3 | EL2809_M162 | 10 | U8 | 8
VFN6012S2 | Desenfumage 012 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 9 | 13123 | 2 | 16416 | 1668 | 2 | EL6021_M178 |  | BITVAL
VFN6013S2 | Desenfumage 013 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3051 | 13 | 13123 | 10 | 16416 | 1669 | 2 | EL6021_M178 |  | BITVAL
VFN6014S2 | Desenfumage 014 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 1 | 13124 | 2 | 16416 | 1670 | 2 | EL6021_M178 |  | BITVAL
VFN6101S2 | Desenfumage 101 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 5 | 13124 | 10 | 16416 | 1671 | 2 | EL6021_M178 |  | BITVAL
VFN6109S2 | Desenfumage 109 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3052 | 9 | 13125 | 2 | 16416 | 1672 | 2 | EL6021_M178 |  | BITVAL
VFN6113S2 | Desenfumage 113 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 1 | 13126 | 2 | 16416 | 1674 | 2 | EL6021_M178 |  | BITVAL
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 10 | 16416 | 1257 | 2 | EL2809_M162 | 14 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 11 | 16416 | 1257 | 3 | EL2809_M162 | 14 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 12 | 16416 | 1257 | 4 | EL2809_M162 | 15 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 13 | 16416 | 1257 | 5 | EL2809_M162 | 15 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 14 | 16416 | 1257 | 6 | EL2809_M162 | 16 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12917 | 15 | 16416 | 1257 | 7 | EL2809_M162 | 16 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 0 | 16416 | 1258 | 0 | EL2809_M163 | 1 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 1 | 16416 | 1258 | 1 | EL2809_M163 | 1 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 2 | 16416 | 1258 | 2 | EL2809_M163 | 2 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 3 | 16416 | 1258 | 3 | EL2809_M163 | 2 | U8 | 8
VFN6117S2 | Desenfumage117 Alimentation Ordinys FAULT (400 V) | AL | N | RES | 1 | E | [9 empty] | 0 |  |  | E | [13 empty] | POL | 1000 |  | E71 | HVAC |  | 4 |  |  | 3053 | 5 | 13126 | 10 | 16416 | 1675 | 2 | EL6021_M178 |  | BITVAL
WEL6001CA | CMD PROJECTEUR 1 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 10 | NA | 12351 | NA | 16416 | 124 | 0 | EL6021_M176 |  | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 10 | 16416 | 1259 | 2 | EL2809_M163 | 7 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 11 | 16416 | 1259 | 3 | EL2809_M163 | 7 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 12 | 16416 | 1259 | 4 | EL2809_M163 | 8 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 13 | 16416 | 1259 | 5 | EL2809_M163 | 8 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 14 | 16416 | 1259 | 6 | EL2809_M163 | 9 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12918 | 15 | 16416 | 1259 | 7 | EL2809_M163 | 9 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12919 | 0 | 16416 | 1260 | 0 | EL2809_M163 | 10 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12919 | 1 | 16416 | 1260 | 1 | EL2809_M163 | 10 | U8 | 2
WEL6001CM | CMD PROJECTEUR 1 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 10 | NA | 12351 | NA | 16416 | 124 | 0 | EL6021_M176 |  | U8 | 2
WEL6002CA | CMD PROJECTEUR 2 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 11 | NA | 12352 | NA | 16416 | 126 | 0 | EL6021_M176 |  | U8 | 1
WEL6002CM | CMD PROJECTEUR 2 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 11 | NA | 12352 | NA | 16416 | 126 | 0 | EL6021_M176 |  | U8 | 2
WEL6003CA | CMD PROJECTEUR 3 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 12 | NA | 12353 | NA | 16416 | 128 | 0 | EL6021_M176 |  | U8 | 1
WEL6003CM | CMD PROJECTEUR 3 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 12 | NA | 12353 | NA | 16416 | 128 | 0 | EL6021_M176 |  | U8 | 2
WEL6004CA | CMD PROJECTEUR 4 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 13 | NA | 12354 | NA | 16416 | 130 | 0 | EL6021_M176 |  | U8 | 1
WEL6004CM | CMD PROJECTEUR 4 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 13 | NA | 12354 | NA | 16416 | 130 | 0 | EL6021_M176 |  | U8 | 2
WBE6001CA | CMD TENSION SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 14 | NA | 12355 | NA | 16416 | 132 | 0 | EL6021_M176 |  | U8 | 1
WBE6001CM | CMD TENSION SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 14 | NA | 12355 | NA | 16416 | 132 | 0 | EL6021_M176 |  | U8 | 2
WBE6002CA | CMD TENSION SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 15 | NA | 12356 | NA | 16416 | 134 | 0 | EL6021_M176 |  | U8 | 1
WBE6002CM | CMD TENSION SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 15 | NA | 12356 | NA | 16416 | 134 | 0 | EL6021_M176 |  | U8 | 2
WPO6001CA | CMD APV SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 16 | NA | 12357 | NA | 16416 | 136 | 0 | EL6021_M176 |  | U8 | 1
WPO6001CM | CMD APV SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 16 | NA | 12357 | NA | 16416 | 136 | 0 | EL6021_M176 |  | U8 | 2
WPO6003CA | CMD APV SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 17 | NA | 12358 | NA | 16416 | 138 | 0 | EL6021_M176 |  | U8 | 1
WPO6003CM | CMD APV SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 17 | NA | 12358 | NA | 16416 | 138 | 0 | EL6021_M176 |  | U8 | 2
WPO6002CA | CMD APV SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 18 | NA | 12359 | NA | 16416 | 140 | 0 | EL6021_M176 |  | U8 | 1
WPO6002CM | CMD APV SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 18 | NA | 12359 | NA | 16416 | 140 | 0 | EL6021_M176 |  | U8 | 2
WBE6003CA | CMD TENSION SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 20 | NA | 12360 | NA | 16416 | 142 | 0 | EL6021_M176 |  | U8 | 1
WBE6003CM | CMD TENSION SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 20 | NA | 12360 | NA | 16416 | 142 | 0 | EL6021_M176 |  | U8 | 2
WEL6005CA | CMD PROJECTEUR 5 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 21 | NA | 12361 | NA | 16416 | 144 | 0 | EL6021_M176 |  | U8 | 1
WEL6005CM | CMD PROJECTEUR 5 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 21 | NA | 12361 | NA | 16416 | 144 | 0 | EL6021_M176 |  | U8 | 2
WEL6006CA | CMD PROJECTEUR 6 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 22 | NA | 12362 | NA | 16416 | 146 | 0 | EL6021_M176 |  | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12920 | 8 | 16416 | 1263 | 0 | EL2809_M164 | 6 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12920 | 9 | 16416 | 1263 | 1 | EL2809_M164 | 6 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12920 | 10 | 16416 | 1263 | 2 | EL2809_M164 | 7 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12920 | 11 | 16416 | 1263 | 3 | EL2809_M164 | 7 | U8 | 8
WEL6006CM | CMD PROJECTEUR 6 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 22 | NA | 12362 | NA | 16416 | 146 | 0 | EL6021_M176 |  | U8 | 2
WCO6001CA | CMD CAMERA CN1 ATT SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 26 | NA | 12363 | NA | 16416 | 148 | 0 | EL6021_M176 |  | U8 | 1
WCO6001CM | CMD CAMERA CN1 ATT SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 26 | NA | 12363 | NA | 16416 | 148 | 0 | EL6021_M176 |  | U8 | 2
WCO6002CA | CMD CAMERA CN2 ATT SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 28 | NA | 12364 | NA | 16416 | 150 | 0 | EL6021_M176 |  | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 0 | 16416 | 1264 | 0 | EL2809_M164 | 10 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 1 | 16416 | 1264 | 1 | EL2809_M164 | 10 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 2 | 16416 | 1264 | 2 | EL2809_M164 | 11 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 3 | 16416 | 1264 | 3 | EL2809_M164 | 11 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 4 | 16416 | 1264 | 4 | EL2809_M164 | 12 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 5 | 16416 | 1264 | 5 | EL2809_M164 | 12 | U8 | 32
WCO6002CM | CMD CAMERA CN2 ATT SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 28 | NA | 12364 | NA | 16416 | 150 | 0 | EL6021_M176 |  | U8 | 2
WCO6003CA | CMD CAMERA CN3 ATT SHELTER POE - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 29 | NA | 12365 | NA | 16416 | 152 | 0 | EL6021_M176 |  | U8 | 1
WCO6003CM | CMD CAMERA CN3 ATT SHELTER POE - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 29 | NA | 12365 | NA | 16416 | 152 | 0 | EL6021_M176 |  | U8 | 2
WCO6004CA | CMD CAMERA CN4 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 30 | NA | 12366 | NA | 16416 | 154 | 0 | EL6021_M176 |  | U8 | 1
WCO6004CM | CMD CAMERA CN4 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 30 | NA | 12366 | NA | 16416 | 154 | 0 | EL6021_M176 |  | U8 | 2
WCO6005CA | CMD CAMERA CN5 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 31 | NA | 12367 | NA | 16416 | 156 | 0 | EL6021_M176 |  | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 12 | 16416 | 1265 | 4 | EL2809_M164 | 16 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12921 | 13 | 16416 | 1265 | 5 | EL2809_M164 | 16 | U8 | 32
WCO6005CM | CMD CAMERA CN5 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 31 | NA | 12367 | NA | 16416 | 156 | 0 | EL6021_M176 |  | U8 | 2
WZC6000CA | CMD ARMEMENT API OPTIQUE - U8(2),ARMEE(2) / U8(2),DESARMEE(2) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 34 | NA | 12368 | NA | 16416 | 158 | 0 | EL6021_M176 |  | U8 | 1
WZC6000CM | CMD ARMEMENT API OPTIQUE - U8(2),ARMEE(2) / U8(2),DESARMEE(2) | CT | N | INT | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [7 empty] | NOT |  |  | W61 | Optique et Video VEGA (W) | CCS | 2 |  |  | 34 | NA | 12368 | NA | 16416 | 158 | 0 | EL6021_M176 |  | U8 | 2
OVP6306CF | CMDE RINCAGE FACADE O PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 10 | NA | 12701 | NA | 16416 | 824 | 0 | EL6021_M177 |  | U8 | 1
OVP6306CO | CMDE RINCAGE FACADE O PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | O | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 10 | NA | 12701 | NA | 16416 | 824 | 0 | EL6021_M177 |  | U8 | 2
OVP6307CF | CMDE RINCAGE FACADE S PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 11 | NA | 12702 | NA | 16416 | 826 | 0 | EL6021_M177 |  | U8 | 1
OVP6307CO | CMDE RINCAGE FACADE S PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 11 | NA | 12702 | NA | 16416 | 826 | 0 | EL6021_M177 |  | U8 | 2
OVP6308CF | CMDE RINCAGE FACADE E PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 12 | NA | 12703 | NA | 16416 | 828 | 0 | EL6021_M177 |  | U8 | 1
OVP6308CO | CMDE RINCAGE FACADE E PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 12 | NA | 12703 | NA | 16416 | 828 | 0 | EL6021_M177 |  | U8 | 2
OVP6309CF | CMDE RINCAGE FACADE N PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 13 | NA | 12704 | NA | 16416 | 830 | 0 | EL6021_M177 |  | U8 | 1
OVP6309CO | CMDE RINCAGE FACADE N PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | O | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 13 | NA | 12704 | NA | 16416 | 830 | 0 | EL6021_M177 |  | U8 | 2
OVP6310CF | CMDE RINCAGE TOITURE O PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 14 | NA | 12705 | NA | 16416 | 832 | 0 | EL6021_M177 |  | U8 | 1
OVP6310CO | CMDE RINCAGE TOITURE O PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | O | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 14 | NA | 12705 | NA | 16416 | 832 | 0 | EL6021_M177 |  | U8 | 2
OVP6311CF | CMDE RINCAGE TOITURE E PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | N | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 15 | NA | 12706 | NA | 16416 | 834 | 0 | EL6021_M177 |  | U8 | 1
OVP6311CO | CMDE RINCAGE TOITURE E PORTIQUE - U16(2),FERMER(1) / U16(2),OUVRIR(2) | CT | O | INT | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 15 | NA | 12706 | NA | 16416 | 834 | 0 | EL6021_M177 |  | U8 | 2
OVP6315CF | CMDE RINCAGE PORTIQUE- U16(2),OUVRIR(1) / U16(2),FERMER(2) | CT | O | INT | 1 | F | [11 empty] | ON | F | NO | NO | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 16 | NA | 12707 | NA | 16416 | 836 | 0 | EL6021_M177 |  | U8 | 2
OVP6315CO | CMDE RINCAGE PORTIQUE- U16(2),OUVRIR(1) / U16(2),FERMER(2) | CT | N | INT | 1 | F | [11 empty] | ON | F | NO | NO | [11 empty] | NOT |  |  | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 16 | NA | 12707 | NA | 16416 | 836 | 0 | EL6021_M177 |  | U8 | 1
WEL6001CA | CMD PROJECTEUR 1 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 10 | NA | 12757 | 0 | 16416 | 936 | 0 | NA |  | U8 | 0
WEL6001CM | CMD PROJECTEUR 1 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [8 empty] | O | NF |  | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 10 | NA | 12757 | 0 | 16416 | 936 | 0 | NA |  | U8 | 1
WEL6002CA | CMD PROJECTEUR 2 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 11 | NA | 12758 | 0 | 16416 | 938 | 0 | NA |  | U8 | 0
WEL6002CM | CMD PROJECTEUR 2 SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 11 | NA | 12758 | 0 | 16416 | 938 | 0 | NA |  | U8 | 1
WEL6003CA | CMD PROJECTEUR 3 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 12 | NA | 12759 | 0 | 16416 | 940 | 0 | NA |  | U8 | 0
WEL6003CM | CMD PROJECTEUR 3 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 12 | NA | 12759 | 0 | 16416 | 940 | 0 | NA |  | U8 | 1
WEL6004CA | CMD PROJECTEUR 4 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 13 | NA | 12760 | 0 | 16416 | 942 | 0 | NA |  | U8 | 0
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 6 | 16416 | 1268 | 6 | EL2809_M165 | 13 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 7 | 16416 | 1268 | 7 | EL2809_M165 | 13 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 8 | 16416 | 1269 | 0 | EL2809_M165 | 14 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 9 | 16416 | 1269 | 1 | EL2809_M165 | 14 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 10 | 16416 | 1269 | 2 | EL2809_M165 | 15 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 11 | 16416 | 1269 | 3 | EL2809_M165 | 15 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 12 | 16416 | 1269 | 4 | EL2809_M165 | 16 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12923 | 13 | 16416 | 1269 | 5 | EL2809_M165 | 16 | U8 | 32
WEL6004CM | CMD PROJECTEUR 4 SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 13 | NA | 12760 | 0 | 16416 | 942 | 0 | NA |  | U8 | 1
WBE6001CA | CMD TENSION SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 14 | NA | 12761 | 0 | 16416 | 944 | 0 | NA |  | U8 | 0
WBE6001CM | CMD TENSION SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 14 | NA | 12761 | 0 | 16416 | 944 | 0 | NA |  | U8 | 1
WBE6002CA | CMD TENSION SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 15 | NA | 12762 | 0 | 16416 | 946 | 0 | NA |  | U8 | 0
WBE6002CM | CMD TENSION SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 15 | NA | 12762 | 0 | 16416 | 946 | 0 | NA |  | U8 | 1
WPO6001CA | CMD APV SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 16 | NA | 12763 | 0 | 16416 | 948 | 0 | NA |  | U8 | 0
WPO6001CM | CMD APV SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 16 | NA | 12763 | 0 | 16416 | 948 | 0 | NA |  | U8 | 1
WPO6003CA | CMD APV SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 17 | NA | 12764 | 0 | 16416 | 950 | 0 | NA |  | U8 | 0
WPO6003CM | CMD APV SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 17 | NA | 12764 | 0 | 16416 | 950 | 0 | NA |  | U8 | 1
WPO6002CA | CMD APV SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 18 | NA | 12765 | 0 | 16416 | 952 | 0 | NA |  | U8 | 0
WPO6002CM | CMD APV SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 18 | NA | 12765 | 0 | 16416 | 952 | 0 | NA |  | U8 | 1
WBE6003CA | CMD TENSION SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 20 | NA | 12766 | 0 | 16416 | 954 | 0 | NA |  | U8 | 0
WBE6003CM | CMD TENSION SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 20 | NA | 12766 | 0 | 16416 | 954 | 0 | NA |  | U8 | 1
WEL6005CA | CMD PROJECTEUR 5 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 21 | NA | 12767 | 0 | 16416 | 956 | 0 | NA |  | U8 | 0
WEL6005CM | CMD PROJECTEUR 5 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 21 | NA | 12767 | 0 | 16416 | 956 | 0 | NA |  | U8 | 1
WEL6006CA | CMD PROJECTEUR 6 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 22 | NA | 12768 | 0 | 16416 | 958 | 0 | NA |  | U8 | 0
WEL6006CM | CMD PROJECTEUR 6 SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 22 | NA | 12768 | 0 | 16416 | 958 | 0 | NA |  | U8 | 1
WCO6001CA | CMD CAMERA CN1 ATT SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 26 | NA | 12769 | 0 | 16416 | 960 | 0 | NA |  | U8 | 0
WCO6001CM | CMD CAMERA CN1 ATT SHELTER N - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 26 | NA | 12769 | 0 | 16416 | 960 | 0 | NA |  | U8 | 1
WCO6002CA | CMD CAMERA CN2 ATT SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 28 | NA | 12770 | 0 | 16416 | 962 | 0 | NA |  | U8 | 0
WCO6002CM | CMD CAMERA CN2 ATT SHELTER E - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 28 | NA | 12770 | 0 | 16416 | 962 | 0 | NA |  | U8 | 1
WCO6003CA | CMD CAMERA CN3 ATT SHELTER POE - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 29 | NA | 12771 | 0 | 16416 | 964 | 0 | NA |  | U8 | 0
WCO6003CM | CMD CAMERA CN3 ATT SHELTER POE - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 29 | NA | 12771 | 0 | 16416 | 964 | 0 | NA |  | U8 | 1
WCO6004CA | CMD CAMERA CN4 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 30 | NA | 12772 | 0 | 16416 | 966 | 0 | NA |  | U8 | 0
WCO6004CM | CMD CAMERA CN4 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 30 | NA | 12772 | 0 | 16416 | 966 | 0 | NA |  | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12925 | 8 | 16416 | 1273 | 0 | EL2809_M166 | 16 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12925 | 9 | 16416 | 1273 | 1 | EL2809_M166 | 16 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12925 | 10 | 16416 | 1273 | 2 | EL2809_M167 | 1 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12925 | 11 | 16416 | 1273 | 3 | EL2809_M167 | 1 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12925 | 12 | 16416 | 1273 | 4 | EL2809_M167 | 2 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12925 | 13 | 16416 | 1273 | 5 | EL2809_M167 | 2 | U8 | 32
WCO6005CA | CMD CAMERA CN5 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 31 | NA | 12773 | 0 | 16416 | 968 | 0 | NA |  | U8 | 0
WCO6005CM | CMD CAMERA CN5 ATT SHELTER O - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF |  |  |  | WZC6001M (OFF) | [10 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 31 | NA | 12773 | 0 | 16416 | 968 | 0 | NA |  | U8 | 1
WZC6000CA | CMD ARMEMENT API OPTIQUE - U8(2),ARMEE(2) / U8(2),DESARMEE(2) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF | [14 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 34 | NA | 12774 | 0 | 16416 | 970 | 0 | NA |  | U8 | 0
WZC6000CM | CMD ARMEMENT API OPTIQUE - U8(2),ARMEE(2) / U8(2),DESARMEE(2) | CT | N | RES | 1 | O | [11 empty] | OFF | O | NO | NF | [14 empty] | W61 | Optique et Video (W) | CCS | 2 |  |  | 34 | NA | 12774 | 0 | 16416 | 970 | 0 | NA |  | U8 | 1
OVP6306CF | CMDE RINCAGE FACADE O PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 10 | NA | 12784 | 0 | 16416 | 990 | 0 | NA |  | U8 | 0
OVP6306CO | CMDE RINCAGE FACADE O PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | O | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 10 | NA | 12784 | 0 | 16416 | 990 | 0 | NA |  | U8 | 1
OVP6307CF | CMDE RINCAGE FACADE S PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 11 | NA | 12785 | 0 | 16416 | 992 | 0 | NA |  | U8 | 0
OVP6307CO | CMDE RINCAGE FACADE S PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 11 | NA | 12785 | 0 | 16416 | 992 | 0 | NA |  | U8 | 1
OVP6308CF | CMDE RINCAGE FACADE E PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 12 | NA | 12786 | 0 | 16416 | 994 | 0 | NA |  | U8 | 0
OVP6308CO | CMDE RINCAGE FACADE E PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 12 | NA | 12786 | 0 | 16416 | 994 | 0 | NA |  | U8 | 1
OVP6309CF | CMDE RINCAGE FACADE N PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 13 | NA | 12787 | 0 | 16416 | 996 | 0 | NA |  | U8 | 0
OVP6309CO | CMDE RINCAGE FACADE N PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | O | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 13 | NA | 12787 | 0 | 16416 | 996 | 0 | NA |  | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 4 | 16416 | 1276 | 4 | EL2809_M167 | 14 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 5 | 16416 | 1276 | 5 | EL2809_M167 | 14 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 6 | 16416 | 1276 | 6 | EL2809_M167 | 15 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 7 | 16416 | 1276 | 7 | EL2809_M167 | 15 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 8 | 16416 | 1277 | 0 | EL2809_M167 | 16 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 9 | 16416 | 1277 | 1 | EL2809_M167 | 16 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 10 | 16416 | 1277 | 2 | EL2809_M168 | 1 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 11 | 16416 | 1277 | 3 | EL2809_M168 | 1 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 12 | 16416 | 1277 | 4 | EL2809_M168 | 2 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 13 | 16416 | 1277 | 5 | EL2809_M168 | 2 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 14 | 16416 | 1277 | 6 | EL2809_M168 | 3 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12927 | 15 | 16416 | 1277 | 7 | EL2809_M168 | 3 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 0 | 16416 | 1278 | 0 | EL2809_M168 | 4 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 1 | 16416 | 1278 | 1 | EL2809_M168 | 4 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 2 | 16416 | 1278 | 2 | EL2809_M168 | 5 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 3 | 16416 | 1278 | 3 | EL2809_M168 | 5 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 4 | 16416 | 1278 | 4 | EL2809_M168 | 6 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 5 | 16416 | 1278 | 5 | EL2809_M168 | 6 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 6 | 16416 | 1278 | 6 | EL2809_M168 | 7 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 7 | 16416 | 1278 | 7 | EL2809_M168 | 7 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 8 | 16416 | 1279 | 0 | EL2809_M168 | 8 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 9 | 16416 | 1279 | 1 | EL2809_M168 | 8 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 10 | 16416 | 1279 | 2 | EL2809_M168 | 9 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 11 | 16416 | 1279 | 3 | EL2809_M168 | 9 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 12 | 16416 | 1279 | 4 | EL2809_M168 | 10 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 13 | 16416 | 1279 | 5 | EL2809_M168 | 10 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 14 | 16416 | 1279 | 6 | EL2809_M168 | 11 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12928 | 15 | 16416 | 1279 | 7 | EL2809_M168 | 11 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 0 | 16416 | 1280 | 0 | EL2809_M168 | 12 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 1 | 16416 | 1280 | 1 | EL2809_M168 | 12 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 2 | 16416 | 1280 | 2 | EL2809_M168 | 13 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 3 | 16416 | 1280 | 3 | EL2809_M168 | 13 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 4 | 16416 | 1280 | 4 | EL2809_M168 | 14 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 5 | 16416 | 1280 | 5 | EL2809_M168 | 14 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 6 | 16416 | 1280 | 6 | EL2809_M168 | 15 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 7 | 16416 | 1280 | 7 | EL2809_M168 | 15 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 8 | 16416 | 1281 | 0 | EL2809_M168 | 16 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 9 | 16416 | 1281 | 1 | EL2809_M168 | 16 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 10 | 16416 | 1281 | 2 | EL2809_M169 | 1 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 11 | 16416 | 1281 | 3 | EL2809_M169 | 1 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 12 | 16416 | 1281 | 4 | EL2809_M169 | 2 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 13 | 16416 | 1281 | 5 | EL2809_M169 | 2 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 14 | 16416 | 1281 | 6 | EL2809_M169 | 3 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12929 | 15 | 16416 | 1281 | 7 | EL2809_M169 | 3 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 0 | 16416 | 1282 | 0 | EL2809_M169 | 4 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 1 | 16416 | 1282 | 1 | EL2809_M169 | 4 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 2 | 16416 | 1282 | 2 | EL2809_M169 | 5 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 3 | 16416 | 1282 | 3 | EL2809_M169 | 5 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 4 | 16416 | 1282 | 4 | EL2809_M169 | 6 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 5 | 16416 | 1282 | 5 | EL2809_M169 | 6 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 6 | 16416 | 1282 | 6 | EL2809_M169 | 7 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12930 | 7 | 16416 | 1282 | 7 | EL2809_M169 | 7 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12930 | 8 | 16416 | 1283 | 0 | EL2809_M169 | 8 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12930 | 9 | 16416 | 1283 | 1 | EL2809_M169 | 8 | U8 | 2
OVP6310CF | CMDE RINCAGE TOITURE O PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 14 | NA | 12788 | 0 | 16416 | 998 | 0 | NA |  | U8 | 0
OVP6310CO | CMDE RINCAGE TOITURE O PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | O | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 14 | NA | 12788 | 0 | 16416 | 998 | 0 | NA |  | U8 | 1
OVP6311CF | CMDE RINCAGE TOITURE E PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 15 | NA | 12789 | 0 | 16416 | 1000 | 0 | NA |  | U8 | 0
OVP6311CO | CMDE RINCAGE TOITURE E PORTIQUE - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | O | RES | 1 | F | [11 empty] | OFF | F | NO | NF | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 15 | NA | 12789 | 0 | 16416 | 1000 | 0 | NA |  | U8 | 1
OVP6315CF | CMDE RINCAGE PORTIQUE- U8(2),OUVRIR(1) / U8(2),FERMER(2) | CT | O | RES | 1 | F | [11 empty] | ON | F | NO | NO | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 16 | NA | 12790 | 0 | 16416 | 1002 | 0 | NA |  | U8 | 1
OVP6315CO | CMDE RINCAGE PORTIQUE- U8(2),OUVRIR(1) / U8(2),FERMER(2) | CT | N | RES | 1 | F | [11 empty] | ON | F | NO | NO | [14 empty] | MG62;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 16 | NA | 12790 | 0 | 16416 | 1002 | 0 | NA |  | U8 | 0
SFE6010CM | CDE FEUX ROUGE PORT. NIV 18.400 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 0 | 16416 | 1246 | 0 | EL2809_M160 | 1 | U8 | 1
SFE6010CA | CDE FEUX ROUGE PORT. NIV 18.400 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 1 | 16416 | 1246 | 0 | EL2809_M160 | 1 | U8 | 2
SFE6011CM | CDE FEUX ORANGE PORT. NIV 18.400 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 2 | 16416 | 1246 | 0 | EL2809_M160 | 2 | U8 | 4
SFE6011CA | CDE FEUX ORANGE PORT. NIV 18.400 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 3 | 16416 | 1246 | 0 | EL2809_M160 | 2 | U8 | 8
SFE6020CM | CDE FEUX ROUGE PORT. NIV 21.200 - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 4 | 16416 | 1246 | 0 | EL2809_M160 | 3 | U8 | 16
SFE6020CA | CDE FEUX ROUGE PORT. NIV 21.200 - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 5 | 16416 | 1246 | 0 | EL2809_M160 | 3 | U8 | 32
SFE6021CM | CDE FEUX ORANGE PORT. NIV 21.200 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 6 | 16416 | 1246 | 0 | EL2809_M160 | 4 | U8 | 64
SFE6021CA | CDE FEUX ORANGE PORT. NIV 21.200 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 7 | 16416 | 1246 | 0 | EL2809_M160 | 4 | U8 | 128
SFE6030CM | CDE FEUX ROUGE PORT. NIV 24.000 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 8 | 16416 | 1247 | 0 | EL2809_M160 | 5 | U8 | 1
SFE6030CA | CDE FEUX ROUGE PORT. NIV 24.000 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 9 | 16416 | 1247 | 0 | EL2809_M160 | 5 | U8 | 2
SFE6031CM | CDE FEUX ORANGE PORT. NIV 24.000 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 10 | 16416 | 1247 | 0 | EL2809_M160 | 6 | U8 | 4
SFE6031CA | CDE FEUX ORANGE PORT. NIV 24.000 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 11 | 16416 | 1247 | 0 | EL2809_M160 | 6 | U8 | 8
SFE6040CM | CDE FEUX ROUGE PORT. PF ELEV 1 - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 12 | 16416 | 1247 | 0 | EL2809_M160 | 7 | U8 | 16
SFE6040CA | CDE FEUX ROUGE PORT. PF ELEV 1 - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 13 | 16416 | 1247 | 0 | EL2809_M160 | 7 | U8 | 32
SFE6041CM | CDE FEUX ORANGE PORT. PF ELEV 1 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 14 | 16416 | 1247 | 0 | EL2809_M160 | 8 | U8 | 64
SFE6041CA | CDE FEUX ORANGE PORT. PF ELEV 1 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12912 | 15 | 16416 | 1247 | 0 | EL2809_M160 | 8 | U8 | 128
SFE6050CM | CDE FEUX ROUGE PORT. PF ELEV 2 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 0 | 16416 | 1248 | 0 | EL2809_M160 | 9 | U8 | 1
SFE6050CA | CDE FEUX ROUGE PORT. PF ELEV 2 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 1 | 16416 | 1248 | 0 | EL2809_M160 | 9 | U8 | 2
SFE6051CM | CDE FEUX ORANGE PORT. PF ELEV 2 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 2 | 16416 | 1248 | 0 | EL2809_M160 | 10 | U8 | 4
SFE6051CA | CDE FEUX ORANGE PORT. PF ELEV 2 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG73 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 3 | 16416 | 1248 | 0 | EL2809_M160 | 10 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 4 | 16416 | 1286 | 4 | EL2809_M170 | 6 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 5 | 16416 | 1286 | 5 | EL2809_M170 | 6 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 6 | 16416 | 1286 | 6 | EL2809_M170 | 7 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 7 | 16416 | 1286 | 7 | EL2809_M170 | 7 | U8 | 128
SFE6002CM | CDE FEUX ACCES INTERDIT ZLV - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | ON | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 4 | 16416 | 1248 | 0 | EL2809_M160 | 11 | U8 | 16
SFE6002CA | CDE FEUX ACCES INTERDIT ZLV - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | ON | S |  | NF |  |  | SFE6001M (ON) | [8 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 5 | 16416 | 1248 | 0 | EL2809_M160 | 11 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 10 | 16416 | 1287 | 2 | EL2809_M170 | 9 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 11 | 16416 | 1287 | 3 | EL2809_M170 | 9 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 12 | 16416 | 1287 | 4 | EL2809_M170 | 10 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 13 | 16416 | 1287 | 5 | EL2809_M170 | 10 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 14 | 16416 | 1287 | 6 | EL2809_M170 | 11 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | NOT | [10 empty] | 12932 | 15 | 16416 | 1287 | 7 | EL2809_M170 | 11 | U8 | 128
SFE6003CM | CDE FEUX PRESENCE LANCEUR ZLV - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 6 | 16416 | 1248 | 0 | EL2809_M160 | 12 | U8 | 64
SFE6003CA | CDE FEUX PRESENCE LANCEUR ZLV - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S |  | NF |  |  | SFE6001M (ON); SFE6002M (ON) |  |  |  |  | OR |  |  |  | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 7 | 16416 | 1248 | 0 | EL2809_M160 | 12 | U8 | 128
SFE6004CM | CDE FEUX ACCES LIBRE ZLV - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 8 | 16416 | 1249 | 0 | EL2809_M160 | 13 | U8 | 1
SFE6004CA | CDE FEUX ACCES LIBRE ZLV - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S |  | NF |  |  | SFE6001M (ON); SFE6002M (ON) |  |  |  |  | OR |  |  |  | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 9 | 16416 | 1249 | 0 | EL2809_M160 | 13 | U8 | 2
SST6001CO | CDE FORCAGE BARRIERE ENTREE ZLV - U8(2),OUVRIR(4) / U8(2),FERMER(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 10 | 16416 | 1249 | 0 | EL2809_M160 | 14 | U8 | 4
SST6001CF | CDE FORCAGE BARRIERE ENTREE ZLV - U8(2),OUVRIR(4) / U8(2),FERMER(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 11 | 16416 | 1249 | 0 | EL2809_M160 | 14 | U8 | 8
SST6002CO | CDE FORCAGE BARRIERE SORTIE ZLV - U8(2),OUVRIR(16) / U8(2),FERMER(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 12 | 16416 | 1249 | 0 | EL2809_M160 | 15 | U8 | 16
SST6002CF | CDE FORCAGE BARRIERE SORTIE ZLV - U8(2),OUVRIR(16) / U8(2),FERMER(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12913 | 13 | 16416 | 1249 | 0 | EL2809_M160 | 15 | U8 | 32
SCX6002CM | CDE EI LOCAL 004 COM - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 6 | 16416 | 1270 | 0 | EL2809_M166 | 7 | U8 | 64
SCX6002CA | CDE EI LOCAL 004 COM - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 7 | 16416 | 1270 | 0 | EL2809_M166 | 7 | U8 | 128
SCX6003CM | CDE EI LOCAL 007 CAT.III CU - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 8 | 16416 | 1271 | 0 | EL2809_M166 | 8 | U8 | 1
SCX6003CA | CDE EI LOCAL 007 CAT.III CU - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 9 | 16416 | 1271 | 0 | EL2809_M166 | 8 | U8 | 2
SCX6004CM | CDE EI LOCAL 008 BATTERIES CUH - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 10 | 16416 | 1271 | 0 | EL2809_M166 | 9 | U8 | 4
SCX6004CA | CDE EI LOCAL 008 BATTERIES CUH - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 11 | 16416 | 1271 | 0 | EL2809_M166 | 9 | U8 | 8
SCX6005CM | CDE EI LOCAL 009 BATTERIES CUB - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 12 | 16416 | 1271 | 0 | EL2809_M166 | 10 | U8 | 16
SCX6005CA | CDE EI LOCAL 009 BATTERIES CUB - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 13 | 16416 | 1271 | 0 | EL2809_M166 | 10 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 0 | 16416 | 1290 | 0 | EL2809_M171 | 4 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 1 | 16416 | 1290 | 1 | EL2809_M171 | 4 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 2 | 16416 | 1290 | 2 | EL2809_M171 | 5 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 3 | 16416 | 1290 | 3 | EL2809_M171 | 5 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 4 | 16416 | 1290 | 4 | EL2809_M171 | 6 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 5 | 16416 | 1290 | 5 | EL2809_M171 | 6 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 6 | 16416 | 1290 | 6 | EL2809_M171 | 7 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 7 | 16416 | 1290 | 7 | EL2809_M171 | 7 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 8 | 16416 | 1291 | 0 | EL2809_M171 | 8 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 9 | 16416 | 1291 | 1 | EL2809_M171 | 8 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 10 | 16416 | 1291 | 2 | EL2809_M171 | 9 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 11 | 16416 | 1291 | 3 | EL2809_M171 | 9 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 12 | 16416 | 1291 | 4 | EL2809_M171 | 10 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 13 | 16416 | 1291 | 5 | EL2809_M171 | 10 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 14 | 16416 | 1291 | 6 | EL2809_M171 | 11 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12934 | 15 | 16416 | 1291 | 7 | EL2809_M171 | 11 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 0 | 16416 | 1292 | 0 | EL2809_M171 | 12 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 1 | 16416 | 1292 | 1 | EL2809_M171 | 12 | U8 | 2
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 2 | 16416 | 1292 | 2 | EL2809_M171 | 13 | U8 | 4
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 3 | 16416 | 1292 | 3 | EL2809_M171 | 13 | U8 | 8
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 4 | 16416 | 1292 | 4 | EL2809_M171 | 14 | U8 | 16
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 5 | 16416 | 1292 | 5 | EL2809_M171 | 14 | U8 | 32
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 6 | 16416 | 1292 | 6 | EL2809_M171 | 15 | U8 | 64
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 7 | 16416 | 1292 | 7 | EL2809_M171 | 15 | U8 | 128
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 8 | 16416 | 1293 | 0 | EL2809_M171 | 16 | U8 | 1
SPARE | SPARE | CT | N | FIL | [28 empty] | POL | [10 empty] | 12935 | 9 | 16416 | 1293 | 1 | EL2809_M171 | 16 | U8 | 2
ZJI6103C | HIGH_Heartbeat_Physical_Channel | CT | N | INT | 0 | [14 empty] | NO | [12 empty] | NOT |  |  |  |  | NEW | [5 empty] | 12971 | 0 | 16416 | 1364 | 0 | EL2809_M187 | 1 | BIT
ZJO6103C | MODE_OUT_Operating_Mode_Physical_Channel | CT | N | INT | 0 | [14 empty] | NO | [12 empty] | NOT |  |  |  |  | NEW | [5 empty] | 12971 | 1 | 16416 | 1364 | 0 | EL2809_M187 | 2 | BIT
SCX6001CM | CDE EI LOCAL 013 ET 002 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 14 | 16416 | 1271 | 0 | EL2809_M166 | 11 | U8 | 64
SCX6001CA | CDE EI LOCAL 013 ET 002 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12924 | 15 | 16416 | 1271 | 0 | EL2809_M166 | 11 | U8 | 128
SCX6006CM | CDE EI LOCAL 101 BAIES CU - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 0 | 16416 | 1272 | 0 | EL2809_M166 | 12 | U8 | 1
SCX6006CA | CDE EI LOCAL 101 BAIES CU - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 1 | 16416 | 1272 | 0 | EL2809_M166 | 12 | U8 | 2
SCX6107CM | CDE EI LOCAL 103 BCV/CCS - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 0 | 16416 | 1252 | 0 | EL2809_M161 | 9 | U8 | 1
SCX6107CA | CDE EI LOCAL 103 BCV/CCS - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 1 | 16416 | 1252 | 0 | EL2809_M161 | 9 | U8 | 2
SCX6108CM | CDE EI LOCAL 111 BATT. CAT.III - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 2 | 16416 | 1252 | 0 | EL2809_M161 | 10 | U8 | 4
SCX6108CA | CDE EI LOCAL 111 BATT. CAT.III - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 3 | 16416 | 1252 | 0 | EL2809_M161 | 10 | U8 | 8
SCX6109CM | CDE EI LOCAL 112 BATT. CAT.III - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 4 | 16416 | 1252 | 0 | EL2809_M161 | 11 | U8 | 16
SCX6109CA | CDE EI LOCAL 112 BATT. CAT.III - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 5 | 16416 | 1252 | 0 | EL2809_M161 | 11 | U8 | 32
SCX6010CM | CDE EI LOCAL 113 UPS - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 14 | 16416 | 1273 | 0 | EL2809_M167 | 3 | U8 | 64
SCX6010CA | CDE EI LOCAL 113 UPS - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 15 | 16416 | 1273 | 0 | EL2809_M167 | 3 | U8 | 128
SCX6111CM | CDE EI LOCAL 115 TGBT - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 8 | 16416 | 1253 | 0 | EL2809_M161 | 13 | U8 | 1
SCX6111CA | CDE EI LOCAL 115 TGBT - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 9 | 16416 | 1253 | 0 | EL2809_M161 | 13 | U8 | 2
SCX6012CM | CDE EI LOCAL 116 HT - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12926 | 2 | 16416 | 1274 | 0 | EL2809_M167 | 5 | U8 | 4
SCX6012CA | CDE EI LOCAL 116 HT - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12926 | 3 | 16416 | 1274 | 0 | EL2809_M167 | 5 | U8 | 8
SCX6013CM | CDE EI LOCAL 126 SCC CLIM - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12926 | 4 | 16416 | 1274 | 0 | EL2809_M167 | 6 | U8 | 16
SCX6013CA | CDE EI LOCAL 126 SCC CLIM - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12926 | 5 | 16416 | 1274 | 0 | EL2809_M167 | 6 | U8 | 32
EEL6001CM | CMDE ECLAIRAGE LANCEUR CONF.A - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12915 | 14 | 16416 | 1253 | 0 | EL2809_M161 | 16 | U8 | 64
EEL6001CA | CMDE ECLAIRAGE LANCEUR CONF.A - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12915 | 15 | 16416 | 1253 | 0 | EL2809_M161 | 16 | U8 | 128
EEL6002CM | CMDE ECLAIRAGE LANCEUR CONF.B - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12917 | 4 | 16416 | 1256 | 0 | EL2809_M162 | 11 | U8 | 16
EEL6002CA | CMDE ECLAIRAGE LANCEUR CONF.B - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12917 | 5 | 16416 | 1256 | 0 | EL2809_M162 | 11 | U8 | 32
EEL6003CM | CMDE ECLAIRAGE LANCEUR CONF.C - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12917 | 6 | 16416 | 1256 | 0 | EL2809_M162 | 12 | U8 | 64
EEL6003CA | CMDE ECLAIRAGE LANCEUR CONF.C - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12917 | 7 | 16416 | 1256 | 0 | EL2809_M162 | 12 | U8 | 128
EEL6004CM | CMDE ECLAIRAGE LANCEUR CONF.D - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12917 | 8 | 16416 | 1257 | 0 | EL2809_M162 | 13 | U8 | 1
EEL6004CA | CMDE ECLAIRAGE LANCEUR CONF.D - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E66 | Energy TGBT et UPS (E) | CCS | [5 empty] | 12917 | 9 | 16416 | 1257 | 0 | EL2809_M162 | 13 | U8 | 2
VVU6106CM | PASSAGE EN CLIM INTERNE LOCAL 106 REPLI - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC12 | HVAC | CCS | [5 empty] | 12918 | 4 | 16416 | 1258 | 0 | EL2809_M163 | 3 | U8 | 16
VVU6106CA | PASSAGE EN CLIM INTERNE LOCAL 106 REPLI - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC12 | HVAC | CCS | [5 empty] | 12918 | 5 | 16416 | 1258 | 0 | EL2809_M163 | 3 | U8 | 32
SCE6001CM | CMDE ALERTE EVACUATION ZLV PULSE | CT | O | FIL | 1 | S | [11 empty] | OFF | S |  | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12918 | 6 | 16416 | 1258 | 0 | EL2809_M163 | 4 | U8 | 64
SCE6011CM | CMDE REARMEMENT ALERTE EVACUATION ZLV PULSE | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12918 | 7 | 16416 | 1258 | 0 | EL2809_M163 | 5 | U8 | 128
OPP6301CM | CDE AUTORISATION POMPE OPP6301 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF |  |  |  | OPP6301L(OFF) | [7 empty] | NOT |  |  | MG65;VG04 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12918 | 8 | 16416 | 1259 | 0 | EL2809_M163 | 6 | U8 | 1
OPP6301CA | CDE AUTORISATION POMPE OPP6301 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF |  |  |  | OPP6301L(OFF) | [7 empty] | NOT |  |  | MG65;VG04 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12918 | 9 | 16416 | 1259 | 0 | EL2809_M163 | 6 | U8 | 2
OPP6302CM | CDE AUTORISATION POMPE OPP6302 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF |  |  |  | OPP6302L(OFF) | [7 empty] | NOT |  |  | MG65;VG04 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 2 | 16416 | 1260 | 0 | EL2809_M163 | 11 | U8 | 4
OPP6302CA | CDE AUTORISATION POMPE OPP6302 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF |  |  |  | OPP6302L(OFF) | [7 empty] | NOT |  |  | MG65;VG04 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 3 | 16416 | 1260 | 0 | EL2809_M163 | 11 | U8 | 8
NPP6001CM | CDE POMPE H2O2 ZLV - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG67;MG69 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12919 | 4 | 16416 | 1260 | 0 | EL2809_M163 | 12 | U8 | 16
NPP6001CA | CDE POMPE H2O2 ZLV - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG67;MG69 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12919 | 5 | 16416 | 1260 | 0 | EL2809_M163 | 12 | U8 | 32
OVP6312CF | CDE VANNE PILOTEE PIED DE MAT RINCAGE ZLV - U8(2),FERMER(64) / U8(2),OUVRIR(128) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NO | [11 empty] | NOT |  |  | MG64;VG03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 6 | 16416 | 1260 | 0 | EL2809_M163 | 13 | U8 | 64
OVP6312CO | CDE VANNE PILOTEE PIED DE MAT RINCAGE ZLV - U8(2),FERMER(64) / U8(2),OUVRIR(128) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NO | [11 empty] | NOT |  |  | MG64;VG03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 7 | 16416 | 1260 | 0 | EL2809_M163 | 13 | U8 | 128
OVP6313CO | CDE VANNE PILOTEE RINCAGE TABLE PALETTE ZLV - U8(2),OUVRIR(1) / U8(2),FERMER(2) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG64;VG03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 8 | 16416 | 1261 | 0 | EL2809_M163 | 14 | U8 | 1
OVP6313CF | CDE VANNE PILOTEE RINCAGE TABLE PALETTE ZLV - U8(2),OUVRIR(1) / U8(2),FERMER(2) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG64;VG03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 9 | 16416 | 1261 | 0 | EL2809_M163 | 14 | U8 | 2
OVP6314CO | CDE VANNE PILOTEE RINCAGE MAT ZLV - U8(2),OUVRIR(4) / U8(2),FERMER(8) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG64;VG03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 10 | 16416 | 1261 | 0 | EL2809_M163 | 15 | U8 | 4
OVP6314CF | CDE VANNE PILOTEE RINCAGE MAT ZLV - U8(2),OUVRIR(4) / U8(2),FERMER(8) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG64;VG03 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 12919 | 11 | 16416 | 1261 | 0 | EL2809_M163 | 15 | U8 | 8
VVU6004CO | CDE DEPOLLUTION LOCAL 004 COM - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12919 | 12 | 16416 | 1261 | 0 | EL2809_M163 | 16 | U8 | 16
VVU6004CF | CDE DEPOLLUTION LOCAL 004 COM - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12919 | 13 | 16416 | 1261 | 0 | EL2809_M163 | 16 | U8 | 32
VVU6007CO | CDE DEPOLLUTION LOCAL 007 CAT.III CU - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12919 | 14 | 16416 | 1261 | 0 | EL2809_M164 | 1 | U8 | 64
VVU6007CF | CDE DEPOLLUTION LOCAL 007 CAT.III CU - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12919 | 15 | 16416 | 1261 | 0 | EL2809_M164 | 1 | U8 | 128
VVU6008CO | CDE DEPOLLUTION LOCAL 008 BAT CUH - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 0 | 16416 | 1262 | 0 | EL2809_M164 | 2 | U8 | 1
VVU6008CF | CDE DEPOLLUTION LOCAL 008 BAT CUH - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 1 | 16416 | 1262 | 0 | EL2809_M164 | 2 | U8 | 2
VVU6009CO | CDE DEPOLLUTION LOCAL 009 BAT CUB - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 2 | 16416 | 1262 | 0 | EL2809_M164 | 3 | U8 | 4
VVU6009CF | CDE DEPOLLUTION LOCAL 009 BAT CUB - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 3 | 16416 | 1262 | 0 | EL2809_M164 | 3 | U8 | 8
VVU6101CO | CDE DEPOLLUTION LOCAL 101 BAIES CU - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 4 | 16416 | 1262 | 0 | EL2809_M164 | 4 | U8 | 16
VVU6101CF | CDE DEPOLLUTION LOCAL 101 BAIES CU - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 5 | 16416 | 1262 | 0 | EL2809_M164 | 4 | U8 | 32
VVU6103CO | CDE DEPOLLUTION LOCAL 103 CCV CCS - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 6 | 16416 | 1262 | 0 | EL2809_M164 | 5 | U8 | 64
VVU6103CF | CDE DEPOLLUTION LOCAL 103 CCV CCS - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 7 | 16416 | 1262 | 0 | EL2809_M164 | 5 | U8 | 128
VVU6111CO | CDE DEPOLLUTION LOCAL 111 BATT - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 12 | 16416 | 1263 | 0 | EL2809_M164 | 8 | U8 | 16
VVU6111CF | CDE DEPOLLUTION LOCAL 111 BATT - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 13 | 16416 | 1263 | 0 | EL2809_M164 | 8 | U8 | 32
VVU6112CO | CDE DEPOLLUTION LOCAL 112 BATT - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 14 | 16416 | 1263 | 0 | EL2809_M164 | 9 | U8 | 64
VVU6112CF | CDE DEPOLLUTION LOCAL 112 BATT - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12920 | 15 | 16416 | 1263 | 0 | EL2809_M164 | 9 | U8 | 128
VVU6113CO | CDE DEPOLLUTION LOCAL 113 CAT.III - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 6 | 16416 | 1264 | 0 | EL2809_M164 | 13 | U8 | 64
VVU6113CF | CDE DEPOLLUTION LOCAL 113 CAT.III - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 7 | 16416 | 1264 | 0 | EL2809_M164 | 13 | U8 | 128
VVU6115CO | CDE DEPOLLUTION LOCAL 115 TGBT - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 8 | 16416 | 1265 | 0 | EL2809_M164 | 14 | U8 | 1
VVU6115CF | CDE DEPOLLUTION LOCAL 115 TGBT - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 9 | 16416 | 1265 | 0 | EL2809_M164 | 14 | U8 | 2
VVU6116CO | CDE DEPOLLUTION LOCAL 116 HT - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 10 | 16416 | 1265 | 0 | EL2809_M164 | 15 | U8 | 4
VVU6116CF | CDE DEPOLLUTION LOCAL 116 HT - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 11 | 16416 | 1265 | 0 | EL2809_M164 | 15 | U8 | 8
VVU6013CO | CDE DEPOLLUTION LOC 013 ET 002 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 14 | 16416 | 1265 | 0 | EL2809_M165 | 1 | U8 | 64
VVU6013CF | CDE DEPOLLUTION LOC 013 ET 002 - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12921 | 15 | 16416 | 1265 | 0 | EL2809_M165 | 1 | U8 | 128
VRU6004CF | CMDE VOLETS EXTIN. N2 LOC.004 COM - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6002GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 0 | 16416 | 1266 | 0 | EL2809_M165 | 2 | U8 | 2
VRU6004CO | CMDE VOLETS EXTIN. N2 LOC.004 COM - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 1 | 16416 | 1266 | 0 | EL2809_M165 | 2 | U8 | 1
VRU6007CF | CMDE VOLETS EXTIN. N2 LOC.007 CU - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6003GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 2 | 16416 | 1266 | 0 | EL2809_M165 | 3 | U8 | 8
VRU6007CO | CMDE VOLETS EXTIN. N2 LOC.007 CU - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 3 | 16416 | 1266 | 0 | EL2809_M165 | 3 | U8 | 4
VRU6008CF | CDE VOLETS EXTINCTION N2 LOC.008 BAT - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6004GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 4 | 16416 | 1266 | 0 | EL2809_M165 | 4 | U8 | 32
VRU6008CO | CDE VOLETS EXTINCTION N2 LOC.008 BAT - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 5 | 16416 | 1266 | 0 | EL2809_M165 | 4 | U8 | 16
VRU6009CF | CDE VOLETS EXTINCTION N2 LOC.009 BAT - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6005GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 6 | 16416 | 1266 | 0 | EL2809_M165 | 5 | U8 | 128
VRU6009CO | CDE VOLETS EXTINCTION N2 LOC.009 BAT - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 7 | 16416 | 1266 | 0 | EL2809_M165 | 5 | U8 | 64
VRU6101CF | CDE VOLETS EXTINCTION N2 LOC.101 B CU - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6006GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 8 | 16416 | 1267 | 0 | EL2809_M165 | 6 | U8 | 2
VRU6101CO | CDE VOLETS EXTINCTION N2 LOC.101 B CU - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 9 | 16416 | 1267 | 0 | EL2809_M165 | 6 | U8 | 1
VRU6103CF | CDE VOLETS EXTINCTION N2 LOC.103 SCC - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6007GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 10 | 16416 | 1267 | 0 | EL2809_M165 | 7 | U8 | 8
VRU6103CO | CDE VOLETS EXTINCTION N2 LOC.103 SCC - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 11 | 16416 | 1267 | 0 | EL2809_M165 | 7 | U8 | 4
VRU6111CF | CDE VOLETS EXTINCTION N2 LOC.111 BATT - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6008GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 12 | 16416 | 1267 | 0 | EL2809_M165 | 8 | U8 | 32
VRU6111CO | CDE VOLETS EXTINCTION N2 LOC.111 BATT - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 13 | 16416 | 1267 | 0 | EL2809_M165 | 8 | U8 | 16
VRU6112CF | CDE VOLETS EXTINCTION N2 LOC.112 BATT - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6009GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 14 | 16416 | 1267 | 0 | EL2809_M165 | 9 | U8 | 128
VRU6112CO | CDE VOLETS EXTINCTION N2 LOC.112 BATT - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12922 | 15 | 16416 | 1267 | 0 | EL2809_M165 | 9 | U8 | 64
VRU6113CF | CDE VOLETS EXTINCTION N2 LOC.113 CIII - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6010GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 0 | 16416 | 1268 | 0 | EL2809_M165 | 10 | U8 | 2
VRU6113CO | CDE VOLETS EXTINCTION N2 LOC.113 CIII - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 1 | 16416 | 1268 | 0 | EL2809_M165 | 10 | U8 | 1
VRU6115CF | CDE VOLETS EXTINCTION N2 LOC.115 TGBT - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6011GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 2 | 16416 | 1268 | 0 | EL2809_M165 | 11 | U8 | 8
VRU6115CO | CDE VOLETS EXTINCTION N2 LOC.115 TGBT - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 3 | 16416 | 1268 | 0 | EL2809_M165 | 11 | U8 | 4
VRU6116CF | CDE VOLETS EXTINCTION N2 LOC.116 HT - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6012GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 4 | 16416 | 1268 | 0 | EL2809_M165 | 12 | U8 | 32
VRU6116CO | CDE VOLETS EXTINCTION N2 LOC.116 HT - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 5 | 16416 | 1268 | 0 | EL2809_M165 | 12 | U8 | 16
VRU6013CF | CDE VOLETS EXTINCTION N2 LOC.013 ET 02 - U8(2),FERMER(64) / U8(2),OUVRIR(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6001GE (ON) | [8 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 14 | 16416 | 1269 | 0 | EL2809_M166 | 1 | U8 | 64
VRU6013CO | CDE VOLETS EXTINCTION N2 LOC.013 ET 02 - U8(2),FERMER(64) / U8(2),OUVRIR(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC11 | HVAC | CCS | [5 empty] | 12923 | 15 | 16416 | 1269 | 0 | EL2809_M166 | 1 | U8 | 128
SSP6001CCQ | MARCHE ALERTE REPLI SIRENE ZLV | CT | O | FIL | 1 | S | [11 empty] | OFF | S |  | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12924 | 0 | 16416 | 1270 | 0 | EL2809_M166 | 2 | U8 | 1
SSP6001CMQ | MARCHE ALERTE EVACUATION SIRENE ZLV | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12924 | 1 | 16416 | 1270 | 0 | EL2809_M166 | 3 | U8 | 2
SSP6001CAQ | ARRET SIRENE ZLV | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12924 | 2 | 16416 | 1270 | 0 | EL2809_M166 | 4 | U8 | 4
SCE6002CM | CMDE MARCHE ALERTE REPLI ZLV PULSE | CT | O | FIL | 1 | S | [11 empty] | OFF | S |  | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12924 | 3 | 16416 | 1270 | 0 | EL2809_M166 | 5 | U8 | 8
SCE6012CM | CMDE ARRET ALERTE REPLI ZLV PULSE | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | 5 | [10 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12924 | 4 | 16416 | 1270 | 0 | EL2809_M166 | 6 | U8 | 16
SCX6102CM | CDE EI LOCAL 004 COMMUNICATION - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12913 | 14 | 16416 | 1249 | 0 | EL2809_M160 | 16 | U8 | 64
SCX6102CA | CDE EI LOCAL 004 COMMUNICATION - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12913 | 15 | 16416 | 1249 | 0 | EL2809_M160 | 16 | U8 | 128
SCX6103CM | CDE EI LOCAL 007 CAT.III CU - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 6 | 16416 | 1250 | 0 | EL2809_M161 | 4 | U8 | 64
SCX6103CA | CDE EI LOCAL 007 CAT.III CU - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 7 | 16416 | 1250 | 0 | EL2809_M161 | 4 | U8 | 128
SCX6104CM | CDE EI LOCAL 008 BATTERIES CUH - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 8 | 16416 | 1251 | 0 | EL2809_M161 | 5 | U8 | 1
SCX6104CA | CDE EI LOCAL 008 BATTERIES CUH - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 9 | 16416 | 1251 | 0 | EL2809_M161 | 5 | U8 | 2
SCX6105CM | CDE EI LOCAL 009 BATTERIES CUB - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 10 | 16416 | 1251 | 0 | EL2809_M161 | 6 | U8 | 4
SCX6105CA | CDE EI LOCAL 009 BATTERIES CUB - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI68 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 11 | 16416 | 1251 | 0 | EL2809_M161 | 6 | U8 | 8
SCX6101CM | CDE EI LOCAL 013 ET 002 - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 12 | 16416 | 1251 | 0 | EL2809_M161 | 7 | U8 | 16
SCX6101CA | CDE EI LOCAL 013 ET 002 - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI71 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 13 | 16416 | 1251 | 0 | EL2809_M161 | 7 | U8 | 32
SCX6106CM | CDE EI LOCAL 101 BAIES CU - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 14 | 16416 | 1251 | 0 | EL2809_M161 | 8 | U8 | 64
SCX6106CA | CDE EI LOCAL 101 BAIES CU - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12914 | 15 | 16416 | 1251 | 0 | EL2809_M161 | 8 | U8 | 128
SCX6007CM | CDE EI LOCAL 103 BCV/CCS - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 2 | 16416 | 1272 | 0 | EL2809_M166 | 13 | U8 | 4
SCX6007CA | CDE EI LOCAL 103 BCV/CCS - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 3 | 16416 | 1272 | 0 | EL2809_M166 | 13 | U8 | 8
SCX6008CM | CDE EI LOCAL 111 BATT. CAT.III - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 4 | 16416 | 1272 | 0 | EL2809_M166 | 14 | U8 | 16
SCX6008CA | CDE EI LOCAL 111 BATT. CAT.III - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI66 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 5 | 16416 | 1272 | 0 | EL2809_M166 | 14 | U8 | 32
SCX6009CM | CDE EI LOCAL 112 BATT. CAT.III - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 6 | 16416 | 1272 | 0 | EL2809_M166 | 15 | U8 | 64
SCX6009CA | CDE EI LOCAL 112 BATT. CAT.III - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12925 | 7 | 16416 | 1272 | 0 | EL2809_M166 | 15 | U8 | 128
SCX6110CM | CDE EI LOCAL 113 UPS - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 6 | 16416 | 1252 | 0 | EL2809_M161 | 12 | U8 | 64
SPASMA1130 | SPARE SER MA 1130 (SOR6101) | MA | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 326 | NA | 12444 | NA | 16416 | 310 | 0 | EL6021_M176 |  | U16 |  | Eliminazione del segnale SOR6101 e aggiunta spare SPASMA1130
SPASMA1131 | SPARE SER MA 1131 (SOR6201) | MA | N | RES | 1 | [27 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 327 | NA | 12445 | NA | 16416 | 312 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SCX6110CA | CDE EI LOCAL 113 UPS - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 7 | 16416 | 1252 | 0 | EL2809_M161 | 12 | U8 | 128
SCX6011CM | CDE EI LOCAL 115 TGBT - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12926 | 0 | 16416 | 1274 | 0 | EL2809_M167 | 4 | U8 | 1
SPASMA1132 | SPARE SER MA 1132 (SOR6103) | MA | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 330 | NA | 12448 | NA | 16416 | 318 | 0 | EL6021_M176 |  | U16 |  | Eliminazione del segnale SOR6101 e aggiunta spare SPASMA1132
SCX6011CA | CDE EI LOCAL 115 TGBT - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12926 | 1 | 16416 | 1274 | 0 | EL2809_M167 | 4 | U8 | 2
SCX6112CM | CDE EI LOCAL 116 HT - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 10 | 16416 | 1253 | 0 | EL2809_M161 | 14 | U8 | 4
SCX6112CA | CDE EI LOCAL 116 HT - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 11 | 16416 | 1253 | 0 | EL2809_M161 | 14 | U8 | 8
SCX6113CM | CDE EI LOCAL 126 SCC CLIM - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 12 | 16416 | 1253 | 0 | EL2809_M161 | 15 | U8 | 16
SPASMA1135 | SPARE SER MA 1135 (SOR6205) | MA | N | RES | 1 | [27 empty] | NOT | 1000 |  |  |  | CCS | 1 |  |  | 335 | NA | 12453 | NA | 16416 | 328 | 0 | EL6021_M176 |  | U16 |  | Eliminazione del segnale SOR6101 e aggiunta spare SPASMA1133
SCX6113CA | CDE EI LOCAL 126 SCC CLIM - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI67 | Extinction Incendie (EI) | CCS | [5 empty] | 12915 | 13 | 16416 | 1253 | 0 | EL2809_M161 | 15 | U8 | 32
SFE6001CM | CDE FEUX EVACUATION ZLV - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12926 | 6 | 16416 | 1274 | 0 | EL2809_M167 | 7 | U8 | 64
SFE6001CA | CDE FEUX EVACUATION ZLV - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S |  | NF |  |  | SFE6002M (ON) | [8 empty] | NOT |  |  | MG71 | Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12926 | 7 | 16416 | 1274 | 0 | EL2809_M167 | 7 | U8 | 128
SZP6014CM | CDE ACTIVATION SONO ALERTE TOXIQUE VEGA | CT | O | FIL | 1 | S | [11 empty] | OFF | S |  | NF | [7 empty] | OR |  |  |  | NOT |  |  | DG60 | Detection Gaz (DG) | CCS | [5 empty] | 12926 | 8 | 16416 | 1275 | 0 | EL2809_M167 | 8 | U8 | 1
SZP6014CA | CDE DESACTIVATION SONO ALERTE TOXIQUE VEGA | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | DG60 | Detection Gaz (DG) | CCS | [5 empty] | 12926 | 9 | 16416 | 1275 | 0 | EL2809_M167 | 8 | U8 | 2
SCX6121CM | CDE EI NIV 18.400 LOCAL 101 ENERGIE - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12930 | 10 | 16416 | 1283 | 0 | EL2809_M169 | 9 | U8 | 4
SCX6121CA | CDE EI NIV 18.400 LOCAL 101 ENERGIE - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12930 | 11 | 16416 | 1283 | 0 | EL2809_M169 | 9 | U8 | 8
SPASMA1039 | SPARE SER 1039 | MA | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 107 | NA | 12623 | NA | 16416 | 668 | 0 | EL6021_M177 |  | UINT
SPASMA1040 | SPARE SER 1040 | MA | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 108 | NA | 12624 | NA | 16416 | 670 | 0 | EL6021_M177 |  | UINT
SCX6122CM | CDE EI NIV 21.200 SAUVEGARDE CFS - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12930 | 12 | 16416 | 1283 | 0 | EL2809_M169 | 10 | U8 | 16
SPASMA1041 | SPARE SER 1041 | MA | N | RES | [28 empty] | NOT | 10000 |  |  |  |  | 3 |  |  | 110 |  | 12626 | 0 | 16416 | 674 | 0 | EL6021_M177
SPASMA1042 | SPARE SER 1042 | MA | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 111 | NA | 12627 | NA | 16416 | 676 | 0 | EL6021_M177 |  | U16 |  | Eliminazione del segnale SOR6001 (CL8 Modification) | DEL
SPASMA1129 | SPARE SER 1129 | MA | N | RES | 1 | [27 empty] | NOT | 1000 | [7 empty] | 112 | NA | 12628 | NA | 16416 | 678 | 0 | EL6021_M177 |  | U16 |  | Eliminazione del segnale SOR6002 (CL8 Modification) | DEL
SCX6122CA | CDE EI NIV 21.200 SAUVEGARDE CFS - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12930 | 13 | 16416 | 1283 | 0 | EL2809_M169 | 10 | U8 | 32
SCX6123CM | CDE EI NIV 29.200 BCV/INTF - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12930 | 14 | 16416 | 1283 | 0 | EL2809_M169 | 11 | U8 | 64
SCX6123CA | CDE EI NIV 29.200 BCV/INTF - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12930 | 15 | 16416 | 1283 | 0 | EL2809_M169 | 11 | U8 | 128
OVP6301CO | CDE RINCAGE LOCAL UDMH PORT. VEGA - U8(2),OUVRIR(1) / U8(2),FERMER(2) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 0 | 16416 | 1284 | 0 | EL2809_M169 | 12 | U8 | 1
OVP6301CF | CDE RINCAGE LOCAL UDMH PORT. VEGA - U8(2),OUVRIR(1) / U8(2),FERMER(2) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 1 | 16416 | 1284 | 0 | EL2809_M169 | 12 | U8 | 2
OVP6302CO | CDE RINCAGE LOCAL UDMH PORT. VEGA - U8(2),OUVRIR(4) / U8(2),FERMER(8) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 2 | 16416 | 1284 | 0 | EL2809_M169 | 13 | U8 | 4
OVP6302CF | CDE RINCAGE LOCAL UDMH PORT. VEGA - U8(2),OUVRIR(4) / U8(2),FERMER(8) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 3 | 16416 | 1284 | 0 | EL2809_M169 | 13 | U8 | 8
OVP6303CO | CDE DELUGE LANCEUR VEGA - U8(2),OUVRIR(16) / U8(2),FERMER(32) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 4 | 16416 | 1284 | 0 | EL2809_M169 | 14 | U8 | 16
OVP6303CF | CDE DELUGE LANCEUR VEGA - U8(2),OUVRIR(16) / U8(2),FERMER(32) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 5 | 16416 | 1284 | 0 | EL2809_M169 | 14 | U8 | 32
OVP6304CO | CDE DELUGE LANCEUR VEGA - U8(2),OUVRIR(64) / U8(2),FERMER(128) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 6 | 16416 | 1284 | 0 | EL2809_M169 | 15 | U8 | 64
OVP6304CF | CDE DELUGE LANCEUR VEGA - U8(2),OUVRIR(64) / U8(2),FERMER(128) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NF | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 7 | 16416 | 1284 | 0 | EL2809_M169 | 15 | U8 | 128
OVP6305CF | CDE DELUGE LANCEUR VEGA - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | O | FIL | 1 | F | [11 empty] | OFF | F | NO | NO | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 8 | 16416 | 1285 | 0 | EL2809_M169 | 16 | U8 | 1
OVP6305CO | CDE DELUGE LANCEUR VEGA - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | FIL | 1 | F | [11 empty] | OFF | F | NO | NO | [11 empty] | NOT |  |  | MG63;VG02 | Process Fluide et Energie VEGA (VG); Moyens Generaux VEGA (MG) | CCS | [5 empty] | 12931 | 9 | 16416 | 1285 | 0 | EL2809_M169 | 16 | U8 | 2
VVU6908CM | CDE DEPOLL.HALL INTEGR.PORTIQUE VEGA - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12931 | 10 | 16416 | 1285 | 0 | EL2809_M170 | 1 | U8 | 4
VVU6908CA | CDE DEPOLL.HALL INTEGR.PORTIQUE VEGA - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12931 | 11 | 16416 | 1285 | 0 | EL2809_M170 | 1 | U8 | 8
VVU6986CM | CDE DEPOLL.N2O4 LOC.701 PORTIQUE VEGA - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12931 | 12 | 16416 | 1285 | 0 | EL2809_M170 | 2 | U8 | 16
VVU6986CA | CDE DEPOLL.N2O4 LOC.701 PORTIQUE VEGA - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12931 | 13 | 16416 | 1285 | 0 | EL2809_M170 | 2 | U8 | 32
VVU6987CM | CDE DEPOLL.UDMH LOC.601 PORTIQUE VEGA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12931 | 14 | 16416 | 1285 | 0 | EL2809_M170 | 3 | U8 | 64
VVU6987CA | CDE DEPOLL.UDMH LOC.601 PORTIQUE VEGA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12931 | 15 | 16416 | 1285 | 0 | EL2809_M170 | 3 | U8 | 128
VVU6981CO | CDE DEPOLLUTION PORTIQUE 101 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12932 | 0 | 16416 | 1286 | 0 | EL2809_M170 | 4 | U8 | 1
VVU6981CF | CDE DEPOLLUTION PORTIQUE 101 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12932 | 1 | 16416 | 1286 | 0 | EL2809_M170 | 4 | U8 | 2
VVU6982CO | CDE DEPOLLUTION PORTIQUE 201 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12932 | 2 | 16416 | 1286 | 0 | EL2809_M170 | 5 | U8 | 4
VVU6982CF | CDE DEPOLLUTION PORTIQUE 201 - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12932 | 3 | 16416 | 1286 | 0 | EL2809_M170 | 5 | U8 | 8
VVU6983CO | CDE DEPOLLUTION PORTIQUE 502 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12932 | 8 | 16416 | 1287 | 0 | EL2809_M170 | 8 | U8 | 1
VVU6983CF | CDE DEPOLLUTION PORTIQUE 502 - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12932 | 9 | 16416 | 1287 | 0 | EL2809_M170 | 8 | U8 | 2
ZZW6000 | WATCHDOG COUNTER WIRE API | MA | N | RES | 1 | A |  |  |  |  | 0 | 65535 | [20 empty] | POL | 6000 |  | VG10 | Process Fluide et Energie VEGA (VG) | NEW | 3 |  |  | 149 | NA | 12665 | NA | 16416 | 752 | 0 | EL6021_M177 |  | U16 |  | WATCHDOG WIRE PLC
EIR6021I1 | TD CAT II PORTIQUE 1602-101-21 Phase currents I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 902 | 0 | 14512 | 0 | 16416 | 4446 | 0 | EL6021_M177 |  | FLOAT
EIR6021I2 | TD CAT II PORTIQUE 1602-101-21 Phase currents I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 904 | 0 | 14514 | 0 | 16416 | 4450 | 0 | EL6021_M177 |  | FLOAT
EIR6021I3 | TD CAT II PORTIQUE 1602-101-21 Phase currents I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 906 | 0 | 14516 | 0 | 16416 | 4454 | 0 | EL6021_M177 |  | FLOAT
EIR6021 | TD CAT II PORTIQUE 1602-101-21 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 908 | 0 | 14518 | 0 | 16416 | 4458 | 0 | EL6021_M177 |  | FLOAT
EUR602112 | TD CAT II PORTIQUE 1602-101-21 line to line voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 910 | 0 | 14520 | 0 | 16416 | 4462 | 0 | EL6021_M177 |  | FLOAT
EUR602123 | TD CAT II PORTIQUE 1602-101-21 line to line voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 912 | 0 | 14522 | 0 | 16416 | 4466 | 0 | EL6021_M177 |  | FLOAT
EUR602131 | TD CAT II PORTIQUE 1602-101-21 line to line voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 914 | 0 | 14524 | 0 | 16416 | 4470 | 0 | EL6021_M177 |  | FLOAT
EUR6021V1 | TD CAT II PORTIQUE 1602-101-21 Phase voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 916 | 0 | 14526 | 0 | 16416 | 4474 | 0 | EL6021_M177 |  | FLOAT
EUR6021V2 | TD CAT II PORTIQUE 1602-101-21 Phase voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 918 | 0 | 14528 | 0 | 16416 | 4478 | 0 | EL6021_M177 |  | FLOAT
EUR6021V3 | TD CAT II PORTIQUE 1602-101-21 Phase voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 920 | 0 | 14530 | 0 | 16416 | 4482 | 0 | EL6021_M177 |  | FLOAT
EWR6021PF | TD CAT II PORTIQUE 1602-101-21 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 922 | 0 | 14532 | 0 | 16416 | 4486 | 0 | EL6021_M177 |  | FLOAT
EFR6021 | TD CAT II PORTIQUE 1602-101-21 Frequency (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D121 | TD CAT II 1602 101 21 (E67) | Energie TD | ENE_MC | 3 |  |  | 924 | 0 | 14534 | 0 | 16416 | 4490 | 0 | EL6021_M177 |  | FLOAT
EIR6020I1 | TD CAT II PORTIQUE 1602-101-20 Phase currents I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 928 | 0 | 14538 | 0 | 16416 | 4498 | 0 | EL6021_M177 |  | FLOAT
EIR6020I2 | TD CAT II PORTIQUE 1602-101-20 Phase currents I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 930 | 0 | 14540 | 0 | 16416 | 4502 | 0 | EL6021_M177 |  | FLOAT
EIR6020I3 | TD CAT II PORTIQUE 1602-101-20 Phase currents I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 932 | 0 | 14542 | 0 | 16416 | 4506 | 0 | EL6021_M177 |  | FLOAT
EIR6020 | TD CAT II PORTIQUE 1602-101-20 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 934 | 0 | 14544 | 0 | 16416 | 4510 | 0 | EL6021_M177 |  | FLOAT
EUR602012 | TD CAT II PORTIQUE 1602-101-20 line to line voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 936 | 0 | 14546 | 0 | 16416 | 4514 | 0 | EL6021_M177 |  | FLOAT
EUR602023 | TD CAT II PORTIQUE 1602-101-20 line to line voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 938 | 0 | 14548 | 0 | 16416 | 4518 | 0 | EL6021_M177 |  | FLOAT
EUR602031 | TD CAT II PORTIQUE 1602-101-20 line to line voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 940 | 0 | 14550 | 0 | 16416 | 4522 | 0 | EL6021_M177 |  | FLOAT
EUR6020V1 | TD CAT II PORTIQUE 1602-101-20 Phase voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 942 | 0 | 14552 | 0 | 16416 | 4526 | 0 | EL6021_M177 |  | FLOAT
EUR6020V2 | TD CAT II PORTIQUE 1602-101-20 Phase voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 944 | 0 | 14554 | 0 | 16416 | 4530 | 0 | EL6021_M177 |  | FLOAT
EUR6020V3 | TD CAT II PORTIQUE 1602-101-20 Phase voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 946 | 0 | 14556 | 0 | 16416 | 4534 | 0 | EL6021_M177 |  | FLOAT
EWR6020PF | TD CAT II PORTIQUE 1602-101-20 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 948 | 0 | 14558 | 0 | 16416 | 4538 | 0 | EL6021_M177 |  | FLOAT
EFR6020 | TD CAT II PORTIQUE 1602-101-20 Frequency (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D120 | TD CAT II 1602 101 20 (E67) | Energie TD | ENE_MC | 3 |  |  | 950 | 0 | 14560 | 0 | 16416 | 4542 | 0 | EL6021_M177 |  | FLOAT
EIR6230I1 | TDGA 1602-101-30 Phase currents I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 954 | 0 | 14564 | 0 | 16416 | 4550 | 0 | EL6021_M177 |  | FLOAT
EIR6230I2 | TDGA 1602-101-30 Phase currents I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 956 | 0 | 14566 | 0 | 16416 | 4554 | 0 | EL6021_M177 |  | FLOAT
EIR6230I3 | TDGA 1602-101-30 Phase currents I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 958 | 0 | 14568 | 0 | 16416 | 4558 | 0 | EL6021_M177 |  | FLOAT
EIR6230 | TDGA 1602-101-30 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 960 | 0 | 14570 | 0 | 16416 | 4562 | 0 | EL6021_M177 |  | FLOAT
EUR623012 | TDGA 1602-101-30 line to line voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 962 | 0 | 14572 | 0 | 16416 | 4566 | 0 | EL6021_M177 |  | FLOAT
EUR623023 | TDGA 1602-101-30 line to line voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 964 | 0 | 14574 | 0 | 16416 | 4570 | 0 | EL6021_M177 |  | FLOAT
EUR623031 | TDGA 1602-101-30 line to line voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 966 | 0 | 14576 | 0 | 16416 | 4574 | 0 | EL6021_M177 |  | FLOAT
EUR6230V1 | TDGA 1602-101-30 Phase voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 968 | 0 | 14578 | 0 | 16416 | 4578 | 0 | EL6021_M177 |  | FLOAT
EUR6230V2 | TDGA 1602-101-30 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 970 | 0 | 14580 | 0 | 16416 | 4582 | 0 | EL6021_M177 |  | FLOAT
EUR6230V3 | TDGA 1602-101-30 Phase voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 972 | 0 | 14582 | 0 | 16416 | 4586 | 0 | EL6021_M177 |  | FLOAT
EWR6230PF | TDGA 1602-101-30 Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 974 | 0 | 14584 | 0 | 16416 | 4590 | 0 | EL6021_M177 |  | FLOAT
EFR6230 | TDGA 1602-101-30 Frequency (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D130 | TDGA 1602 101 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 976 | 0 | 14586 | 0 | 16416 | 4594 | 0 | EL6021_M177 |  | FLOAT
EIR6231I1 | TDGA 1602-101-31 Phase currents I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 980 | 0 | 14590 | 0 | 16416 | 4602 | 0 | EL6021_M177 |  | FLOAT
EIR6231I2 | TDGA 1602-101-31 Phase currents I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 982 | 0 | 14592 | 0 | 16416 | 4606 | 0 | EL6021_M177 |  | FLOAT
EIR6231I3 | TDGA 1602-101-31 Phase currents I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 984 | 0 | 14594 | 0 | 16416 | 4610 | 0 | EL6021_M177 |  | FLOAT
EIR6231 | TDGA 1602-101-31 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 986 | 0 | 14596 | 0 | 16416 | 4614 | 0 | EL6021_M177 |  | FLOAT
EUR623112 | TDGA 1602-101-31 line to line voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 988 | 0 | 14598 | 0 | 16416 | 4618 | 0 | EL6021_M177 |  | FLOAT
EUR623123 | TDGA 1602-101-31 line to line voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 990 | 0 | 14600 | 0 | 16416 | 4622 | 0 | EL6021_M177 |  | FLOAT
EUR623131 | TDGA 1602-101-31 line to line voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 992 | 0 | 14602 | 0 | 16416 | 4626 | 0 | EL6021_M177 |  | FLOAT
EUR6231V1 | TDGA 1602-101-31 Phase voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 994 | 0 | 14604 | 0 | 16416 | 4630 | 0 | EL6021_M177 |  | FLOAT
EUR6231V2 | TDGA 1602-101-31 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 996 | 0 | 14606 | 0 | 16416 | 4634 | 0 | EL6021_M177 |  | FLOAT
EUR6231V3 | TDGA 1602-101-31 Phase voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 998 | 0 | 14608 | 0 | 16416 | 4638 | 0 | EL6021_M177 |  | FLOAT
EWR6231PF | TDGA 1602-101-31 Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1000 | 0 | 14610 | 0 | 16416 | 4642 | 0 | EL6021_M177 |  | FLOAT
EFR6231 | TDGA 1602-101-31 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D131 | TDGA 1602 101 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1002 | 0 | 14612 | 0 | 16416 | 4646 | 0 | EL6021_M177 |  | FLOAT
EIR6430I1 | TDGA 1602-201-30 Phase currents I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1006 | 0 | 14616 | 0 | 16416 | 4654 | 0 | EL6021_M177 |  | FLOAT
EIR6430I2 | TDGA 1602-201-30 Phase currents I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1008 | 0 | 14618 | 0 | 16416 | 4658 | 0 | EL6021_M177 |  | FLOAT
EIR6430I3 | TDGA 1602-201-30 Phase currents I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1010 | 0 | 14620 | 0 | 16416 | 4662 | 0 | EL6021_M177 |  | FLOAT
EIR6430 | TDGA 1602-201-30 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1012 | 0 | 14622 | 0 | 16416 | 4666 | 0 | EL6021_M177 |  | FLOAT
EUR643012 | TDGA 1602-201-30 line to line voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1014 | 0 | 14624 | 0 | 16416 | 4670 | 0 | EL6021_M177 |  | FLOAT
EUR643023 | TDGA 1602-201-30 line to line voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1016 | 0 | 14626 | 0 | 16416 | 4674 | 0 | EL6021_M177 |  | FLOAT
EUR643031 | TDGA 1602-201-30 line to line voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1018 | 0 | 14628 | 0 | 16416 | 4678 | 0 | EL6021_M177 |  | FLOAT
EUR6430V1 | TDGA 1602-201-30 Phase voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1020 | 0 | 14630 | 0 | 16416 | 4682 | 0 | EL6021_M177 |  | FLOAT
EUR6430V2 | TDGA 1602-201-30 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1022 | 0 | 14632 | 0 | 16416 | 4686 | 0 | EL6021_M177 |  | FLOAT
EUR6430V3 | TDGA 1602-201-30 Phase voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1024 | 0 | 14634 | 0 | 16416 | 4690 | 0 | EL6021_M177 |  | FLOAT
EWR6430PF | TDGA 1602-201-30 Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1026 | 0 | 14636 | 0 | 16416 | 4694 | 0 | EL6021_M177 |  | FLOAT
EFR6430 | TDGA 1602-201-30 Frequency (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D230 | TDGA 1602 201 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1028 | 0 | 14638 | 0 | 16416 | 4698 | 0 | EL6021_M177 |  | FLOAT
EIR6431I1 | TDGA 1602-201-31 Phase currents I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1032 | 0 | 14642 | 0 | 16416 | 4706 | 0 | EL6021_M177 |  | FLOAT
EIR6431I2 | TDGA 1602-201-31 Phase currents I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1034 | 0 | 14644 | 0 | 16416 | 4710 | 0 | EL6021_M177 |  | FLOAT
EIR6431I3 | TDGA 1602-201-31 Phase currents I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1036 | 0 | 14646 | 0 | 16416 | 4714 | 0 | EL6021_M177 |  | FLOAT
EIR6431 | TDGA 1602-201-31 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1038 | 0 | 14648 | 0 | 16416 | 4718 | 0 | EL6021_M177 |  | FLOAT
EUR643112 | TDGA 1602-201-31 line to line voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1040 | 0 | 14650 | 0 | 16416 | 4722 | 0 | EL6021_M177 |  | FLOAT
EUR643123 | TDGA 1602-201-31 line to line voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1042 | 0 | 14652 | 0 | 16416 | 4726 | 0 | EL6021_M177 |  | FLOAT
EUR643131 | TDGA 1602-201-31 line to line voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1044 | 0 | 14654 | 0 | 16416 | 4730 | 0 | EL6021_M177 |  | FLOAT
EUR6431V1 | TDGA 1602-201-31 Phase voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1046 | 0 | 14656 | 0 | 16416 | 4734 | 0 | EL6021_M177 |  | FLOAT
EUR6431V2 | TDGA 1602-201-31 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1048 | 0 | 14658 | 0 | 16416 | 4738 | 0 | EL6021_M177 |  | FLOAT
EUR6431V3 | TDGA 1602-201-31 Phase voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1050 | 0 | 14660 | 0 | 16416 | 4742 | 0 | EL6021_M177 |  | FLOAT
EWR6431PF | TDGA 1602-201-31 Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1052 | 0 | 14662 | 0 | 16416 | 4746 | 0 | EL6021_M177 |  | FLOAT
EFR6431 | TDGA 1602-201-31 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D231 | TDGA 1602 201 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1054 | 0 | 14664 | 0 | 16416 | 4750 | 0 | EL6021_M177 |  | FLOAT
EIR6530I1 | TDGA 1602-501-30 Phase currents I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1058 | 0 | 14668 | 0 | 16416 | 4758 | 0 | EL6021_M177 |  | FLOAT
EIR6530I2 | TDGA 1602-501-30 Phase currents I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1060 | 0 | 14670 | 0 | 16416 | 4762 | 0 | EL6021_M177 |  | FLOAT
EIR6530I3 | TDGA 1602-501-30 Phase currents I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1062 | 0 | 14672 | 0 | 16416 | 4766 | 0 | EL6021_M177 |  | FLOAT
EIR6530 | TDGA 1602-501-30 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1064 | 0 | 14674 | 0 | 16416 | 4770 | 0 | EL6021_M177 |  | FLOAT
EUR653012 | TDGA 1602-501-30 line to line voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1066 | 0 | 14676 | 0 | 16416 | 4774 | 0 | EL6021_M177 |  | FLOAT
EUR653023 | TDGA 1602-501-30 line to line voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1068 | 0 | 14678 | 0 | 16416 | 4778 | 0 | EL6021_M177 |  | FLOAT
EUR653031 | TDGA 1602-501-30 line to line voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1070 | 0 | 14680 | 0 | 16416 | 4782 | 0 | EL6021_M177 |  | FLOAT
EUR6530V1 | TDGA 1602-501-30 Phase voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1072 | 0 | 14682 | 0 | 16416 | 4786 | 0 | EL6021_M177 |  | FLOAT
EUR6530V2 | TDGA 1602-501-30 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1074 | 0 | 14684 | 0 | 16416 | 4790 | 0 | EL6021_M177 |  | FLOAT
EUR6530V3 | TDGA 1602-501-30 Phase voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1076 | 0 | 14686 | 0 | 16416 | 4794 | 0 | EL6021_M177 |  | FLOAT
EWR6530PF | TDGA 1602-501-30 Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1078 | 0 | 14688 | 0 | 16416 | 4798 | 0 | EL6021_M177 |  | FLOAT
EFR6530 | TDGA 1602-501-30 Frequency (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D530 | TDGA 1602 501 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1080 | 0 | 14690 | 0 | 16416 | 4802 | 0 | EL6021_M177 |  | FLOAT
EIR6531I1 | TDGA 1602-501-31 Phase currents I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1084 | 0 | 14694 | 0 | 16416 | 4810 | 0 | EL6021_M177 |  | FLOAT
EIR6531I2 | TDGA 1602-501-31 Phase currents I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1086 | 0 | 14696 | 0 | 16416 | 4814 | 0 | EL6021_M177 |  | FLOAT
EIR6531I3 | TDGA 1602-501-31 Phase currents I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1088 | 0 | 14698 | 0 | 16416 | 4818 | 0 | EL6021_M177 |  | FLOAT
EIR6531 | TDGA 1602-501-31 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1090 | 0 | 14700 | 0 | 16416 | 4822 | 0 | EL6021_M177 |  | FLOAT
EUR653112 | TDGA 1602-501-31 line to line voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1092 | 0 | 14702 | 0 | 16416 | 4826 | 0 | EL6021_M177 |  | FLOAT
EUR653123 | TDGA 1602-501-31 line to line voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1094 | 0 | 14704 | 0 | 16416 | 4830 | 0 | EL6021_M177 |  | FLOAT
EUR653131 | TDGA 1602-501-31 line to line voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1096 | 0 | 14706 | 0 | 16416 | 4834 | 0 | EL6021_M177 |  | FLOAT
EUR6531V1 | TDGA 1602-501-31 Phase voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1098 | 0 | 14708 | 0 | 16416 | 4838 | 0 | EL6021_M177 |  | FLOAT
EUR6531V2 | TDGA 1602-501-31 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1100 | 0 | 14710 | 0 | 16416 | 4842 | 0 | EL6021_M177 |  | FLOAT
EUR6531V3 | TDGA 1602-501-31 Phase voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1102 | 0 | 14712 | 0 | 16416 | 4846 | 0 | EL6021_M177 |  | FLOAT
EWR6531PF | TDGA 1602-501-31 Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1104 | 0 | 14714 | 0 | 16416 | 4850 | 0 | EL6021_M177 |  | FLOAT
EFR6531 | TDGA 1602-501-31 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D531 | TDGA 1602 501 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1106 | 0 | 14716 | 0 | 16416 | 4854 | 0 | EL6021_M177 |  | FLOAT
EIR6630I1 | TDGA 1602-502-30 Phase currents I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1110 | 0 | 14720 | 0 | 16416 | 4862 | 0 | EL6021_M177 |  | FLOAT
EIR6630I2 | TDGA 1602-502-30 Phase currents I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1112 | 0 | 14722 | 0 | 16416 | 4866 | 0 | EL6021_M177 |  | FLOAT
EIR6630I3 | TDGA 1602-502-30 Phase currents I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1114 | 0 | 14724 | 0 | 16416 | 4870 | 0 | EL6021_M177 |  | FLOAT
EIR6630 | TDGA 1602-502-30 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1116 | 0 | 14726 | 0 | 16416 | 4874 | 0 | EL6021_M177 |  | FLOAT
EUR663012 | TDGA 1602-502-30 line to line voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1118 | 0 | 14728 | 0 | 16416 | 4878 | 0 | EL6021_M177 |  | FLOAT
EUR663023 | TDGA 1602-502-30 line to line voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1120 | 0 | 14730 | 0 | 16416 | 4882 | 0 | EL6021_M177 |  | FLOAT
EUR663031 | TDGA 1602-502-30 line to line voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1122 | 0 | 14732 | 0 | 16416 | 4886 | 0 | EL6021_M177 |  | FLOAT
EUR6630V1 | TDGA 1602-502-30 Phase voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1124 | 0 | 14734 | 0 | 16416 | 4890 | 0 | EL6021_M177 |  | FLOAT
EUR6630V2 | TDGA 1602-502-30 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1126 | 0 | 14736 | 0 | 16416 | 4894 | 0 | EL6021_M177 |  | FLOAT
EUR6630V3 | TDGA 1602-502-30 Phase voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1128 | 0 | 14738 | 0 | 16416 | 4898 | 0 | EL6021_M177 |  | FLOAT
EWR6630PF | TDGA 1602-502-30 Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1130 | 0 | 14740 | 0 | 16416 | 4902 | 0 | EL6021_M177 |  | FLOAT
EFR6630 | TDGA 1602-502-30 Frequency (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D630 | TDGA 1602 502 30 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1132 | 0 | 14742 | 0 | 16416 | 4906 | 0 | EL6021_M177 |  | FLOAT
EIR6631I1 | TDGA 1602-502-31 Phase currents I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1136 | 0 | 14746 | 0 | 16416 | 4914 | 0 | EL6021_M177 |  | FLOAT
EIR6631I2 | TDGA 1602-502-31 Phase currents I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1138 | 0 | 14748 | 0 | 16416 | 4918 | 0 | EL6021_M177 |  | FLOAT
EIR6631I3 | TDGA 1602-502-31 Phase currents I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1140 | 0 | 14750 | 0 | 16416 | 4922 | 0 | EL6021_M177 |  | FLOAT
EIR6631 | TDGA 1602-502-31 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1142 | 0 | 14752 | 0 | 16416 | 4926 | 0 | EL6021_M177 |  | FLOAT
EUR663112 | TDGA 1602-502-31 line to line voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1144 | 0 | 14754 | 0 | 16416 | 4930 | 0 | EL6021_M177 |  | FLOAT
EUR663123 | TDGA 1602-502-31 line to line voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1146 | 0 | 14756 | 0 | 16416 | 4934 | 0 | EL6021_M177 |  | FLOAT
EUR663131 | TDGA 1602-502-31 line to line voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1148 | 0 | 14758 | 0 | 16416 | 4938 | 0 | EL6021_M177 |  | FLOAT
EUR6631V1 | TDGA 1602-502-31 Phase voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1150 | 0 | 14760 | 0 | 16416 | 4942 | 0 | EL6021_M177 |  | FLOAT
EUR6631V2 | TDGA 1602-502-31 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1152 | 0 | 14762 | 0 | 16416 | 4946 | 0 | EL6021_M177 |  | FLOAT
EUR6631V3 | TDGA 1602-502-31 Phase voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1154 | 0 | 14764 | 0 | 16416 | 4950 | 0 | EL6021_M177 |  | FLOAT
EWR6631PF | TDGA 1602-502-31 Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1156 | 0 | 14766 | 0 | 16416 | 4954 | 0 | EL6021_M177 |  | FLOAT
EFR6631 | TDGA 1602-502-31 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D631 | TDGA 1602 502 31 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1158 | 0 | 14768 | 0 | 16416 | 4958 | 0 | EL6021_M177 |  | FLOAT
EIR6702AI1 | TD AXIMA 1602-401-002 Phase currents I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1162 | 0 | 14772 | 0 | 16416 | 4966 | 0 | EL6021_M177 |  | FLOAT
EIR6702AI2 | TD AXIMA 1602-401-002 Phase currents I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1164 | 0 | 14774 | 0 | 16416 | 4970 | 0 | EL6021_M177 |  | FLOAT
EIR6702AI3 | TD AXIMA 1602-401-002 Phase currents I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1166 | 0 | 14776 | 0 | 16416 | 4974 | 0 | EL6021_M177 |  | FLOAT
EIR6702A | TD AXIMA 1602-401-002 Neutral Current (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1168 | 0 | 14778 | 0 | 16416 | 4978 | 0 | EL6021_M177 |  | FLOAT
EUR6702A12 | TD AXIMA 1602-401-002 line to line voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1170 | 0 | 14780 | 0 | 16416 | 4982 | 0 | EL6021_M177 |  | FLOAT
EUR6702A23 | TD AXIMA 1602-401-002 line to line voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1172 | 0 | 14782 | 0 | 16416 | 4986 | 0 | EL6021_M177 |  | FLOAT
EUR6702A31 | TD AXIMA 1602-401-002 line to line voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1174 | 0 | 14784 | 0 | 16416 | 4990 | 0 | EL6021_M177 |  | FLOAT
EUR6702AV1 | TD AXIMA 1602-401-002 Phase voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1176 | 0 | 14786 | 0 | 16416 | 4994 | 0 | EL6021_M177 |  | FLOAT
EUR6702AV2 | TD AXIMA 1602-401-002 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1178 | 0 | 14788 | 0 | 16416 | 4998 | 0 | EL6021_M177 |  | FLOAT
EUR6702AV3 | TD AXIMA 1602-401-002 Phase voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1180 | 0 | 14790 | 0 | 16416 | 5002 | 0 | EL6021_M177 |  | FLOAT
EWR6702APF | TD AXIMA 1602-401-002 Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1182 | 0 | 14792 | 0 | 16416 | 5006 | 0 | EL6021_M177 |  | FLOAT
EFR6702A | TD AXIMA 1602-401-002 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325AD42 | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1184 | 0 | 14794 | 0 | 16416 | 5010 | 0 | EL6021_M177 |  | FLOAT
EIR6702BI1 | TD AXIMA 1602-401-002 Phase currents I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1188 | 0 | 14798 | 0 | 16416 | 5018 | 0 | EL6021_M177 |  | FLOAT
EIR6702BI2 | TD AXIMA 1602-401-002 Phase currents I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1190 | 0 | 14800 | 0 | 16416 | 5022 | 0 | EL6021_M177 |  | FLOAT
EIR6702BI3 | TD AXIMA 1602-401-002 Phase currents I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1192 | 0 | 14802 | 0 | 16416 | 5026 | 0 | EL6021_M177 |  | FLOAT
EIR6702B | TD AXIMA 1602-401-002 Neutral Current (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1194 | 0 | 14804 | 0 | 16416 | 5030 | 0 | EL6021_M177 |  | FLOAT
EUR6702B12 | TD AXIMA 1602-401-002 line to line voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1196 | 0 | 14806 | 0 | 16416 | 5034 | 0 | EL6021_M177 |  | FLOAT
EUR6702B23 | TD AXIMA 1602-401-002 line to line voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1198 | 0 | 14808 | 0 | 16416 | 5038 | 0 | EL6021_M177 |  | FLOAT
EUR6702B31 | TD AXIMA 1602-401-002 line to line voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1200 | 0 | 14810 | 0 | 16416 | 5042 | 0 | EL6021_M177 |  | FLOAT
EUR6702BV1 | TD AXIMA 1602-401-002 Phase voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1202 | 0 | 14812 | 0 | 16416 | 5046 | 0 | EL6021_M177 |  | FLOAT
EUR6702BV2 | TD AXIMA 1602-401-002 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1204 | 0 | 14814 | 0 | 16416 | 5050 | 0 | EL6021_M177 |  | FLOAT
EUR6702BV3 | TD AXIMA 1602-401-002 Phase voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1206 | 0 | 14816 | 0 | 16416 | 5054 | 0 | EL6021_M177 |  | FLOAT
EWR6702BPF | TD AXIMA 1602-401-002 Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1208 | 0 | 14818 | 0 | 16416 | 5058 | 0 | EL6021_M177 |  | FLOAT
EFR6702B | TD AXIMA 1602-401-002 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325BD42 | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1210 | 0 | 14820 | 0 | 16416 | 5062 | 0 | EL6021_M177 |  | FLOAT
EIR6701I1 | TD AXIMA 1602-401-001 Phase currents I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1214 | 0 | 14824 | 0 | 16416 | 5070 | 0 | EL6021_M177 |  | FLOAT
EIR6701I2 | TD AXIMA 1602-401-001 Phase currents I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1216 | 0 | 14826 | 0 | 16416 | 5074 | 0 | EL6021_M177 |  | FLOAT
EIR6701I3 | TD AXIMA 1602-401-001 Phase currents I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1218 | 0 | 14828 | 0 | 16416 | 5078 | 0 | EL6021_M177 |  | FLOAT
EIR6701 | TD AXIMA 1602-401-001 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1220 | 0 | 14830 | 0 | 16416 | 5082 | 0 | EL6021_M177 |  | FLOAT
EUR670112 | TD AXIMA 1602-401-001 line to line voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1222 | 0 | 14832 | 0 | 16416 | 5086 | 0 | EL6021_M177 |  | FLOAT
EUR670123 | TD AXIMA 1602-401-001 line to line voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1224 | 0 | 14834 | 0 | 16416 | 5090 | 0 | EL6021_M177 |  | FLOAT
EUR670131 | TD AXIMA 1602-401-001 line to line voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1226 | 0 | 14836 | 0 | 16416 | 5094 | 0 | EL6021_M177 |  | FLOAT
EUR6701V1 | TD AXIMA 1602-401-001 Phase voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1228 | 0 | 14838 | 0 | 16416 | 5098 | 0 | EL6021_M177 |  | FLOAT
EUR6701V2 | TD AXIMA 1602-401-001 Phase voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1230 | 0 | 14840 | 0 | 16416 | 5102 | 0 | EL6021_M177 |  | FLOAT
EUR6701V3 | TD AXIMA 1602-401-001 Phase voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1232 | 0 | 14842 | 0 | 16416 | 5106 | 0 | EL6021_M177 |  | FLOAT
EWR6701PF | TD AXIMA 1602-401-001 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1234 | 0 | 14844 | 0 | 16416 | 5110 | 0 | EL6021_M177 |  | FLOAT
EFR6701 | TD AXIMA 1602-401-001 Frequency (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D41 | TD AXIMA 1602 401 001 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1236 | 0 | 14846 | 0 | 16416 | 5114 | 0 | EL6021_M177 |  | FLOAT
EIR6703I1 | TD AXIMA 1602-401-003 Phase currents I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1240 | 0 | 14850 | 0 | 16416 | 5122 | 0 | EL6021_M177 |  | FLOAT
EIR6703I2 | TD AXIMA 1602-401-003 Phase currents I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1242 | 0 | 14852 | 0 | 16416 | 5126 | 0 | EL6021_M177 |  | FLOAT
EIR6703I3 | TD AXIMA 1602-401-003 Phase currents I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1244 | 0 | 14854 | 0 | 16416 | 5130 | 0 | EL6021_M177 |  | FLOAT
EIR6703 | TD AXIMA 1602-401-003 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1246 | 0 | 14856 | 0 | 16416 | 5134 | 0 | EL6021_M177 |  | FLOAT
EUR670312 | TD AXIMA 1602-401-003 line to line voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1248 | 0 | 14858 | 0 | 16416 | 5138 | 0 | EL6021_M177 |  | FLOAT
EUR670323 | TD AXIMA 1602-401-003 line to line voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1250 | 0 | 14860 | 0 | 16416 | 5142 | 0 | EL6021_M177 |  | FLOAT
EUR670331 | TD AXIMA 1602-401-003 line to line voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1252 | 0 | 14862 | 0 | 16416 | 5146 | 0 | EL6021_M177 |  | FLOAT
EUR6703V1 | TD AXIMA 1602-401-003 Phase voltage 1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1254 | 0 | 14864 | 0 | 16416 | 5150 | 0 | EL6021_M177 |  | FLOAT
EUR6703V2 | TD AXIMA 1602-401-003 Phase voltage 2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1256 | 0 | 14866 | 0 | 16416 | 5154 | 0 | EL6021_M177 |  | FLOAT
EUR6703V3 | TD AXIMA 1602-401-003 Phase voltage 3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1258 | 0 | 14868 | 0 | 16416 | 5158 | 0 | EL6021_M177 |  | FLOAT
EWR6703PF | TD AXIMA 1602-401-003 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1260 | 0 | 14870 | 0 | 16416 | 5162 | 0 | EL6021_M177 |  | FLOAT
EFR6703 | TD AXIMA 1602-401-003 Frequency (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D43 | TD AXIMA 1602 401 003 CAT II (E67) | Energie TD | ENE_MC | 3 |  |  | 1262 | 0 | 14872 | 0 | 16416 | 5166 | 0 | EL6021_M177 |  | FLOAT
EIR6832I1 | TD3 Local 101 IIIA 1602-101-32 Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1266 | 0 | 14876 | 0 | 16416 | 5174 | 0 | EL6021_M177 |  | FLOAT
EIR6832I2 | TD3 Local 101 IIIA 1602-101-32 Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1268 | 0 | 14878 | 0 | 16416 | 5178 | 0 | EL6021_M177 |  | FLOAT
EIR6832I3 | TD3 Local 101 IIIA 1602-101-32 Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1270 | 0 | 14880 | 0 | 16416 | 5182 | 0 | EL6021_M177 |  | FLOAT
EIR6832 | TD3 Local 101 IIIA 1602-101-32 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1272 | 0 | 14882 | 0 | 16416 | 5186 | 0 | EL6021_M177 |  | FLOAT
EUR683212 | TD3 Local 101 IIIA 1602-101-32 line to line voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1274 | 0 | 14884 | 0 | 16416 | 5190 | 0 | EL6021_M177 |  | FLOAT
EUR683223 | TD3 Local 101 IIIA 1602-101-32 line to line voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1276 | 0 | 14886 | 0 | 16416 | 5194 | 0 | EL6021_M177 |  | FLOAT
EUR683231 | TD3 Local 101 IIIA 1602-101-32 line to line voltage 3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1278 | 0 | 14888 | 0 | 16416 | 5198 | 0 | EL6021_M177 |  | FLOAT
EUR6832V1 | TD3 Local 101 IIIA 1602-101-32 Phase voltage 1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1280 | 0 | 14890 | 0 | 16416 | 5202 | 0 | EL6021_M177 |  | FLOAT
EUR6832V2 | TD3 Local 101 IIIA 1602-101-32 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1282 | 0 | 14892 | 0 | 16416 | 5206 | 0 | EL6021_M177 |  | FLOAT
EUR6832V3 | TD3 Local 101 IIIA 1602-101-32 Phase voltage 2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1284 | 0 | 14894 | 0 | 16416 | 5210 | 0 | EL6021_M177 |  | FLOAT
EWR6832PF | TD3 Local 101 IIIA 1602-101-32 Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1286 | 0 | 14896 | 0 | 16416 | 5214 | 0 | EL6021_M177 |  | FLOAT
EFR6832 | TD3 Local 101 IIIA 1602-101-32 Frequency (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D132 | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energie TD | ENE_MC | 3 |  |  | 1288 | 0 | 14898 | 0 | 16416 | 5218 | 0 | EL6021_M177 |  | FLOAT
EIR6833I1 | TD3 Local 101 IIIB 1602-101-33 Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1292 | 0 | 14902 | 0 | 16416 | 5226 | 0 | EL6021_M177 |  | FLOAT
EIR6833I2 | TD3 Local 101 IIIB 1602-101-33 Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1294 | 0 | 14904 | 0 | 16416 | 5230 | 0 | EL6021_M177 |  | FLOAT
EIR6833I3 | TD3 Local 101 IIIB 1602-101-33 Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1296 | 0 | 14906 | 0 | 16416 | 5234 | 0 | EL6021_M177 |  | FLOAT
EIR6833 | TD3 Local 101 IIIB 1602-101-33 Neutral Current | MA | N | RES | 1 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1298 | 0 | 14908 | 0 | 16416 | 5238 | 0 | EL6021_M177 |  | FLOAT
EUR683312 | TD3 Local 101 IIIB 1602-101-33 line to line voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1300 | 0 | 14910 | 0 | 16416 | 5242 | 0 | EL6021_M177 |  | FLOAT
EUR683323 | TD3 Local 101 IIIB 1602-101-33 line to line voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1302 | 0 | 14912 | 0 | 16416 | 5246 | 0 | EL6021_M177 |  | FLOAT
EUR683331 | TD3 Local 101 IIIB 1602-101-33 line to line voltage 3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1304 | 0 | 14914 | 0 | 16416 | 5250 | 0 | EL6021_M177 |  | FLOAT
EUR6833V1 | TD3 Local 101 IIIB 1602-101-33 Phase voltage 1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1306 | 0 | 14916 | 0 | 16416 | 5254 | 0 | EL6021_M177 |  | FLOAT
EUR6833V2 | TD3 Local 101 IIIB 1602-101-33 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1308 | 0 | 14918 | 0 | 16416 | 5258 | 0 | EL6021_M177 |  | FLOAT
EUR6833V3 | TD3 Local 101 IIIB 1602-101-33 Phase voltage 2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1310 | 0 | 14920 | 0 | 16416 | 5262 | 0 | EL6021_M177 |  | FLOAT
EWR6833PF | TD3 Local 101 IIIB 1602-101-33 Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1312 | 0 | 14922 | 0 | 16416 | 5266 | 0 | EL6021_M177 |  | FLOAT
EFR6833 | TD3 Local 101 IIIB 1602-101-33 Frequency (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | EZC6325D133 | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energie TD | ENE_MC | 3 |  |  | 1314 | 0 | 14924 | 0 | 16416 | 5270 | 0 | EL6021_M177 |  | FLOAT
VRU6981CF | CDE VOLETS EXTINCTION N2 PORTIQUE 101 - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6021GE (ON) | [8 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 0 | 16416 | 1288 | 0 | EL2809_M170 | 12 | U8 | 1
VRU6981CO | CDE VOLETS EXTINCTION N2 PORTIQUE 101 - U8(2),FERMER(1) / U8(2),OUVRIR(2) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 1 | 16416 | 1288 | 0 | EL2809_M170 | 12 | U8 | 2
VRU6982CF | CDE VOLETS EXTINCTION N2 PORTIQUE 201 - U8(2),FERMER(4) / U8(2),OUVRIR(8) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6022GE (ON) | [8 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 2 | 16416 | 1288 | 0 | EL2809_M170 | 13 | U8 | 4
VRU6982CO | CDE VOLETS EXTINCTION N2 PORTIQUE 201 - U8(2),FERMER(4) / U8(2),OUVRIR(8) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 3 | 16416 | 1288 | 0 | EL2809_M170 | 13 | U8 | 8
VRU6983CF | CDE VOLETS EXTINCTION N2 PORTIQUE 502 - U8(2),FERMER(16) / U8(2),OUVRIR(32) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NO |  |  | SCX6023GE (ON) | [8 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 4 | 16416 | 1288 | 0 | EL2809_M170 | 14 | U8 | 16
VRU6983CO | CDE VOLETS EXTINCTION N2 PORTIQUE 502 - U8(2),FERMER(16) / U8(2),OUVRIR(32) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NO | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 5 | 16416 | 1288 | 0 | EL2809_M170 | 14 | U8 | 32
VVU6907CM | CDE BALAYAGE UDMH LOC.601 PORTIQUE VEGA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 6 | 16416 | 1288 | 0 | EL2809_M170 | 15 | U8 | 64
VVU6907CA | CDE BALAYAGE UDMH LOC.601 PORTIQUE VEGA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 7 | 16416 | 1288 | 0 | EL2809_M170 | 15 | U8 | 128
SPASMA0182 | SPARE SER 0182 | MA | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 4 |  |  | 3069 | NA | 13138 | NA | 16416 | 1698 | 0 | EL6021_M178 |  | U16
SCX6021CM | CDE EI NIV 18.400 LOCAL 101 ENERGIE - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12933 | 8 | 16416 | 1289 | 0 | EL2809_M170 | 16 | U8 | 1
SCX6021CA | CDE EI NIV 18.400 LOCAL 101 ENERGIE - U8(2),MARCHE(1) / U8(2),ARRET(2) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12933 | 9 | 16416 | 1289 | 0 | EL2809_M170 | 16 | U8 | 2
SCX6022CM | CDE EI NIV 21.200 SAUVEGARDE CFS - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12933 | 10 | 16416 | 1289 | 0 | EL2809_M171 | 1 | U8 | 4
SCX6022CA | CDE EI NIV 21.200 SAUVEGARDE CFS - U8(2),MARCHE(4) / U8(2),ARRET(8) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12933 | 11 | 16416 | 1289 | 0 | EL2809_M171 | 1 | U8 | 8
SCX6023CM | CDE EI NIV 29.200 BCV/INTF - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | O | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12933 | 12 | 16416 | 1289 | 0 | EL2809_M171 | 2 | U8 | 16
SCX6023CA | CDE EI NIV 29.200 BCV/INTF - U8(2),MARCHE(16) / U8(2),ARRET(32) | CT | N | FIL | 1 | S | [11 empty] | OFF | S | NO | NF | [11 empty] | NOT |  |  | EI69 | Extinction Incendie (EI) | CCS | [5 empty] | 12933 | 13 | 16416 | 1289 | 0 | EL2809_M171 | 2 | U8 | 32
VVU6906CM | CDE BALAYAGE N2O4 LOC.701 PORTIQUE VEGA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | O | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 14 | 16416 | 1289 | 0 | EL2809_M171 | 3 | U8 | 64
VVU6906CA | CDE BALAYAGE N2O4 LOC.701 PORTIQUE VEGA - U8(2),MARCHE(64) / U8(2),ARRET(128) | CT | N | FIL | 1 | C | [11 empty] | OFF | C | NO | NF | [11 empty] | NOT |  |  | HVAC16 | HVAC | CCS | [5 empty] | 12933 | 15 | 16416 | 1289 | 0 | EL2809_M171 | 3 | U8 | 128
EQF6002CA | CMDE "SECOURS INVERSE" TGBT - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | INT | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E61 | Energie TGBT et UPS VEGA (E) | CCS | 4 |  |  | 3000 | NA | 13032 | NA | 16416 | 1486 | 0 | EL6021_M178 |  | U8 | 1
EWR6081P | TGBT ZLV ARRIVEE TM 7002 CAT.II Total Active Power P | MA | N | RES | 1 | E |  |  | kW | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3079 | NA | 13148 | NA | 16416 | 1718 | 0 | EL6021_M178 |  | INT
EWR6081Q | TGBT ZLV ARRIVEE TM 7002 CAT.II Total Reactive Power Q | MA | N | RES | 1 | E |  |  | kVAr | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3080 | NA | 13149 | NA | 16416 | 1720 | 0 | EL6021_M178 |  | INT
EWR6081S | TGBT ZLV ARRIVEE TM 7002 CAT.II Total Apparent Power S | MA | N | RES | 1 | E |  |  | kVA | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3081 | NA | 13150 | NA | 16416 | 1722 | 0 | EL6021_M178 |  | INT
EQF6002CM | CMDE "SECOURS INVERSE" TGBT - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | INT | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E61 | Energie TGBT et UPS VEGA (E) | CCS | 4 |  |  | 3000 | NA | 13032 | NA | 16416 | 1486 | 0 | EL6021_M178 |  | U8 | 2
EQF6951CA | CMDE "SECOURS INVERSE" TGBT-C - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | INT | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E62 | Energie TGBT et UPS VEGA (E) | CCS | 4 |  |  | 3001 | NA | 13033 | NA | 16416 | 1488 | 0 | EL6021_M178 |  | U8 | 1
SPASMA0183 | SPARE SER 0183 | MA | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 4 |  |  | 3084 | NA | 13153 | NA | 16416 | 1728 | 0 | EL6021_M178 |  | INT
SPASMA0184 | SPARE SER 0184 | MA | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 4 |  |  | 3085 | NA | 13154 | NA | 16416 | 1730 | 0 | EL6021_M178 |  | INT
SPASMA0185 | SPARE SER 0185 | MA | N | RES | [28 empty] | POL | 10000 |  | VMC06 | VMC (Z) |  | 4 |  |  | 3086 | NA | 13155 | NA | 16416 | 1732 | 0 | EL6021_M178 |  | INT
SPASMA0186 | SPARE SER 0186 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3087 | NA | 13156 | NA | 16416 | 1734 | 0 | EL6021_M178 |  | INT
SPASMA0187 | SPARE SER 0187 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3088 | NA | 13157 | NA | 16416 | 1736 | 0 | EL6021_M178 |  | INT
SPASMA0188 | SPARE SER 0188 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3089 | NA | 13158 | NA | 16416 | 1738 | 0 | EL6021_M178 |  | INT
EQF6951CM | CMDE "SECOURS INVERSE" TGBT-C - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | INT | 1 | E | [11 empty] | OFF | E | NO | NF | [11 empty] | NOT |  |  | E62 | Energie TGBT et UPS VEGA (E) | CCS | 4 |  |  | 3001 | NA | 13033 | NA | 16416 | 1488 | 0 | EL6021_M178 |  | U8 | 2
VVU6126CM1 | CMDE INSTALLATION HVAC BUNKER API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3000 | NA | 13717 | NA | 16416 | 2856 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CA1 | CMDE INSTALLATION HVAC BUNKER API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3000 | NA | 13717 | NA | 16416 | 2856 | 0 | EL6021_M180 |  | U8 | 1
VVU6126CM3 | CMDE MODE OPE/ECO HVAC BUNKER API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3001 | NA | 13718 | NA | 16416 | 2858 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CA3 | CMDE MODE OPE/ECO HVAC BUNKER API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3001 | NA | 13718 | NA | 16416 | 2858 | 0 | EL6021_M180 |  | U8 | 1
VVU6126CM101 | BUNKER API: INFO GANTRY HVAC INSTALLATION - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT | [5 empty] | 6 |  |  | 3002 | NA | 13719 | NA | 16416 | 2860 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CA101 | BUNKER API: INFO GANTRY HVAC INSTALLATION - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT | [5 empty] | 6 |  |  | 3002 | NA | 13719 | NA | 16416 | 2860 | 0 | EL6021_M180 |  | U8 | 1
VVU6126CM103 | BUNKER API: INFO MODE OPE/ECO GANTRY HVAC - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT | [5 empty] | 6 |  |  | 3003 | NA | 13720 | NA | 16416 | 2862 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CA403 | BUNKER API: INFO MODE OPE/ECO GANTRY HVAC - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT | [5 empty] | 6 |  |  | 3003 | NA | 13720 | NA | 16416 | 2862 | 0 | EL6021_M180 |  | U8 | 1
EWR6082P | TGBT ZLV ARRIVEE TM 7004 CAT.I Total Active Power P | MA | N | RES | 1 | E |  |  | kW | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3099 | NA | 13168 | NA | 16416 | 1758 | 0 | EL6021_M178 |  | INT
EWR6082Q | TGBT ZLV ARRIVEE TM 7004 CAT.I Total Reactive Power Q | MA | N | RES | 1 | E |  |  | kVAr | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3100 | NA | 13169 | NA | 16416 | 1760 | 0 | EL6021_M178 |  | INT
EWR6082S | TGBT ZLV ARRIVEE TM 7004 CAT.I Total Apparent Power S | MA | N | RES | 1 | E |  |  | kVA | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3101 | NA | 13170 | NA | 16416 | 1762 | 0 | EL6021_M178 |  | INT
VZC6126CZ | VEGA BUNKER PLC : CLEARING DEFAULTS | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3004 | NA | 13721 | NA | 16416 | 2864 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CM4 | BUNKER API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3006 | NA | 13723 | NA | 16416 | 2868 | 0 | EL6021_M180 |  | U8 | 2
SPASMA0189 | SPARE SER 0189 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3104 | NA | 13173 | NA | 16416 | 1768 | 0 | EL6021_M178 |  | INT
SPASMA0190 | SPARE SER 0190 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3105 | NA | 13174 | NA | 16416 | 1770 | 0 | EL6021_M178 |  | INT
SPASMA0191 | SPARE SER 0191 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3106 | NA | 13175 | NA | 16416 | 1772 | 0 | EL6021_M178 |  | INT
SPASMA0192 | SPARE SER 0192 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3107 | NA | 13176 | NA | 16416 | 1774 | 0 | EL6021_M178 |  | INT
SPASMA0193 | SPARE SER 0193 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3108 | NA | 13177 | NA | 16416 | 1776 | 0 | EL6021_M178 |  | INT
SPASMA0194 | SPARE SER 0194 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3109 | NA | 13178 | NA | 16416 | 1778 | 0 | EL6021_M178 |  | INT
VVU6126CA4 | BUNKER API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3006 | NA | 13723 | NA | 16416 | 2868 | 0 | EL6021_M180 |  | U8 | 1
VCF6126CF | BUNKER API: DECLENCHEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3007 | NA | 13724 | NA | 16416 | 2870 | 0 | EL6021_M180 |  | U8 | 2
VCF6126CF2 | BUNKER API: DECLENCHEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3007 | NA | 13724 | NA | 16416 | 2870 | 0 | EL6021_M180 |  | U8 | 1
VCF6126CO | BUNKER API: REARMEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3008 | NA | 13725 | NA | 16416 | 2872 | 0 | EL6021_M180 |  | U8 | 2
VCF6126CO2 | BUNKER API: REARMEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3008 | NA | 13725 | NA | 16416 | 2872 | 0 | EL6021_M180 |  | U8 | 1
VVU6126CO100 | BUNKER API: PORT HALL GANTRY INFO - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT | [5 empty] | 6 |  |  | 3009 | NA | 13726 | NA | 16416 | 2874 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CF100 | BUNKER API: PORT HALL GANTRY INFO - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT | [5 empty] | 6 |  |  | 3009 | NA | 13726 | NA | 16416 | 2874 | 0 | EL6021_M180 |  | U8 | 1
VVU6126CM2 | BUNKER API: CMD CLIM INTERNE HVAC CTA BUNKER - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3011 | NA | 13728 | NA | 16416 | 2878 | 0 | EL6021_M180 |  | U8 | 2
VVU6126CA2 | BUNKER API: CMD CLIM INTERNE HVAC CTA BUNKER - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3011 | NA | 13728 | NA | 16416 | 2878 | 0 | EL6021_M180 |  | U8 | 1
EWR6083P | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Total Active Power P | MA | N | RES | 1 | E |  |  | kW | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3119 | NA | 13188 | NA | 16416 | 1798 | 0 | EL6021_M178 |  | INT
EWR6083Q | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Total Reactive Power Q | MA | N | RES | 1 | E |  |  | kVAr | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3120 | NA | 13189 | NA | 16416 | 1800 | 0 | EL6021_M178 |  | INT
EWR6083S | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Total Apparent Power S | MA | N | RES | 1 | E |  |  | kVA | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3121 | NA | 13190 | NA | 16416 | 1802 | 0 | EL6021_M178 |  | INT
VRP6126CO1 | BUNKER API: CMD PRISE AIR NEUF LOCALE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3016 | NA | 13733 | NA | 16416 | 2888 | 0 | EL6021_M180 |  | U8 | 2
VRP6126CF1 | BUNKER API: CMD PRISE AIR NEUF LOCALE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3016 | NA | 13733 | NA | 16416 | 2888 | 0 | EL6021_M180 |  | U8 | 1
SPASMA0195 | SPARE SER 0195 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3124 | NA | 13193 | NA | 16416 | 1808 | 0 | EL6021_M178 |  | INT
SPASMA0196 | SPARE SER 0196 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3125 | NA | 13194 | NA | 16416 | 1810 | 0 | EL6021_M178 |  | INT
SPASMA0197 | SPARE SER 0197 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3126 | NA | 13195 | NA | 16416 | 1812 | 0 | EL6021_M178 |  | INT
SPASMA0198 | SPARE SER 0198 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3127 | NA | 13196 | NA | 16416 | 1814 | 0 | EL6021_M178 |  | INT
SPASMA0199 | SPARE SER 0199 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3128 | NA | 13197 | NA | 16416 | 1816 | 0 | EL6021_M178 |  | INT
SPASMA0200 | SPARE SER 0200 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3129 | NA | 13198 | NA | 16416 | 1818 | 0 | EL6021_M178 |  | INT
VRP6126CO2 | BUNKER API: CMD PRISE AIR NEUF DISTANTE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3017 | NA | 13734 | NA | 16416 | 2890 | 0 | EL6021_M180 |  | U8 | 2
VRP6126CF2 | BUNKER API: CMD PRISE AIR NEUF DISTANTE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6126V (OFF) | [7 empty] | NOT |  |  | HVAC12 | HVAC |  | 6 |  |  | 3017 | NA | 13734 | NA | 16416 | 2890 | 0 | EL6021_M180 |  | U8 | 1
VVU6401CM1 | CMDE INSTALLATION HVAC GANTRY API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT | [5 empty] | 7 |  |  | 3000 | NA | 14098 | NA | 16416 | 3618 | 0 | EL6021_M181 |  | U8 | 2
VVU6401CA1 | CMDE INSTALLATION HVAC GANTRY API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT | [5 empty] | 7 |  |  | 3000 | NA | 14098 | NA | 16416 | 3618 | 0 | EL6021_M181 |  | U8 | 1
VVU6401CM3 | CMDE MODE OPE/ECO HVAC GANTRY API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT | [5 empty] | 7 |  |  | 3001 | NA | 14099 | NA | 16416 | 3620 | 0 | EL6021_M181 |  | U8 | 2
VVU6401CA3 | CMDE MODE OPE/ECO HVAC GANTRY API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT | [5 empty] | 7 |  |  | 3001 | NA | 14099 | NA | 16416 | 3620 | 0 | EL6021_M181 |  | U8 | 1
VZC6401CZ | VEGA GANTRY PLC : CLEARING DEFAULTS | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3004 | NA | 14102 | NA | 16416 | 3626 | 0 | EL6021_M181 |  | U8 | 2
VPZ6999CO | GANTRY API: CMDE PORTE HALL GANTRY - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT | [5 empty] | 7 |  |  | 3005 | NA | 14103 | NA | 16416 | 3628 | 0 | EL6021_M181 |  | U8 | 2
VPZ6999CF | GANTRY API: CMDE PORTE HALL GANTRY - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT | [5 empty] | 7 |  |  | 3005 | NA | 14103 | NA | 16416 | 3628 | 0 | EL6021_M181 |  | U8 | 1
EWR6084P | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Total Active Power P | MA | N | RES | 1 | E |  |  | kW | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3139 | NA | 13208 | NA | 16416 | 1838 | 0 | EL6021_M178 |  | INT
EWR6084Q | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Total Reactive Power Q | MA | N | RES | 1 | E |  |  | kVAr | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3140 | NA | 13209 | NA | 16416 | 1840 | 0 | EL6021_M178 |  | INT
EWR6084S | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Total Apparent Power S | MA | N | RES | 1 | E |  |  | kVA | 1 | -32767 | 32767 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3141 | NA | 13210 | NA | 16416 | 1842 | 0 | EL6021_M178 |  | INT
VZN6701CM | GANTRY API: REMPLISSAGE N2O4 - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3006 | NA | 14104 | NA | 16416 | 3630 | 0 | EL6021_M181 |  | U8 | 2
VZN6701CA | GANTRY API: REMPLISSAGE N2O4 - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3006 | NA | 14104 | NA | 16416 | 3630 | 0 | EL6021_M181 |  | U8 | 1
SPASMA0201 | SPARE SER 0201 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3144 | NA | 13213 | NA | 16416 | 1848 | 0 | EL6021_M178 |  | INT
SPASMA0202 | SPARE SER 0202 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3145 | NA | 13214 | NA | 16416 | 1850 | 0 | EL6021_M178 |  | INT
SPASMA0203 | SPARE SER 0203 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3146 | NA | 13215 | NA | 16416 | 1852 | 0 | EL6021_M178 |  | INT
SPASMA0204 | SPARE SER 0204 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3147 | NA | 13216 | NA | 16416 | 1854 | 0 | EL6021_M178 |  | INT
SPASMA0205 | SPARE SER 0205 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3148 | NA | 13217 | NA | 16416 | 1856 | 0 | EL6021_M178 |  | INT
SPASMA0206 | SPARE SER 0206 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3149 | NA | 13218 | NA | 16416 | 1858 | 0 | EL6021_M178 |  | INT
VZU6601CM | GANTRY API: REMPLISSAGE UDMH - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3007 | NA | 14105 | NA | 16416 | 3632 | 0 | EL6021_M181 |  | U8 | 2
VZU6601CA | GANTRY API: REMPLISSAGE UDMH - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3007 | NA | 14105 | NA | 16416 | 3632 | 0 | EL6021_M181 |  | U8 | 1
VVU6401CM4 | GANTRY API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3008 | NA | 14106 | NA | 16416 | 3634 | 0 | EL6021_M181 |  | U8 | 2
VVU6401CA4 | GANTRY API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3008 | NA | 14106 | NA | 16416 | 3634 | 0 | EL6021_M181 |  | U8 | 1
VVU6401CM2 | GANTRY API: CMD CLIM INTERNE HVAC - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3011 | NA | 14109 | NA | 16416 | 3640 | 0 | EL6021_M181 |  | U8 | 2
VVU6401CA2 | GANTRY API: CMD CLIM INTERNE HVAC - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | INT | 1 | C | [11 empty] | NO | C | NO | NO |  |  |  | VUM6401V (OFF) | [7 empty] | NOT |  |  | HVAC17 | HVAC |  | 7 |  |  | 3011 | NA | 14109 | NA | 16416 | 3640 | 0 | EL6021_M181 |  | U8 | 1
EQF6002CA | CMDE "SECOURS INVERSE" TGBT - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | RES | 1 | E | [11 empty] | OFF | E | NO | NF | [14 empty] | E61 |  |  | 4 |  |  | 3000 | NA | 14446 | 0 | 16416 | 4314 | 0 | NA |  | U8 | 0
EQF6002CM | CMDE "SECOURS INVERSE" TGBT - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | RES | 1 | E | [11 empty] | OFF | E | NO | NF | [14 empty] | E61 |  |  | 4 |  |  | 3000 | NA | 14446 | 0 | 16416 | 4314 | 0 | NA |  | U8 | 1
EQF6951CA | CMDE "SECOURS INVERSE" TGBT-C - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | RES | 1 | E | [11 empty] | OFF | E | NO | NF | [14 empty] | E62 |  |  | 4 |  |  | 3001 | NA | 14447 | 0 | 16416 | 4316 | 0 | NA |  | U8 | 0
EQF6951CM | CMDE "SECOURS INVERSE" TGBT-C - U8(2),énergie CAT2(2) / U8(2),énergie CAT1(1) | CT | N | RES | 1 | E | [11 empty] | OFF | E | NO | NF | [14 empty] | E62 |  |  | 4 |  |  | 3001 | NA | 14447 | 0 | 16416 | 4316 | 0 | NA |  | U8 | 1
EWR6091P | TGBT CAT.IIIA Total Active Power P | MA | N | RES | 1 | E |  |  | kW | 0.001 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3170 | NA | 13239 | NA | 16416 | 1900 | 0 | EL6021_M178 |  | I32
EWR6091Q | TGBT CAT.IIIA Total Reactive Power Q | MA | N | RES | 1 | E |  |  | kVAr | 0.001 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3172 | NA | 13241 | NA | 16416 | 1904 | 0 | EL6021_M178 |  | I32
VVU6126CM1 | CMDE INSTALLATION HVAC BUNKER API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3000 | NA | 14448 | 0 | 16416 | 4318 | 0 | NA |  | U8 | 1
VVU6126CA1 | CMDE INSTALLATION HVAC BUNKER API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3000 | NA | 14448 | 0 | 16416 | 4318 | 0 | NA |  | U8 | 0
SPASMA0207 | SPARE SER 0207 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3178 | NA | 13247 | NA | 16416 | 1916 | 0 | EL6021_M178 |  | I32
SPASMA0208 | SPARE SER 0208 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3180 | NA | 13249 | NA | 16416 | 1920 | 0 | EL6021_M178 |  | I32
SPASMA0209 | SPARE SER 0209 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3182 | NA | 13251 | NA | 16416 | 1924 | 0 | EL6021_M178 |  | I32
SPASMA0210 | SPARE SER 0210 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3184 | NA | 13253 | NA | 16416 | 1928 | 0 | EL6021_M178 |  | I32
SPASMA0211 | SPARE SER 0211 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3186 | NA | 13255 | NA | 16416 | 1932 | 0 | EL6021_M178 |  | I32
SPASMA0212 | SPARE SER 0212 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3188 | NA | 13257 | NA | 16416 | 1936 | 0 | EL6021_M178 |  | I32
VVU6126CM3 | CMDE MODE OPE/ECO HVAC BUNKER API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3001 | NA | 14449 | 0 | 16416 | 4320 | 0 | NA |  | U8 | 1
VVU6126CA3 | CMDE MODE OPE/ECO HVAC BUNKER API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3001 | NA | 14449 | 0 | 16416 | 4320 | 0 | NA |  | U8 | 0
VVU6126CM101 | BUNKER API: INFO GANTRY HVAC INSTALLATION - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 6 |  |  | 3002 | NA | 14450 | 0 | 16416 | 4322 | 0 | NA |  | U8 | 1
VVU6126CA101 | BUNKER API: INFO GANTRY HVAC INSTALLATION - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 6 |  |  | 3002 | NA | 14450 | 0 | 16416 | 4322 | 0 | NA |  | U8 | 0
VVU6126CM103 | BUNKER API: INFO MODE OPE/ECO GANTRY HVAC - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 6 |  |  | 3003 | NA | 14451 | 0 | 16416 | 4324 | 0 | NA |  | U8 | 1
VVU6126CA403 | BUNKER API: INFO MODE OPE/ECO GANTRY HVAC - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 6 |  |  | 3003 | NA | 14451 | 0 | 16416 | 4324 | 0 | NA |  | U8 | 0
VZC6126CZ | VEGA BUNKER PLC : CLEARING DEFAULTS | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3004 | NA | 14452 | 0 | 16416 | 4326 | 0 | NA |  | U8 | 1
VVU6126CM4 | BUNKER API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3006 | NA | 14454 | 0 | 16416 | 4330 | 0 | NA |  | U8 | 1
VVU6126CA4 | BUNKER API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3006 | NA | 14454 | 0 | 16416 | 4330 | 0 | NA |  | U8 | 0
VCF6126CF | BUNKER API: DECLENCHEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3007 | NA | 14455 | 0 | 16416 | 4332 | 0 | NA |  | U8 | 1
EWR6092P | TGBT CAT.IIIB Total Active Power P | MA | N | RES | 1 | E |  |  | kW | 0.001 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3210 | NA | 13279 | NA | 16416 | 1980 | 0 | EL6021_M178 |  | I32
EWR6092Q | TGBT CAT.IIIB Total Reactive Power Q | MA | N | RES | 1 | E |  |  | kVAr | 0.001 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3212 | NA | 13281 | NA | 16416 | 1984 | 0 | EL6021_M178 |  | I32
VCF6126CF2 | BUNKER API: DECLENCHEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3007 | NA | 14455 | 0 | 16416 | 4332 | 0 | NA |  | U8 | 0
VCF6126CO | BUNKER API: REARMEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3008 | NA | 14456 | 0 | 16416 | 4334 | 0 | NA |  | U8 | 1
VCF6126CO2 | BUNKER API: REARMEMENT CCF - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3008 | NA | 14456 | 0 | 16416 | 4334 | 0 | NA |  | U8 | 0
VPZ6126CO100 | BUNKER API: PORT HALL GANTRY INFO - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 6 |  |  | 3009 | NA | 14457 | 0 | 16416 | 4336 | 0 | NA |  | U8 | 1
VPZ6126CF100 | BUNKER API: PORT HALL GANTRY INFO - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 6 |  |  | 3009 | NA | 14457 | 0 | 16416 | 4336 | 0 | NA |  | U8 | 0
EUR6071V1 | Onduleur IIIA-1 UL7001 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3233 | NA | 13302 | NA | 16416 | 2026 | 0 | EL6021_M178 |  | UINT
EUR6071V2 | Onduleur IIIA-1 UL7001 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3234 | NA | 13303 | NA | 16416 | 2028 | 0 | EL6021_M178 |  | UINT
EUR6071V3 | Onduleur IIIA-1 UL7001 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3235 | NA | 13304 | NA | 16416 | 2030 | 0 | EL6021_M178 |  | UINT
EUR607112 | Onduleur IIIA-1 UL7001 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3236 | NA | 13305 | NA | 16416 | 2032 | 0 | EL6021_M178 |  | UINT
EUR607123 | Onduleur IIIA-1 UL7001 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3237 | NA | 13306 | NA | 16416 | 2034 | 0 | EL6021_M178 |  | UINT
EUR607131 | Onduleur IIIA-1 UL7001 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3238 | NA | 13307 | NA | 16416 | 2036 | 0 | EL6021_M178 |  | UINT
VVU6126CM2 | BUNKER API: CMD INTERNAL HVAC CTA BUNKER - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3011 | NA | 14459 | 0 | 16416 | 4340 | 0 | NA |  | U8 | 1
EWR6071PF | Onduleur IIIA-1 UL7001 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3240 | NA | 13309 | NA | 16416 | 2040 | 0 | EL6021_M178 |  | UINT
VVU6126CA2 | BUNKER API: CMD INTERNAL HVAC CTA BUNKER - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3011 | NA | 14459 | 0 | 16416 | 4340 | 0 | NA |  | U8 | 0
EDR6071 | Onduleur IIIA-1 UL7001 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3242 | NA | 13311 | NA | 16416 | 2044 | 0 | EL6021_M178 |  | UINT
ETR6071 | Onduleur IIIA-1 UL7001 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3243 | NA | 13312 | NA | 16416 | 2046 | 0 | EL6021_M178 |  | UINT
ENR6071 | Onduleur IIIA-1 UL7001 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3244 | NA | 13313 | NA | 16416 | 2048 | 0 | EL6021_M178 |  | UINT
EWR6071S | Onduleur IIIA-1 UL7001 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3245 | NA | 13314 | NA | 16416 | 2050 | 0 | EL6021_M178 |  | UINT
SPASMA0213 | SPARE SER 0213 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3246 | NA | 13315 | NA | 16416 | 2052 | 0 | EL6021_M178 |  | UINT
SPASMA0214 | SPARE SER 0214 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3247 | NA | 13316 | NA | 16416 | 2054 | 0 | EL6021_M178 |  | UINT
SPASMA0215 | SPARE SER 0215 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3248 | NA | 13317 | NA | 16416 | 2056 | 0 | EL6021_M178 |  | UINT
SPASMA0216 | SPARE SER 0216 | MA | N | RES | [28 empty] | POL | 10000 |  |  | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3249 | NA | 13318 | NA | 16416 | 2058 | 0 | EL6021_M178 |  | UINT
VRP6126CO1 | BUNKER API: CMD PRISE AIR NEUF LOCALE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3016 | NA | 14464 | 0 | 16416 | 4350 | 0 | NA |  | U8 | 1
VRP6126CF1 | BUNKER API: CMD PRISE AIR NEUF LOCALE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3016 | NA | 14464 | 0 | 16416 | 4350 | 0 | NA |  | U8 | 0
VRP6126CO2 | BUNKER API: CMD PRISE AIR NEUF DISTANTE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3017 | NA | 14465 | 0 | 16416 | 4352 | 0 | NA |  | U8 | 1
EUR6072V1 | Onduleur IIIA-2 UL7002 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3253 | NA | 13322 | NA | 16416 | 2066 | 0 | EL6021_M178 |  | UINT
EUR6072V2 | Onduleur IIIA-2 UL7002 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3254 | NA | 13323 | NA | 16416 | 2068 | 0 | EL6021_M178 |  | UINT
EUR6072V3 | Onduleur IIIA-2 UL7002 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3255 | NA | 13324 | NA | 16416 | 2070 | 0 | EL6021_M178 |  | UINT
EUR607212 | Onduleur IIIA-2 UL7002 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3256 | NA | 13325 | NA | 16416 | 2072 | 0 | EL6021_M178 |  | UINT
EUR607223 | Onduleur IIIA-2 UL7002 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3257 | NA | 13326 | NA | 16416 | 2074 | 0 | EL6021_M178 |  | UINT
EUR607231 | Onduleur IIIA-2 UL7002 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3258 | NA | 13327 | NA | 16416 | 2076 | 0 | EL6021_M178 |  | UINT
VRP6126CF2 | BUNKER API: CMD PRISE AIR NEUF DISTANTE - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC12 |  |  | 6 |  |  | 3017 | NA | 14465 | 0 | 16416 | 4352 | 0 | NA |  | U8 | 0
EWR6072PF | Onduleur IIIA-2 UL7002 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3260 | NA | 13329 | NA | 16416 | 2080 | 0 | EL6021_M178 |  | UINT
VVU6401CM1 | CMDE INSTALLATION HVAC GANTRY API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 7 |  |  | 3000 | NA | 14483 | 0 | 16416 | 4388 | 0 | NA |  | U8 | 1
EDR6072 | Onduleur IIIA-2 UL7002 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3262 | NA | 13331 | NA | 16416 | 2084 | 0 | EL6021_M178 |  | UINT
ETR6072 | Onduleur IIIA-2 UL7002 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3263 | NA | 13332 | NA | 16416 | 2086 | 0 | EL6021_M178 |  | UINT
ENR6072 | Onduleur IIIA-2 UL7002 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3264 | NA | 13333 | NA | 16416 | 2088 | 0 | EL6021_M178 |  | UINT
EWR6072S | Onduleur IIIA-2 UL7002 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3265 | NA | 13334 | NA | 16416 | 2090 | 0 | EL6021_M178 |  | UINT
SPASMA0217 | SPARE SER 0217 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3266 | NA | 13335 | NA | 16416 | 2092 | 0 | EL6021_M178 |  | UINT
SPASMA0218 | SPARE SER 0218 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3267 | NA | 13336 | NA | 16416 | 2094 | 0 | EL6021_M178 |  | UINT
SPASMA0219 | SPARE SER 0219 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3268 | NA | 13337 | NA | 16416 | 2096 | 0 | EL6021_M178 |  | UINT
SPASMA0220 | SPARE SER 0220 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3269 | NA | 13338 | NA | 16416 | 2098 | 0 | EL6021_M178 |  | UINT
VVU6401CA1 | CMDE INSTALLATION HVAC GANTRY API - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 7 |  |  | 3000 | NA | 14483 | 0 | 16416 | 4388 | 0 | NA |  | U8 | 0
VVU6401CM3 | CMDE MODE OPE/ECO HVAC GANTRY API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 7 |  |  | 3001 | NA | 14484 | 0 | 16416 | 4390 | 0 | NA |  | U8 | 1
VVU6401CA3 | CMDE MODE OPE/ECO HVAC GANTRY API - U8(2),MODE ECO(2) / U8(2),MODE OPE(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 7 |  |  | 3001 | NA | 14484 | 0 | 16416 | 4390 | 0 | NA |  | U8 | 0
EUR6073V1 | Onduleur IIIB-1 UL7003 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3273 | NA | 13342 | NA | 16416 | 2106 | 0 | EL6021_M178 |  | UINT
EUR6073V2 | Onduleur IIIB-1 UL7003 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3274 | NA | 13343 | NA | 16416 | 2108 | 0 | EL6021_M178 |  | UINT
EUR6073V3 | Onduleur IIIB-1 UL7003 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3275 | NA | 13344 | NA | 16416 | 2110 | 0 | EL6021_M178 |  | UINT
EUR607312 | Onduleur IIIB-1 UL7003 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3276 | NA | 13345 | NA | 16416 | 2112 | 0 | EL6021_M178 |  | UINT
EUR607323 | Onduleur IIIB-1 UL7003 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3277 | NA | 13346 | NA | 16416 | 2114 | 0 | EL6021_M178 |  | UINT
EUR607331 | Onduleur IIIB-1 UL7003 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3278 | NA | 13347 | NA | 16416 | 2116 | 0 | EL6021_M178 |  | UINT
VZC6401CZ | VEGA GANTRY PLC : CLEARING DEFAULTS | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3004 | NA | 14487 | 0 | 16416 | 4396 | 0 | NA |  | U8 | 1
EWR6073PF | Onduleur IIIB-1 UL7003 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3280 | NA | 13349 | NA | 16416 | 2120 | 0 | EL6021_M178 |  | UINT
VPZ6999CO | GANTRY API: CMDE PORTE HALL GANTRY - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 7 |  |  | 3005 | NA | 14488 | 0 | 16416 | 4398 | 0 | NA |  | U8 | 1
EDR6073 | Onduleur IIIB-1 UL7003 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3282 | NA | 13351 | NA | 16416 | 2124 | 0 | EL6021_M178 |  | UINT
ETR6073 | Onduleur IIIB-1 UL7003 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3283 | NA | 13352 | NA | 16416 | 2126 | 0 | EL6021_M178 |  | UINT
ENR6073 | Onduleur IIIB-1 UL7003 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3284 | NA | 13353 | NA | 16416 | 2128 | 0 | EL6021_M178 |  | UINT
EWR6073S | Onduleur IIIB-1 UL7003 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3285 | NA | 13354 | NA | 16416 | 2130 | 0 | EL6021_M178 |  | UINT
SPASMA0221 | SPARE SER 0221 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3286 | NA | 13355 | NA | 16416 | 2132 | 0 | EL6021_M178 |  | UINT
SPASMA0222 | SPARE SER 0222 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3287 | NA | 13356 | NA | 16416 | 2134 | 0 | EL6021_M178 |  | UINT
SPASMA0223 | SPARE SER 0223 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3288 | NA | 13357 | NA | 16416 | 2136 | 0 | EL6021_M178 |  | UINT
SPASMA1047 | SPARE SER 0224 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3289 | NA | 13358 | NA | 16416 | 2138 | 0 | EL6021_M178 |  | UINT
VPZ6999CF | GANTRY API: CMDE PORTE HALL GANTRY - U8(2),OUVRIR(2) / U8(2)FERMER(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [18 empty] | 7 |  |  | 3005 | NA | 14488 | 0 | 16416 | 4398 | 0 | NA |  | U8 | 0
VZN6701CM | GANTRY API: REMPLISSAGE N2O4 - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3006 | NA | 14489 | 0 | 16416 | 4400 | 0 | NA |  | U8 | 1
VZN6701CA | GANTRY API: REMPLISSAGE N2O4 - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3006 | NA | 14489 | 0 | 16416 | 4400 | 0 | NA |  | U8 | 0
EUR6074V1 | Onduleur IIIB-2 UL7004 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3293 | NA | 13362 | NA | 16416 | 2146 | 0 | EL6021_M178 |  | UINT
EUR6074V2 | Onduleur IIIB-2 UL7004 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3294 | NA | 13363 | NA | 16416 | 2148 | 0 | EL6021_M178 |  | UINT
EUR6074V3 | Onduleur IIIB-2 UL7004 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3295 | NA | 13364 | NA | 16416 | 2150 | 0 | EL6021_M178 |  | UINT
EUR607412 | Onduleur IIIB-2 UL7004 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3296 | NA | 13365 | NA | 16416 | 2152 | 0 | EL6021_M178 |  | UINT
EUR607423 | Onduleur IIIB-2 UL7004 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3297 | NA | 13366 | NA | 16416 | 2154 | 0 | EL6021_M178 |  | UINT
EUR607431 | Onduleur IIIB-2 UL7004 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3298 | NA | 13367 | NA | 16416 | 2156 | 0 | EL6021_M178 |  | UINT
VZU6601CM | GANTRY API: REMPLISSAGE UDMH - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3007 | NA | 14490 | 0 | 16416 | 4402 | 0 | NA |  | U8 | 1
EWR6074PF | Onduleur IIIB-2 UL7004 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3300 | NA | 13369 | NA | 16416 | 2160 | 0 | EL6021_M178 |  | UINT
VZU6601CA | GANTRY API: REMPLISSAGE UDMH - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3007 | NA | 14490 | 0 | 16416 | 4402 | 0 | NA |  | U8 | 0
EDR6074 | Onduleur IIIB-2 UL7004 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3302 | NA | 13371 | NA | 16416 | 2164 | 0 | EL6021_M178 |  | UINT
ETR6074 | Onduleur IIIB-2 UL7004 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3303 | NA | 13372 | NA | 16416 | 2166 | 0 | EL6021_M178 |  | UINT
ENR6074 | Onduleur IIIB-2 UL7004 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3304 | NA | 13373 | NA | 16416 | 2168 | 0 | EL6021_M178 |  | UINT
EWR6074S | Onduleur IIIB-2 UL7004 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3305 | NA | 13374 | NA | 16416 | 2170 | 0 | EL6021_M178 |  | UINT
SPASMA1048 | SPARE SER 0225 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3306 | NA | 13375 | NA | 16416 | 2172 | 0 | EL6021_M178 |  | UINT
SPASMA1049 | SPARE SER 0226 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3307 | NA | 13376 | NA | 16416 | 2174 | 0 | EL6021_M178 |  | UINT
SPASMA1050 | SPARE SER 0227 | MA | N | RES | [28 empty] | POL | [5 empty] | 4 |  |  | 3308 | NA | 13377 | NA | 16416 | 2176 | 0 | EL6021_M178 |  | UINT
SPASMA1051 | SPARE SER 0228 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3309 | NA | 13378 | NA | 16416 | 2178 | 0 | EL6021_M178 |  | UINT
VVU6401CM4 | GANTRY API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3008 | NA | 14491 | 0 | 16416 | 4404 | 0 | NA |  | U8 | 1
VVU6401CA4 | GANTRY API: VERROUILLAGE CONFIG (D-1) - U8(2),ON(2) / U8(2),OFF(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3008 | NA | 14491 | 0 | 16416 | 4404 | 0 | NA |  | U8 | 0
VVU6401CM2 | GANTRY API: CMD CLIM INTERNE HVAC - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3011 | NA | 14494 | 0 | 16416 | 4410 | 0 | NA |  | U8 | 1
EUR6075V1 | Onduleur III CUB UL7005 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3313 | NA | 13382 | NA | 16416 | 2186 | 0 | EL6021_M178 |  | UINT
EUR6075V2 | Onduleur III CUB UL7005 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3314 | NA | 13383 | NA | 16416 | 2188 | 0 | EL6021_M178 |  | UINT
EUR6075V3 | Onduleur III CUB UL7005 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3315 | NA | 13384 | NA | 16416 | 2190 | 0 | EL6021_M178 |  | UINT
EUR607512 | Onduleur III CUB UL7005 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3316 | NA | 13385 | NA | 16416 | 2192 | 0 | EL6021_M178 |  | UINT
EUR607523 | Onduleur III CUB UL7005 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3317 | NA | 13386 | NA | 16416 | 2194 | 0 | EL6021_M178 |  | UINT
EUR607531 | Onduleur III CUB UL7005 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3318 | NA | 13387 | NA | 16416 | 2196 | 0 | EL6021_M178 |  | UINT
VVU6401CA2 | GANTRY API: CMD CLIM INTERNE HVAC - U8(2),MARCHE(2) / U8(2),ARRET(1) | CT | N | RES | 1 | C | [12 empty] | C | NO | [15 empty] | HVAC17 |  |  | 7 |  |  | 3011 | NA | 14494 | 0 | 16416 | 4410 | 0 | NA |  | U8 | 0
EWR6075PF | Onduleur III CUB UL7005 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3320 | NA | 13389 | NA | 16416 | 2200 | 0 | EL6021_M178 |  | UINT
QKO6000CM | CMDE ACQUISITION CAPTEURS SHM - BIT(0),MARCHE(1) / BIT(0),ARRET(0) | CT | N | TIP | 1 | H | [12 empty] | H | NO | [12 empty] | SHM |  |  | SHM60 | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 10 | [8 empty] | BIT | 1
EDR6075 | Onduleur III CUB UL7005 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3322 | NA | 13391 | NA | 16416 | 2204 | 0 | EL6021_M178 |  | UINT
ETR6075 | Onduleur III CUB UL7005 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3323 | NA | 13392 | NA | 16416 | 2206 | 0 | EL6021_M178 |  | UINT
ENR6075 | Onduleur III CUB UL7005 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3324 | NA | 13393 | NA | 16416 | 2208 | 0 | EL6021_M178 |  | UINT
EWR6075S | Onduleur III CUB UL7005 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3325 | NA | 13394 | NA | 16416 | 2210 | 0 | EL6021_M178 |  | UINT
SPASMA1052 | SPARE SER 0229 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3326 | NA | 13395 | NA | 16416 | 2212 | 0 | EL6021_M178 |  | UINT
SPASMA1053 | SPARE SER 0230 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3327 | NA | 13396 | NA | 16416 | 2214 | 0 | EL6021_M178 |  | UINT
SPASMA1054 | SPARE SER 0231 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3328 | NA | 13397 | NA | 16416 | 2216 | 0 | EL6021_M178 |  | UINT
SPASMA1055 | SPARE SER 0232 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3329 | NA | 13398 | NA | 16416 | 2218 | 0 | EL6021_M178 |  | UINT
QKO6000CA | CMDE ACQUISITION CAPTEURS SHM - BIT(0),MARCHE(1) / BIT(0),ARRET(0) | CT | N | TIP | 1 | H | [12 empty] | H | NO | [12 empty] | SHM |  |  | SHM60 | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 10 | [8 empty] | BIT | 0
VVU6CM1GC | VEGA GANTRY PLC : STARTING HVAC INSTALLATION | CT | N | INT | 1 | C | [12 empty] | C | NO |  |  | VVU6401CM1 VVU6126CM401 | [12 empty] | HVAC17 | [14 empty] | U8 | 2
VVU6CA1GC | VEGA GANTRY PLC : STOPPINGING HVAC INSTALLATION | CT | N | INT | 1 | C | [12 empty] | C | NO |  |  | VVU6401CA1 VVU6126CA401 | [27 empty] | U8 | 1
EUR6076V1 | Onduleur III CUH UL7006 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3333 | NA | 13402 | NA | 16416 | 2226 | 0 | EL6021_M178 |  | UINT
EUR6076V2 | Onduleur III CUH UL7006 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3334 | NA | 13403 | NA | 16416 | 2228 | 0 | EL6021_M178 |  | UINT
EUR6076V3 | Onduleur III CUH UL7006 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3335 | NA | 13404 | NA | 16416 | 2230 | 0 | EL6021_M178 |  | UINT
EUR607612 | Onduleur III CUH UL7006 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3336 | NA | 13405 | NA | 16416 | 2232 | 0 | EL6021_M178 |  | UINT
EUR607623 | Onduleur III CUH UL7006 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3337 | NA | 13406 | NA | 16416 | 2234 | 0 | EL6021_M178 |  | UINT
EUR607631 | Onduleur III CUH UL7006 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3338 | NA | 13407 | NA | 16416 | 2236 | 0 | EL6021_M178 |  | UINT
VVU6CM3GC | VEGA GANTRY PLC : OPERATING IN ECO MODE ON | CT | N | INT | 1 | C | [12 empty] | C | NO |  |  | VVU6401CM3 VVU6126CM103 | [12 empty] | HVAC17 | [14 empty] | U8 | 2
EWR6076PF | Onduleur III CUH UL7006 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3340 | NA | 13409 | NA | 16416 | 2240 | 0 | EL6021_M178 |  | UINT
VVU6CA3GC | VEGA GANTRY PLC : OPERATING IN ECO MODE OFF | CT | N | INT | 1 | C | [12 empty] | C | NO |  |  | VVU6401CA3 VVU6126CA403 | [27 empty] | U8 | 1
EDR6076 | Onduleur III CUH UL7006 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3342 | NA | 13411 | NA | 16416 | 2244 | 0 | EL6021_M178 |  | UINT
ETR6076 | Onduleur III CUH UL7006 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3343 | NA | 13412 | NA | 16416 | 2246 | 0 | EL6021_M178 |  | UINT
ENR6076 | Onduleur III CUH UL7006 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3344 | NA | 13413 | NA | 16416 | 2248 | 0 | EL6021_M178 |  | UINT
EWR6076S | Onduleur III CUH UL7006 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [20 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3345 | NA | 13414 | NA | 16416 | 2250 | 0 | EL6021_M178 |  | UINT
SPASMA1056 | SPARE SER 0233 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3346 | NA | 13415 | NA | 16416 | 2252 | 0 | EL6021_M178 |  | UINT
SPASMA1057 | SPARE SER 0234 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3347 | NA | 13416 | NA | 16416 | 2254 | 0 | EL6021_M178 |  | UINT
SPASMA1058 | SPARE SER 0235 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3348 | NA | 13417 | NA | 16416 | 2256 | 0 | EL6021_M178 |  | UINT
SPASMA1059 | SPARE SER 0236 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 3349 | NA | 13418 | NA | 16416 | 2258 | 0 | EL6021_M178 |  | UINT
VPZ6CO1GC | VEGA GANTRY PLC : OPENNING HALL DOOR | CT | N | INT | 1 | C | [12 empty] | C | NO |  |  | VPZ6999CO VPZ6126CO401 | [12 empty] | HVAC17 | [14 empty] | U8 | 2
VPZ6CF1GC | VEGA GANTRY PLC : CLOSING HALL DOOR | CT | N | INT | 1 | C | [12 empty] | C | NO |  |  | VPZ6999CF VPZ6126CF401 | [27 empty] | U8 | 1
VRU7232CF | CMDE FERMETURE INCENDIE HVAC QE HVAC 184-20-32 - BIT(0),MARCHE(1) / BIT(0),ARRET(0) | CT | O | FIL | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 52 | NA | [7 empty] | BIT | 1
EUR6077V1 | Frequency Converter UL7007 Output phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3353 | NA | 13422 | NA | 16416 | 2266 | 0 | EL6021_M178 |  | UINT
EUR6077V2 | Frequency Converter UL7007 Output phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3354 | NA | 13423 | NA | 16416 | 2268 | 0 | EL6021_M178 |  | UINT
EUR6077V3 | Frequency Converter UL7007 Output phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3355 | NA | 13424 | NA | 16416 | 2270 | 0 | EL6021_M178 |  | UINT
EUR607712 | Frequency Converter UL7007 Output line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3356 | NA | 13425 | NA | 16416 | 2272 | 0 | EL6021_M178 |  | UINT
EUR607723 | Frequency Converter UL7007 Output line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3357 | NA | 13426 | NA | 16416 | 2274 | 0 | EL6021_M178 |  | UINT
EUR607731 | Frequency Converter UL7007 Output line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3358 | NA | 13427 | NA | 16416 | 2276 | 0 | EL6021_M178 |  | UINT
VRU7232CO | CMDE FERMETURE INCENDIE HVAC QE HVAC 184-20-32 - BIT(0),MARCHE(1) / BIT(0),ARRET(0) | CT | O | FIL | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 52 | NA | [7 empty] | BIT | 0
EWR6077PF | Frequency Converter UL7007 Output power factor (x100) | MA | N | RES | 1 | E |  |  | NA | 1 | 0 | 65535 | [14 empty] | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3360 | NA | 13429 | NA | 16416 | 2280 | 0 | EL6021_M178 |  | UINT
VRU7120CF | CMDE FERMETURE INCENDIE HVAC QE TGBT 184-13-20 - BIT(0),MARCHE(1) / BIT(0),ARRET(0) | CT | O | FIL | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 53 | NA | [7 empty] | BIT | 1
EDR6077 | Frequency Converter UL7007 Battery remaining runtime | MA | N | RES | 1 | E |  |  | min | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3362 | NA | 13431 | NA | 16416 | 2284 | 0 | EL6021_M178 |  | UINT
ETR6077 | Frequency Converter UL7007 Battery temperature | MA | N | RES | 1 | E |  |  | °C | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3363 | NA | 13432 | NA | 16416 | 2286 | 0 | EL6021_M178 |  | UINT
ENR6077 | Frequency Converter UL7007 Battery remaining capacity | MA | N | RES | 1 | E |  |  | % | 1 | 0 | 100 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3364 | NA | 13433 | NA | 16416 | 2288 | 0 | EL6021_M178 |  | UINT
EWR6077S | Frequency Converter UL7007 Nominal output apparent power UPS | MA | N | RES | 1 | E |  |  | kVA | 1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3365 | NA | 13434 | NA | 16416 | 2290 | 0 | EL6021_M178 |  | UINT
EZC6115 | PLC TGBT Watchdog | MA | N | RES | 1 | A |  |  | A |  | 0 | 65535 |  |  | 0 | 32767 | [16 empty] | POL | 6000 |  | E61;E62;E63;E64;E65 | Energie TGBT et UPS (E) |  | 4 |  |  | 4000 | NA | 13439 | NA | 16416 | 2300 | 0 | EL6021_M178 |  | UINT
EIR6101I1 | TD 013 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5000 | NA | 15200 | 0 | 16416 | 5822 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6101I2 | TD 013 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5002 | NA | 15202 | 0 | 16416 | 5826 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6101I3 | TD 013 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5004 | NA | 15204 | 0 | 16416 | 5830 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6101IN | TD 013 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5006 | NA | 15206 | 0 | 16416 | 5834 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610112 | TD 013 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5008 | NA | 15208 | 0 | 16416 | 5838 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610123 | TD 013 IIIA Line to line voltage U23(CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5010 | NA | 15210 | 0 | 16416 | 5842 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610131 | TD 013 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5012 | NA | 15212 | 0 | 16416 | 5846 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6101V1 | TD 013 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5014 | NA | 15214 | 0 | 16416 | 5850 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6101V2 | TD 013 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5016 | NA | 15216 | 0 | 16416 | 5854 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6101V3 | TD 013 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5018 | NA | 15218 | 0 | 16416 | 5858 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6101PF | TD 013 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5020 | NA | 15220 | 0 | 16416 | 5862 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6101 | TD 013 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6101D | TD 1601-013-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5022 | NA | 15222 | 0 | 16416 | 5866 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1060 | SPARE SER 0237 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5024 | NA | 15224 | 0 | 16416 | 5870 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1061 | SPARE SER 0238 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5026 | NA | 15226 | 0 | 16416 | 5874 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1062 | SPARE SER 0239 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5028 | NA | 15228 | 0 | 16416 | 5878 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1063 | SPARE SER 0240 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5030 | NA | 15230 | 0 | 16416 | 5882 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1064 | SPARE SER 0241 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5032 | NA | 15232 | 0 | 16416 | 5886 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1065 | SPARE SER 0242 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5034 | NA | 15234 | 0 | 16416 | 5890 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1066 | SPARE SER 0243 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5036 | NA | 15236 | 0 | 16416 | 5894 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1067 | SPARE SER 0244 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5038 | NA | 15238 | 0 | 16416 | 5898 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6102I1 | TD 013 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5040 | NA | 15240 | 0 | 16416 | 5902 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6102I2 | TD 013 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5042 | NA | 15242 | 0 | 16416 | 5906 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6102I3 | TD 013 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5044 | NA | 15244 | 0 | 16416 | 5910 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6102IN | TD 013 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5046 | NA | 15246 | 0 | 16416 | 5914 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610212 | TD 013 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5048 | NA | 15248 | 0 | 16416 | 5918 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610223 | TD 013 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5050 | NA | 15250 | 0 | 16416 | 5922 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610231 | TD 013 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5052 | NA | 15252 | 0 | 16416 | 5926 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6102V1 | TD 013 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5054 | NA | 15254 | 0 | 16416 | 5930 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6102V2 | TD 013 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5056 | NA | 15256 | 0 | 16416 | 5934 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6102V3 | TD 013 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5058 | NA | 15258 | 0 | 16416 | 5938 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6102PF | TD 013 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5060 | NA | 15260 | 0 | 16416 | 5942 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6102 | TD 013 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6102D | TD 1601-013-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5062 | NA | 15262 | 0 | 16416 | 5946 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1068 | SPARE SER 0245 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5064 | NA | 15264 | 0 | 16416 | 5950 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1069 | SPARE SER 0246 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5066 | NA | 15266 | 0 | 16416 | 5954 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1070 | SPARE SER 0247 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5068 | NA | 15268 | 0 | 16416 | 5958 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1071 | SPARE SER 0248 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5070 | NA | 15270 | 0 | 16416 | 5962 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1072 | SPARE SER 0249 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5072 | NA | 15272 | 0 | 16416 | 5966 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1073 | SPARE SER 0250 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5074 | NA | 15274 | 0 | 16416 | 5970 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1074 | SPARE SER 0251 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5076 | NA | 15276 | 0 | 16416 | 5974 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1075 | SPARE SER 0252 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5078 | NA | 15278 | 0 | 16416 | 5978 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6103I1 | TD1 004 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5080 | NA | 15280 | 0 | 16416 | 5982 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6103I2 | TD1 004 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5082 | NA | 15282 | 0 | 16416 | 5986 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6103I3 | TD1 004 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5084 | NA | 15284 | 0 | 16416 | 5990 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6103IN | TD1 004 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5086 | NA | 15286 | 0 | 16416 | 5994 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610312 | TD1 004 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5088 | NA | 15288 | 0 | 16416 | 5998 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610323 | TD1 004 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5090 | NA | 15290 | 0 | 16416 | 6002 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610331 | TD1 004 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5092 | NA | 15292 | 0 | 16416 | 6006 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6103V1 | TD1 004 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5094 | NA | 15294 | 0 | 16416 | 6010 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6103V2 | TD1 004 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5096 | NA | 15296 | 0 | 16416 | 6014 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6103V3 | TD1 004 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5098 | NA | 15298 | 0 | 16416 | 6018 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6103PF | TD1 004 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5100 | NA | 15300 | 0 | 16416 | 6022 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6103 | TD1 004 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6103D | TD1 1601-004-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5102 | NA | 15302 | 0 | 16416 | 6026 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1076 | SPARE SER 0253 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5104 | NA | 15304 | 0 | 16416 | 6030 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1077 | SPARE SER 0254 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5106 | NA | 15306 | 0 | 16416 | 6034 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1078 | SPARE SER 0255 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5108 | NA | 15308 | 0 | 16416 | 6038 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1079 | SPARE SER 0256 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5110 | NA | 15310 | 0 | 16416 | 6042 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1080 | SPARE SER 0257 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5112 | NA | 15312 | 0 | 16416 | 6046 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1081 | SPARE SER 0258 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5114 | NA | 15314 | 0 | 16416 | 6050 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1082 | SPARE SER 0259 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5116 | NA | 15316 | 0 | 16416 | 6054 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1083 | SPARE SER 0260 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5118 | NA | 15318 | 0 | 16416 | 6058 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6104I1 | TD2 004 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5120 | NA | 15320 | 0 | 16416 | 6062 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6104I2 | TD2 004 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5122 | NA | 15322 | 0 | 16416 | 6066 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6104I3 | TD2 004 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5124 | NA | 15324 | 0 | 16416 | 6070 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6104IN | TD2 004 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5126 | NA | 15326 | 0 | 16416 | 6074 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610412 | TD2 004 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5128 | NA | 15328 | 0 | 16416 | 6078 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610423 | TD2 004 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5130 | NA | 15330 | 0 | 16416 | 6082 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610431 | TD2 004 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5132 | NA | 15332 | 0 | 16416 | 6086 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6104V1 | TD2 004 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5134 | NA | 15334 | 0 | 16416 | 6090 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6104V2 | TD2 004 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5136 | NA | 15336 | 0 | 16416 | 6094 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6104V3 | TD2 004 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5138 | NA | 15338 | 0 | 16416 | 6098 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6104PF | TD2 004 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5140 | NA | 15340 | 0 | 16416 | 6102 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6104 | TD2 004 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6104D | TD2 1601-004-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5142 | NA | 15342 | 0 | 16416 | 6106 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1084 | SPARE SER 0261 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5144 | NA | 15344 | 0 | 16416 | 6110 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1085 | SPARE SER 0262 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5146 | NA | 15346 | 0 | 16416 | 6114 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1086 | SPARE SER 0263 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5148 | NA | 15348 | 0 | 16416 | 6118 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1087 | SPARE SER 0264 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5150 | NA | 15350 | 0 | 16416 | 6122 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1088 | SPARE SER 0265 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5152 | NA | 15352 | 0 | 16416 | 6126 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1089 | SPARE SER 0266 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5154 | NA | 15354 | 0 | 16416 | 6130 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1090 | SPARE SER 0267 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5156 | NA | 15356 | 0 | 16416 | 6134 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1091 | SPARE SER 0268 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5158 | NA | 15358 | 0 | 16416 | 6138 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6105I1 | TD1 004 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5160 | NA | 15360 | 0 | 16416 | 6142 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6105I2 | TD1 004 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5162 | NA | 15362 | 0 | 16416 | 6146 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6105I3 | TD1 004 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5164 | NA | 15364 | 0 | 16416 | 6150 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6105IN | TD1 004 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5166 | NA | 15366 | 0 | 16416 | 6154 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610512 | TD1 004 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5168 | NA | 15368 | 0 | 16416 | 6158 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610523 | TD1 004 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5170 | NA | 15370 | 0 | 16416 | 6162 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610531 | TD1 004 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5172 | NA | 15372 | 0 | 16416 | 6166 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6105V1 | TD1 004 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5174 | NA | 15374 | 0 | 16416 | 6170 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6105V2 | TD1 004 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5176 | NA | 15376 | 0 | 16416 | 6174 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6105V3 | TD1 004 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5178 | NA | 15378 | 0 | 16416 | 6178 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6105PF | TD1 004 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5180 | NA | 15380 | 0 | 16416 | 6182 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6105 | TD1 004 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6105D | TD1 1601-004-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5182 | NA | 15382 | 0 | 16416 | 6186 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1092 | SPARE SER 0269 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5184 | NA | 15384 | 0 | 16416 | 6190 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1093 | SPARE SER 0270 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5186 | NA | 15386 | 0 | 16416 | 6194 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1094 | SPARE SER 0271 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5188 | NA | 15388 | 0 | 16416 | 6198 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1095 | SPARE SER 0272 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5190 | NA | 15390 | 0 | 16416 | 6202 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1096 | SPARE SER 0273 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5192 | NA | 15392 | 0 | 16416 | 6206 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1097 | SPARE SER 0274 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5194 | NA | 15394 | 0 | 16416 | 6210 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1098 | SPARE SER 0275 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5196 | NA | 15396 | 0 | 16416 | 6214 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1099 | SPARE SER 0276 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5198 | NA | 15398 | 0 | 16416 | 6218 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6106I1 | TD2 004 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5200 | NA | 15400 | 0 | 16416 | 6222 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6106I2 | TD2 004 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5202 | NA | 15402 | 0 | 16416 | 6226 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6106I3 | TD2 004 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5204 | NA | 15404 | 0 | 16416 | 6230 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6106IN | TD2 004 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5206 | NA | 15406 | 0 | 16416 | 6234 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610612 | TD2 004 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5208 | NA | 15408 | 0 | 16416 | 6238 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610623 | TD2 004 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5210 | NA | 15410 | 0 | 16416 | 6242 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610631 | TD2 004 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5212 | NA | 15412 | 0 | 16416 | 6246 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6106V1 | TD2 004 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5214 | NA | 15414 | 0 | 16416 | 6250 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6106V2 | TD2 004 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5216 | NA | 15416 | 0 | 16416 | 6254 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6106V3 | TD2 004 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5218 | NA | 15418 | 0 | 16416 | 6258 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6106PF | TD2 004 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5220 | NA | 15420 | 0 | 16416 | 6262 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6106 | TD2 004 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6106D | TD2 1601-004-34 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5222 | NA | 15422 | 0 | 16416 | 6266 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1100 | SPARE SER 0277 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5224 | NA | 15424 | 0 | 16416 | 6270 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1101 | SPARE SER 0278 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5226 | NA | 15426 | 0 | 16416 | 6274 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1102 | SPARE SER 0279 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5228 | NA | 15428 | 0 | 16416 | 6278 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1103 | SPARE SER 0280 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5230 | NA | 15430 | 0 | 16416 | 6282 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1104 | SPARE SER 0281 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5232 | NA | 15432 | 0 | 16416 | 6286 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1105 | SPARE SER 0282 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5234 | NA | 15434 | 0 | 16416 | 6290 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1106 | SPARE SER 0283 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5236 | NA | 15436 | 0 | 16416 | 6294 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1107 | SPARE SER 0284 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5238 | NA | 15438 | 0 | 16416 | 6298 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6107I1 | TD1 103 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5240 | NA | 15440 | 0 | 16416 | 6302 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6107I2 | TD1 103 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5242 | NA | 15442 | 0 | 16416 | 6306 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6107I3 | TD1 103 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5244 | NA | 15444 | 0 | 16416 | 6310 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6107IN | TD1 103 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5246 | NA | 15446 | 0 | 16416 | 6314 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610712 | TD1 103 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5248 | NA | 15448 | 0 | 16416 | 6318 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610723 | TD1 103 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5250 | NA | 15450 | 0 | 16416 | 6322 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610731 | TD1 103 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5252 | NA | 15452 | 0 | 16416 | 6326 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6107V1 | TD1 103 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5254 | NA | 15454 | 0 | 16416 | 6330 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6107V2 | TD1 103 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5256 | NA | 15456 | 0 | 16416 | 6334 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6107V3 | TD1 103 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5258 | NA | 15458 | 0 | 16416 | 6338 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6107PF | TD1 103 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5260 | NA | 15460 | 0 | 16416 | 6342 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6107 | TD1 103 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6107D | TD1 1601-103-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5262 | NA | 15462 | 0 | 16416 | 6346 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1108 | SPARE SER 0285 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5264 | NA | 15464 | 0 | 16416 | 6350 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1109 | SPARE SER 0286 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5266 | NA | 15466 | 0 | 16416 | 6354 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1110 | SPARE SER 0287 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5268 | NA | 15468 | 0 | 16416 | 6358 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1111 | SPARE SER 0288 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5270 | NA | 15470 | 0 | 16416 | 6362 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1112 | SPARE SER 0289 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5272 | NA | 15472 | 0 | 16416 | 6366 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1113 | SPARE SER 0290 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5274 | NA | 15474 | 0 | 16416 | 6370 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1114 | SPARE SER 0291 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5276 | NA | 15476 | 0 | 16416 | 6374 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1115 | SPARE SER 0292 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5278 | NA | 15478 | 0 | 16416 | 6378 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6108I1 | TD2 103 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5280 | NA | 15480 | 0 | 16416 | 6382 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6108I2 | TD2 103 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5282 | NA | 15482 | 0 | 16416 | 6386 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6108I3 | TD2 103 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5284 | NA | 15484 | 0 | 16416 | 6390 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6108IN | TD2 103 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5286 | NA | 15486 | 0 | 16416 | 6394 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610812 | TD2 103 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5288 | NA | 15488 | 0 | 16416 | 6398 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610823 | TD2 103 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5290 | NA | 15490 | 0 | 16416 | 6402 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610831 | TD2 103 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5292 | NA | 15492 | 0 | 16416 | 6406 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6108V1 | TD2 103 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5294 | NA | 15494 | 0 | 16416 | 6410 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6108V2 | TD2 103 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5296 | NA | 15496 | 0 | 16416 | 6414 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6108V3 | TD2 103 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5298 | NA | 15498 | 0 | 16416 | 6418 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6108PF | TD2 103 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5300 | NA | 15500 | 0 | 16416 | 6422 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6108 | TD2 103 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6108D | TD2 1601-103-32 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5302 | NA | 15502 | 0 | 16416 | 6426 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1116 | SPARE SER 0293 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5304 | NA | 15504 | 0 | 16416 | 6430 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1117 | SPARE SER 0294 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5306 | NA | 15506 | 0 | 16416 | 6434 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1118 | SPARE SER 0295 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5308 | NA | 15508 | 0 | 16416 | 6438 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1119 | SPARE SER 0296 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5310 | NA | 15510 | 0 | 16416 | 6442 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1120 | SPARE SER 0297 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5312 | NA | 15512 | 0 | 16416 | 6446 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1121 | SPARE SER 0298 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5314 | NA | 15514 | 0 | 16416 | 6450 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1122 | SPARE SER 0299 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5316 | NA | 15516 | 0 | 16416 | 6454 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1123 | SPARE SER 0300 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5318 | NA | 15518 | 0 | 16416 | 6458 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6109I1 | TD3 103 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5320 | NA | 15520 | 0 | 16416 | 6462 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6109I2 | TD3 103 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5322 | NA | 15522 | 0 | 16416 | 6466 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6109I3 | TD3 103 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5324 | NA | 15524 | 0 | 16416 | 6470 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6109IN | TD3 103 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5326 | NA | 15526 | 0 | 16416 | 6474 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610912 | TD3 103 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5328 | NA | 15528 | 0 | 16416 | 6478 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610923 | TD3 103 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5330 | NA | 15530 | 0 | 16416 | 6482 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR610931 | TD3 103 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5332 | NA | 15532 | 0 | 16416 | 6486 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6109V1 | TD3 103 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5334 | NA | 15534 | 0 | 16416 | 6490 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6109V2 | TD3 103 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5336 | NA | 15536 | 0 | 16416 | 6494 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6109V3 | TD3 103 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5338 | NA | 15538 | 0 | 16416 | 6498 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6109PF | TD3 103 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5340 | NA | 15540 | 0 | 16416 | 6502 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6109 | TD3 103 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6109D | TD3 1601-103-34 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5342 | NA | 15542 | 0 | 16416 | 6506 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1124 | SPARE SER 0301 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5344 | NA | 15544 | 0 | 16416 | 6510 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1125 | SPARE SER 0302 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5346 | NA | 15546 | 0 | 16416 | 6514 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA1126 | SPARE SER 0303 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5348 | NA | 15548 | 0 | 16416 | 6518 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0304 | SPARE SER 0304 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5350 | NA | 15550 | 0 | 16416 | 6522 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0305 | SPARE SER 0305 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5352 | NA | 15552 | 0 | 16416 | 6526 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0306 | SPARE SER 0306 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5354 | NA | 15554 | 0 | 16416 | 6530 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0307 | SPARE SER 0307 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5356 | NA | 15556 | 0 | 16416 | 6534 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0308 | SPARE SER 0308 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5358 | NA | 15558 | 0 | 16416 | 6538 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6110I1 | TD4 103 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5360 | NA | 15560 | 0 | 16416 | 6542 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6110I2 | TD4 103 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5362 | NA | 15562 | 0 | 16416 | 6546 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6110I3 | TD4 103 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5364 | NA | 15564 | 0 | 16416 | 6550 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6110IN | TD4 103 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5366 | NA | 15566 | 0 | 16416 | 6554 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611012 | TD4 103 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5368 | NA | 15568 | 0 | 16416 | 6558 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611023 | TD4 103 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5370 | NA | 15570 | 0 | 16416 | 6562 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611031 | TD4 103 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5372 | NA | 15572 | 0 | 16416 | 6566 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6110V1 | TD4 103 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5374 | NA | 15574 | 0 | 16416 | 6570 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6110V2 | TD4 103 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5376 | NA | 15576 | 0 | 16416 | 6574 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6110V3 | TD4 103 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5378 | NA | 15578 | 0 | 16416 | 6578 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6110PF | TD4 103 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5380 | NA | 15580 | 0 | 16416 | 6582 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6110 | TD4 103 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6110D | TD4 1601-103-36 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5382 | NA | 15582 | 0 | 16416 | 6586 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0309 | SPARE SER 0309 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5384 | NA | 15584 | 0 | 16416 | 6590 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0310 | SPARE SER 0310 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5386 | NA | 15586 | 0 | 16416 | 6594 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0311 | SPARE SER 0311 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5388 | NA | 15588 | 0 | 16416 | 6598 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0312 | SPARE SER 0312 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5390 | NA | 15590 | 0 | 16416 | 6602 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0313 | SPARE SER 0313 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5392 | NA | 15592 | 0 | 16416 | 6606 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0314 | SPARE SER 0314 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5394 | NA | 15594 | 0 | 16416 | 6610 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0315 | SPARE SER 0315 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5396 | NA | 15596 | 0 | 16416 | 6614 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0316 | SPARE SER 0316 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5398 | NA | 15598 | 0 | 16416 | 6618 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6111I1 | TD1 103 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5400 | NA | 15600 | 0 | 16416 | 6622 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6111I2 | TD1 103 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5402 | NA | 15602 | 0 | 16416 | 6626 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6111I3 | TD1 103 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5404 | NA | 15604 | 0 | 16416 | 6630 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6111IN | TD1 103 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5406 | NA | 15606 | 0 | 16416 | 6634 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611112 | TD1 103 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5408 | NA | 15608 | 0 | 16416 | 6638 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611123 | TD1 103 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5410 | NA | 15610 | 0 | 16416 | 6642 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611131 | TD1 103 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5412 | NA | 15612 | 0 | 16416 | 6646 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6111V1 | TD1 103 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5414 | NA | 15614 | 0 | 16416 | 6650 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6111V2 | TD1 103 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5416 | NA | 15616 | 0 | 16416 | 6654 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6111V3 | TD1 103 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5418 | NA | 15618 | 0 | 16416 | 6658 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6111PF | TD1 103 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5420 | NA | 15620 | 0 | 16416 | 6662 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6111 | TD1 103 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6111D | TD1 1601-103-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5422 | NA | 15622 | 0 | 16416 | 6666 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0317 | SPARE SER 0317 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5424 | NA | 15624 | 0 | 16416 | 6670 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0318 | SPARE SER 0318 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5426 | NA | 15626 | 0 | 16416 | 6674 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0319 | SPARE SER 0319 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5428 | NA | 15628 | 0 | 16416 | 6678 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0320 | SPARE SER 0320 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5430 | NA | 15630 | 0 | 16416 | 6682 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0321 | SPARE SER 0321 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5432 | NA | 15632 | 0 | 16416 | 6686 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0322 | SPARE SER 0322 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5434 | NA | 15634 | 0 | 16416 | 6690 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0323 | SPARE SER 0323 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5436 | NA | 15636 | 0 | 16416 | 6694 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0324 | SPARE SER 0324 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5438 | NA | 15638 | 0 | 16416 | 6698 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6112I1 | TD2 103 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5440 | NA | 15640 | 0 | 16416 | 6702 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6112I2 | TD2 103 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5442 | NA | 15642 | 0 | 16416 | 6706 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6112I3 | TD2 103 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5444 | NA | 15644 | 0 | 16416 | 6710 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6112IN | TD2 103 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5446 | NA | 15646 | 0 | 16416 | 6714 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611212 | TD2 103 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5448 | NA | 15648 | 0 | 16416 | 6718 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611223 | TD2 103 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5450 | NA | 15650 | 0 | 16416 | 6722 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611231 | TD2 103 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5452 | NA | 15652 | 0 | 16416 | 6726 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6112V1 | TD2 103 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5454 | NA | 15654 | 0 | 16416 | 6730 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6112V2 | TD2 103 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5456 | NA | 15656 | 0 | 16416 | 6734 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6112V3 | TD2 103 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5458 | NA | 15658 | 0 | 16416 | 6738 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6112PF | TD2 103 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5460 | NA | 15660 | 0 | 16416 | 6742 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6112 | TD2 103 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6112D | TD2 1601-103-33 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5462 | NA | 15662 | 0 | 16416 | 6746 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0224 | SPARE SER 0224 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5464 | NA | 15664 | 0 | 16416 | 6750 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0225 | SPARE SER 0225 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5466 | NA | 15666 | 0 | 16416 | 6754 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0226 | SPARE SER 0226 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5468 | NA | 15668 | 0 | 16416 | 6758 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0227 | SPARE SER 0227 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5470 | NA | 15670 | 0 | 16416 | 6762 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0228 | SPARE SER 0228 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5472 | NA | 15672 | 0 | 16416 | 6766 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0229 | SPARE SER 0229 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5474 | NA | 15674 | 0 | 16416 | 6770 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0230 | SPARE SER 0230 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5476 | NA | 15676 | 0 | 16416 | 6774 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0231 | SPARE SER 0231 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5478 | NA | 15678 | 0 | 16416 | 6778 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6113I1 | TD3 103 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5480 | NA | 15680 | 0 | 16416 | 6782 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6113I2 | TD3 103 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5482 | NA | 15682 | 0 | 16416 | 6786 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6113I3 | TD3 103 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5484 | NA | 15684 | 0 | 16416 | 6790 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6113IN | TD3 103 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5486 | NA | 15686 | 0 | 16416 | 6794 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611312 | TD3 103 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5488 | NA | 15688 | 0 | 16416 | 6798 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611323 | TD3 103 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5490 | NA | 15690 | 0 | 16416 | 6802 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611331 | TD3 103 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5492 | NA | 15692 | 0 | 16416 | 6806 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6113V1 | TD3 103 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5494 | NA | 15694 | 0 | 16416 | 6810 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6113V2 | TD3 103 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5496 | NA | 15696 | 0 | 16416 | 6814 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6113V3 | TD3 103 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5498 | NA | 15698 | 0 | 16416 | 6818 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6113PF | TD3 103 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5500 | NA | 15700 | 0 | 16416 | 6822 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6113 | TD3 103 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6113D | TD3 1601-103-35 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5502 | NA | 15702 | 0 | 16416 | 6826 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0232 | SPARE SER 0232 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5504 | NA | 15704 | 0 | 16416 | 6830 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0233 | SPARE SER 0233 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5506 | NA | 15706 | 0 | 16416 | 6834 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0234 | SPARE SER 0234 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5508 | NA | 15708 | 0 | 16416 | 6838 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0235 | SPARE SER 0235 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5510 | NA | 15710 | 0 | 16416 | 6842 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0236 | SPARE SER 0236 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5512 | NA | 15712 | 0 | 16416 | 6846 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0237 | SPARE SER 0237 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5514 | NA | 15714 | 0 | 16416 | 6850 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0238 | SPARE SER 0238 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5516 | NA | 15716 | 0 | 16416 | 6854 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0239 | SPARE SER 0239 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5518 | NA | 15718 | 0 | 16416 | 6858 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6114I1 | TD4 103 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5520 | NA | 15720 | 0 | 16416 | 6862 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6114I2 | TD4 103 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5522 | NA | 15722 | 0 | 16416 | 6866 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6114I3 | TD4 103 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5524 | NA | 15724 | 0 | 16416 | 6870 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6114IN | TD4 103 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5526 | NA | 15726 | 0 | 16416 | 6874 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611412 | TD4 103 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5528 | NA | 15728 | 0 | 16416 | 6878 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611423 | TD4 103 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5530 | NA | 15730 | 0 | 16416 | 6882 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611431 | TD4 103 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5532 | NA | 15732 | 0 | 16416 | 6886 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6114V1 | TD4 103 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5534 | NA | 15734 | 0 | 16416 | 6890 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6114V2 | TD4 103 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5536 | NA | 15736 | 0 | 16416 | 6894 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6114V3 | TD4 103 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5538 | NA | 15738 | 0 | 16416 | 6898 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6114PF | TD4 103 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5540 | NA | 15740 | 0 | 16416 | 6902 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6114 | TD4 103 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6114D | TD4 1601-103-37 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5542 | NA | 15742 | 0 | 16416 | 6906 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0240 | SPARE SER 0240 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5544 | NA | 15744 | 0 | 16416 | 6910 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0241 | SPARE SER 0241 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5546 | NA | 15746 | 0 | 16416 | 6914 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0242 | SPARE SER 0242 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5548 | NA | 15748 | 0 | 16416 | 6918 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0243 | SPARE SER 0243 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5550 | NA | 15750 | 0 | 16416 | 6922 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0244 | SPARE SER 0244 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5552 | NA | 15752 | 0 | 16416 | 6926 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0245 | SPARE SER 0245 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5554 | NA | 15754 | 0 | 16416 | 6930 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0246 | SPARE SER 0246 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5556 | NA | 15756 | 0 | 16416 | 6934 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0247 | SPARE SER 0247 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5558 | NA | 15758 | 0 | 16416 | 6938 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6115I1 | TD 126 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5560 | NA | 15760 | 0 | 16416 | 6942 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6115I2 | TD 126 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5562 | NA | 15762 | 0 | 16416 | 6946 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6115I3 | TD 126 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5564 | NA | 15764 | 0 | 16416 | 6950 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6115IN | TD 126 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5566 | NA | 15766 | 0 | 16416 | 6954 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611512 | TD 126 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5568 | NA | 15768 | 0 | 16416 | 6958 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611523 | TD 126 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5570 | NA | 15770 | 0 | 16416 | 6962 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611531 | TD 126 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5572 | NA | 15772 | 0 | 16416 | 6966 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6115V1 | TD 126 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5574 | NA | 15774 | 0 | 16416 | 6970 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6115V2 | TD 126 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5576 | NA | 15776 | 0 | 16416 | 6974 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6115V3 | TD 126 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5578 | NA | 15778 | 0 | 16416 | 6978 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6115PF | TD 126 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5580 | NA | 15780 | 0 | 16416 | 6982 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6115 | TD 126 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6115D | TD AXIMA 1601-126-002 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5582 | NA | 15782 | 0 | 16416 | 6986 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0248 | SPARE SER 0248 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5584 | NA | 15784 | 0 | 16416 | 6990 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0249 | SPARE SER 0249 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5586 | NA | 15786 | 0 | 16416 | 6994 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0250 | SPARE SER 0250 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5588 | NA | 15788 | 0 | 16416 | 6998 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0251 | SPARE SER 0251 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5590 | NA | 15790 | 0 | 16416 | 7002 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0252 | SPARE SER 0252 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5592 | NA | 15792 | 0 | 16416 | 7006 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0253 | SPARE SER 0253 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5594 | NA | 15794 | 0 | 16416 | 7010 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0254 | SPARE SER 0254 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5596 | NA | 15796 | 0 | 16416 | 7014 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0255 | SPARE SER 0255 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5598 | NA | 15798 | 0 | 16416 | 7018 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6116I1 | TD 126 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5600 | NA | 15800 | 0 | 16416 | 7022 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6116I2 | TD 126 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5602 | NA | 15802 | 0 | 16416 | 7026 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6116I3 | TD 126 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5604 | NA | 15804 | 0 | 16416 | 7030 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6116IN | TD 126 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5606 | NA | 15806 | 0 | 16416 | 7034 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611612 | TD 126 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5608 | NA | 15808 | 0 | 16416 | 7038 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611623 | TD 126 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5610 | NA | 15810 | 0 | 16416 | 7042 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611631 | TD 126 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5612 | NA | 15812 | 0 | 16416 | 7046 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6116V1 | TD 126 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5614 | NA | 15814 | 0 | 16416 | 7050 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6116V2 | TD 126 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5616 | NA | 15816 | 0 | 16416 | 7054 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6116V3 | TD 126 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5618 | NA | 15818 | 0 | 16416 | 7058 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6116PF | TD 126 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5620 | NA | 15820 | 0 | 16416 | 7062 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6116 | TD 126 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6116D | TD AXIMA 1601-126-002 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5622 | NA | 15822 | 0 | 16416 | 7066 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0256 | SPARE SER 0256 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5624 | NA | 15824 | 0 | 16416 | 7070 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0257 | SPARE SER 0257 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5626 | NA | 15826 | 0 | 16416 | 7074 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0258 | SPARE SER 0258 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5628 | NA | 15828 | 0 | 16416 | 7078 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0259 | SPARE SER 0259 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5630 | NA | 15830 | 0 | 16416 | 7082 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0260 | SPARE SER 0260 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5632 | NA | 15832 | 0 | 16416 | 7086 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0261 | SPARE SER 0261 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5634 | NA | 15834 | 0 | 16416 | 7090 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0262 | SPARE SER 0262 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5636 | NA | 15836 | 0 | 16416 | 7094 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0263 | SPARE SER 0263 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5638 | NA | 15838 | 0 | 16416 | 7098 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6117I1 | TD AUX CLIM LOCAL 126 SECT.1 Phase current I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5640 | NA | 15840 | 0 | 16416 | 7102 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6117I2 | TD AUX CLIM LOCAL 126 SECT.1 Phase current I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5642 | NA | 15842 | 0 | 16416 | 7106 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6117I3 | TD AUX CLIM LOCAL 126 SECT.1 Phase current I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5644 | NA | 15844 | 0 | 16416 | 7110 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6117IN | TD AUX CLIM LOCAL 126 SECT.1 Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5646 | NA | 15846 | 0 | 16416 | 7114 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611712 | TD AUX CLIM LOCAL 126 SECT.1 Line to line voltage U12 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5648 | NA | 15848 | 0 | 16416 | 7118 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611723 | TD AUX CLIM LOCAL 126 SECT.1 Line to line voltage U23 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5650 | NA | 15850 | 0 | 16416 | 7122 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611731 | TD AUX CLIM LOCAL 126 SECT.1 Line to line voltage U31 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5652 | NA | 15852 | 0 | 16416 | 7126 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6117V1 | TD AUX CLIM LOCAL 126 SECT.1 phase voltage V1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5654 | NA | 15854 | 0 | 16416 | 7130 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6117V2 | TD AUX CLIM LOCAL 126 SECT.1 phase voltage V2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5656 | NA | 15856 | 0 | 16416 | 7134 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6117V3 | TD AUX CLIM LOCAL 126 SECT.1 phase voltage V3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5658 | NA | 15858 | 0 | 16416 | 7138 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6117PF | TD AUX CLIM LOCAL 126 SECT.1 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5660 | NA | 15860 | 0 | 16416 | 7142 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6117 | TD AUX CLIM LOCAL 126 SECT.1 Frequency F (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6117D | TD AXIMA 1601-126-001 Sect I (E70) | Energie TD |  | 4 |  |  | 5662 | NA | 15862 | 0 | 16416 | 7146 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0264 | SPARE SER 0264 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5664 | NA | 15864 | 0 | 16416 | 7150 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0265 | SPARE SER 0265 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5666 | NA | 15866 | 0 | 16416 | 7154 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0266 | SPARE SER 0266 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5668 | NA | 15868 | 0 | 16416 | 7158 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0267 | SPARE SER 0267 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5670 | NA | 15870 | 0 | 16416 | 7162 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0268 | SPARE SER 0268 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5672 | NA | 15872 | 0 | 16416 | 7166 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0269 | SPARE SER 0269 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5674 | NA | 15874 | 0 | 16416 | 7170 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0270 | SPARE SER 0270 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5676 | NA | 15876 | 0 | 16416 | 7174 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0271 | SPARE SER 0271 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5678 | NA | 15878 | 0 | 16416 | 7178 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6118I1 | TD AUX CLIM LOCAL 126 SECT.3 Phase current I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5680 | NA | 15880 | 0 | 16416 | 7182 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6118I2 | TD AUX CLIM LOCAL 126 SECT.3 Phase current I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5682 | NA | 15882 | 0 | 16416 | 7186 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6118I3 | TD AUX CLIM LOCAL 126 SECT.3 Phase current I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5684 | NA | 15884 | 0 | 16416 | 7190 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6118IN | TD AUX CLIM LOCAL 126 SECT.3 Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5686 | NA | 15886 | 0 | 16416 | 7194 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611812 | TD AUX CLIM LOCAL 126 SECT.3 Line to line voltage U12 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5688 | NA | 15888 | 0 | 16416 | 7198 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611823 | TD AUX CLIM LOCAL 126 SECT.3 Line to line voltage U23 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5690 | NA | 15890 | 0 | 16416 | 7202 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611831 | TD AUX CLIM LOCAL 126 SECT.3 Line to line voltage U31 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5692 | NA | 15892 | 0 | 16416 | 7206 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6118V1 | TD AUX CLIM LOCAL 126 SECT.3 phase voltage V1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5694 | NA | 15894 | 0 | 16416 | 7210 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6118V2 | TD AUX CLIM LOCAL 126 SECT.3 phase voltage V2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5696 | NA | 15896 | 0 | 16416 | 7214 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6118V3 | TD AUX CLIM LOCAL 126 SECT.3 phase voltage V3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5698 | NA | 15898 | 0 | 16416 | 7218 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6118PF | TD AUX CLIM LOCAL 126 SECT.3 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5700 | NA | 15900 | 0 | 16416 | 7222 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6118 | TD AUX CLIM LOCAL 126 SECT.3 Frequency F (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6118D | TD AXIMA 1601-126-003 Sect 3 (E70) | Energie TD |  | 4 |  |  | 5702 | NA | 15902 | 0 | 16416 | 7226 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0272 | SPARE SER 0272 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5704 | NA | 15904 | 0 | 16416 | 7230 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0273 | SPARE SER 0273 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5706 | NA | 15906 | 0 | 16416 | 7234 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0274 | SPARE SER 0274 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5708 | NA | 15908 | 0 | 16416 | 7238 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0275 | SPARE SER 0275 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5710 | NA | 15910 | 0 | 16416 | 7242 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0276 | SPARE SER 0276 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5712 | NA | 15912 | 0 | 16416 | 7246 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0277 | SPARE SER 0277 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5714 | NA | 15914 | 0 | 16416 | 7250 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0278 | SPARE SER 0278 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5716 | NA | 15916 | 0 | 16416 | 7254 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0279 | SPARE SER 0279 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5718 | NA | 15918 | 0 | 16416 | 7258 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6119I1 | TD LOCAL 117 Phase current I1 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5720 | NA | 15920 | 0 | 16416 | 7262 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6119I2 | TD LOCAL 117 Phase current I2 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5722 | NA | 15922 | 0 | 16416 | 7266 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6119I3 | TD LOCAL 117 Phase current I3 (CAT II) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5724 | NA | 15924 | 0 | 16416 | 7270 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6119IN | TD LOCAL 117 Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5726 | NA | 15926 | 0 | 16416 | 7274 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611912 | TD LOCAL 117 Line to line voltage U12 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5728 | NA | 15928 | 0 | 16416 | 7278 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611923 | TD LOCAL 117 Line to line voltage U23 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5730 | NA | 15930 | 0 | 16416 | 7282 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR611931 | TD LOCAL 117 Line to line voltage U31 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5732 | NA | 15932 | 0 | 16416 | 7286 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6119V1 | TD LOCAL 117 phase voltage V1 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5734 | NA | 15934 | 0 | 16416 | 7290 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6119V2 | TD LOCAL 117 phase voltage V2 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5736 | NA | 15936 | 0 | 16416 | 7294 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6119V3 | TD LOCAL 117 phase voltage V3 (CAT II) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5738 | NA | 15938 | 0 | 16416 | 7298 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6119PF | TD LOCAL 117 Power factor (CAT II) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5740 | NA | 15940 | 0 | 16416 | 7302 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6119 | TD LOCAL 117 Frequency F (CAT II) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6119D | TD 1601-117-20 (E70) | Energie TD |  | 4 |  |  | 5742 | NA | 15942 | 0 | 16416 | 7306 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0280 | SPARE SER 0280 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5744 | NA | 15944 | 0 | 16416 | 7310 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0281 | SPARE SER 0281 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5746 | NA | 15946 | 0 | 16416 | 7314 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0282 | SPARE SER 0282 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5748 | NA | 15948 | 0 | 16416 | 7318 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0283 | SPARE SER 0283 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5750 | NA | 15950 | 0 | 16416 | 7322 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0284 | SPARE SER 0284 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5752 | NA | 15952 | 0 | 16416 | 7326 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0285 | SPARE SER 0285 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5754 | NA | 15954 | 0 | 16416 | 7330 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0286 | SPARE SER 0286 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5756 | NA | 15956 | 0 | 16416 | 7334 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0287 | SPARE SER 0287 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5758 | NA | 15958 | 0 | 16416 | 7338 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6120I1 | TD1 002 IIIA Phase current I1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5760 | NA | 15960 | 0 | 16416 | 7342 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6120I2 | TD1 002 IIIA Phase current I2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5762 | NA | 15962 | 0 | 16416 | 7346 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6120I3 | TD1 002 IIIA Phase current I3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5764 | NA | 15964 | 0 | 16416 | 7350 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6120IN | TD1 002 IIIA Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5766 | NA | 15966 | 0 | 16416 | 7354 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR612012 | TD1 002 IIIA Line to line voltage U12 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5768 | NA | 15968 | 0 | 16416 | 7358 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR612023 | TD1 002 IIIA Line to line voltage U23 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5770 | NA | 15970 | 0 | 16416 | 7362 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR612031 | TD1 002 IIIA Line to line voltage U31 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5772 | NA | 15972 | 0 | 16416 | 7366 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6120V1 | TD1 002 IIIA phase voltage V1 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5774 | NA | 15974 | 0 | 16416 | 7370 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6120V2 | TD1 002 IIIA phase voltage V2 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5776 | NA | 15976 | 0 | 16416 | 7374 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6120V3 | TD1 002 IIIA phase voltage V3 (CAT IIIA) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5778 | NA | 15978 | 0 | 16416 | 7378 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6120PF | TD1 002 IIIA Power factor (CAT IIIA) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5780 | NA | 15980 | 0 | 16416 | 7382 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6120 | TD1 002 IIIA Frequency F (CAT IIIA) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6120D | TD1 1601-002-30 CAT IIIA (E70) | Energie TD |  | 4 |  |  | 5782 | NA | 15982 | 0 | 16416 | 7386 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0288 | SPARE SER 0288 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5784 | NA | 15984 | 0 | 16416 | 7390 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0289 | SPARE SER 0289 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5786 | NA | 15986 | 0 | 16416 | 7394 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0290 | SPARE SER 0290 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5788 | NA | 15988 | 0 | 16416 | 7398 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0291 | SPARE SER 0291 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5790 | NA | 15990 | 0 | 16416 | 7402 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0292 | SPARE SER 0292 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5792 | NA | 15992 | 0 | 16416 | 7406 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0293 | SPARE SER 0293 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5794 | NA | 15994 | 0 | 16416 | 7410 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0294 | SPARE SER 0294 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5796 | NA | 15996 | 0 | 16416 | 7414 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0295 | SPARE SER 0295 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5798 | NA | 15998 | 0 | 16416 | 7418 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6121I1 | TD1 002 IIIB Phase current I1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5800 | NA | 16000 | 0 | 16416 | 7422 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6121I2 | TD1 002 IIIB Phase current I2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5802 | NA | 16002 | 0 | 16416 | 7426 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6121I3 | TD1 002 IIIB Phase current I3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5804 | NA | 16004 | 0 | 16416 | 7430 | 0 | EL6021_M178 |  | INT 32 (DINT)
EIR6121IN | TD1 002 IIIB Neutral current In | MA | N | RES | 1 | E |  |  | A | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5806 | NA | 16006 | 0 | 16416 | 7434 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR612112 | TD1 002 IIIB Line to line voltage U12 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5808 | NA | 16008 | 0 | 16416 | 7438 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR612123 | TD1 002 IIIB Line to line voltage U23 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5810 | NA | 16010 | 0 | 16416 | 7442 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR612131 | TD1 002 IIIB Line to line voltage U31 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5812 | NA | 16012 | 0 | 16416 | 7446 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6121V1 | TD1 002 IIIB phase voltage V1 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5814 | NA | 16014 | 0 | 16416 | 7450 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6121V2 | TD1 002 IIIB phase voltage V2 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5816 | NA | 16016 | 0 | 16416 | 7454 | 0 | EL6021_M178 |  | INT 32 (DINT)
EUR6121V3 | TD1 002 IIIB phase voltage V3 (CAT IIIB) | MA | N | RES | 1 | E |  |  | V | 0.01 | -215000000000 | 215000000000 | [13 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5818 | NA | 16018 | 0 | 16416 | 7458 | 0 | EL6021_M178 |  | INT 32 (DINT)
EWR6121PF | TD1 002 IIIB Power factor (CAT IIIB) | MA | N | RES | 1 | E |  |  | NA | 0.01 | -215000000000 | 215000000000 | [20 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5820 | NA | 16020 | 0 | 16416 | 7462 | 0 | EL6021_M178 |  | INT 32 (DINT)
EFR6121 | TD1 002 IIIB Frequency F (CAT IIIB) | MA | N | RES | 1 | E |  |  | Hz | 0.01 | -215000000000 | 215000000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6121D | TD1 1601-002-31 CAT IIIB (E70) | Energie TD |  | 4 |  |  | 5822 | NA | 16022 | 0 | 16416 | 7466 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0296 | SPARE SER 0296 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5824 | NA | 16024 | 0 | 16416 | 7470 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0297 | SPARE SER 0297 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5826 | NA | 16026 | 0 | 16416 | 7474 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0298 | SPARE SER 0298 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5828 | NA | 16028 | 0 | 16416 | 7478 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0299 | SPARE SER 0299 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5830 | NA | 16030 | 0 | 16416 | 7482 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0300 | SPARE SER 0300 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5832 | NA | 16032 | 0 | 16416 | 7486 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0301 | SPARE SER 0301 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5834 | NA | 16034 | 0 | 16416 | 7490 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0302 | SPARE SER 0302 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5836 | NA | 16036 | 0 | 16416 | 7494 | 0 | EL6021_M178 |  | INT 32 (DINT)
SPASMA0303 | SPARE SER 0303 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 4 |  |  | 5838 | NA | 16038 | 0 | 16416 | 7498 | 0 | EL6021_M178 |  | INT 32 (DINT)
VRU7120CO | CMDE FERMETURE INCENDIE HVAC QE TGBT 184-13-20 - BIT(0),MARCHE(1) / BIT(0),ARRET(0) | CT | O | FIL | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 53 | NA | [7 empty] | BIT | 0
VCF7000CO | CMDE REARMEMENT CLAPETS COUPE FEU | CT | O | FIL | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 54 | NA | [7 empty] | BIT | 1
VCF7000CF | CMDE ARRET REARMEMENT CLAPETS COUPE FEU | CT | O | FIL | 2 | C | [12 empty] | C | [13 empty] | MTCP |  |  | HVAC23 | HVAC (C) | LGRNG | 9 |  |  | 54 | NA | [7 empty] | BIT | 0
SPASMA0345 | SPARE SER 0345 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1004 | NA | 13471 | NA | 16416 | 2364 | 0 | EL6021_M179 |  | U16
SPASMA0346 | SPARE SER 0346 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1005 | NA | 13472 | NA | 16416 | 2366 | 0 | EL6021_M179 |  | U16
SPASMA0347 | SPARE SER 0347 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1006 | NA | 13473 | NA | 16416 | 2368 | 0 | EL6021_M179 |  | U16
SPASMA0348 | SPARE SER 0348 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1007 | NA | 13474 | NA | 16416 | 2370 | 0 | EL6021_M179 |  | U16
SPASMA0349 | SPARE SER 0349 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1008 | NA | 13475 | NA | 16416 | 2372 | 0 | EL6021_M179 |  | U16
SPASMA0350 | SPARE SER 0350 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1009 | NA | 13476 | NA | 16416 | 2374 | 0 | EL6021_M179 |  | U16
SPASMA0351 | SPARE SER 0351 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1010 | NA | 13477 | NA | 16416 | 2376 | 0 | EL6021_M179 |  | U16
SPASMA0352 | SPARE SER 0352 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1011 | NA | 13478 | NA | 16416 | 2378 | 0 | EL6021_M179 |  | U16
SCX7001CA | CMDE ARRET EXTI UPS BATT | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO | [11 empty] | MTCP |  |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 72 | NA | [7 empty] | BIT | 0
SCX7001CM | CMDE MARCHE EXTI UPS BATT | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO | [11 empty] | MTCP |  |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 72 | NA | [7 empty] | BIT | 1
SCX7002CA | CMDE ARRET EXTI TECH LAU | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO | [11 empty] | MTCP |  |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 74 | NA | [7 empty] | BIT | 0
SCX7002CM | CMDE MARCHE EXTI TECH LAU | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO | [11 empty] | MTCP |  |  | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI) | LGRNG | 9 |  |  | 74 | NA | [7 empty] | BIT | 1
SCE7003CM | CMDE REPORT ALERT EVACUATION TO COPV PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6001S (ON) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 80 | NA | [7 empty] | BIT | 1
SCE7003CA | CMDE REPORT ALERT EVACUATION TO COPV PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6001S (OFF) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 80 | NA | [7 empty] | BIT | 0
SPASMA0353 | SPARE SER 0353 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1018 | NA | 13485 | NA | 16416 | 2392 | 0 | EL6021_M179 |  | U16
SPASMA0354 | SPARE SER 0354 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1019 | NA | 13486 | NA | 16416 | 2394 | 0 | EL6021_M179 |  | U16
SPASMA0355 | SPARE SER 0355 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1020 | NA | 13487 | NA | 16416 | 2396 | 0 | EL6021_M179 |  | U16
SCE7004CM | CMDE REPORT ALERT REPLI TO COPV PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6002S (ON) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 81 | NA | [7 empty] | BIT | 1
SCE7004CA | CMDE REPORT ALERT REPLI TO COPV PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6002S (OFF) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 81 | NA | [7 empty] | BIT | 0
EIR6001T1 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Itrip tripping currents 1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1036 | NA | 13503 | NA | 16416 | 2428 | 0 | EL6021_M179 |  | U32
EIR6001T2 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Itrip tripping currents 2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1038 | NA | 13505 | NA | 16416 | 2432 | 0 | EL6021_M179 |  | U32
EIR6001T3 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Itrip tripping currents 3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1040 | NA | 13507 | NA | 16416 | 2436 | 0 | EL6021_M179 |  | U32
SCE7005CM | CMDE REPORT ALERT EVACUATION TO PRS PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6001S (ON) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 82 | NA | [7 empty] | BIT | 1
SCE7005CA | CMDE REPORT ALERT EVACUATION TO PRS PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6001S (OFF) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 82 | NA | [7 empty] | BIT | 0
SCE7006CM | CMDE REPORT ALERT REPLI TO PRS PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6002S (ON) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 83 | NA | [7 empty] | BIT | 1
SPASMA0356 | SPARE SER 0356 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1054 | NA | 13514 | NA | 16416 | 2450 | 0 | EL6021_M179 |  | U16
SPASMA0357 | SPARE SER 0357 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1055 | NA | 13515 | NA | 16416 | 2452 | 0 | EL6021_M179 |  | U16
SPASMA0358 | SPARE SER 0358 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1056 | NA | 13516 | NA | 16416 | 2454 | 0 | EL6021_M179 |  | U16
SPASMA0359 | SPARE SER 0359 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1057 | NA | 13517 | NA | 16416 | 2456 | 0 | EL6021_M179 |  | U16
SPASMA0360 | SPARE SER 0360 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1058 | NA | 13518 | NA | 16416 | 2458 | 0 | EL6021_M179 |  | U16
SPASMA0361 | SPARE SER 0361 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1059 | NA | 13519 | NA | 16416 | 2460 | 0 | EL6021_M179 |  | U16
SPASMA0362 | SPARE SER 0362 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1060 | NA | 13520 | NA | 16416 | 2462 | 0 | EL6021_M179 |  | U16
SPASMA0363 | SPARE SER 0363 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1061 | NA | 13521 | NA | 16416 | 2464 | 0 | EL6021_M179 |  | U16
SCE7006CA | CMDE REPORT ALERT REPLI TO PRS PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6002S (OFF) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 83 | NA | [7 empty] | BIT | 0
SCE7007CM | CMDE REPORT ALERT EVACUATION TO PANDORA PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6001S (ON) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 84 | NA | [7 empty] | BIT | 1
SCE7007CA | CMDE REPORT ALERT EVACUATION TO PANDORA PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6001S (OFF) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 84 | NA | [7 empty] | BIT | 0
SCE7008CM | CMDE REPORT ALERT REPLI TO PANDORA PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6002S (ON) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 85 | NA | [7 empty] | BIT | 1
SCE7008CA | CMDE REPORT ALERT REPLI TO PANDORA PLATINE | CT | O | FIL | 2 | S | [11 empty] | ON | S | NO | NO |  |  | SCE6002S (OFF) | [8 empty] | MTCP |  |  | MG72 | Moyens Generaux (MG) | LGRNG | 9 |  |  | 85 | NA | [7 empty] | BIT | 0
SOR6102 | MESURE 1 CONCENTRATION LIE DETECTEUR CL8-1-1 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 |  | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 328 | NA | 12446 | NA | 16416 | 314 | 0 | EL6021_M176 |  | U16 |  | Eliminazione del segnale SOR6101 e aggiunta spare SPASMA1131
SPASMA0364 | SPARE SER 0364 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1068 | NA | 13528 | NA | 16416 | 2478 | 0 | EL6021_M179 |  | U16
SPASMA0365 | SPARE SER 0365 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1069 | NA | 13529 | NA | 16416 | 2480 | 0 | EL6021_M179 |  | U16
SPASMA0366 | SPARE SER 0366 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1070 | NA | 13530 | NA | 16416 | 2482 | 0 | EL6021_M179 |  | U16
SOR6202 | MESURE 2 CONCENTRATION LIE DETECTEUR CL8-1-2 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 329 | NA | 12447 | NA | 16416 | 316 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SPASMA1133 | SPARE SER MA 1133 (SOR6203) | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 331 | NA | 12449 | NA | 16416 | 320 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
EIR6002T1 | CAT.II 1D60 TO TGBT ZLV (1D61) Itrip tripping currents 1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1086 | NA | 13546 | NA | 16416 | 2514 | 0 | EL6021_M179 |  | U32
EIR6002T2 | CAT.II 1D60 TO TGBT ZLV (1D61) Itrip tripping currents 2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1088 | NA | 13548 | NA | 16416 | 2518 | 0 | EL6021_M179 |  | U32
EIR6002T3 | CAT.II 1D60 TO TGBT ZLV (1D61) Itrip tripping currents 3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1090 | NA | 13550 | NA | 16416 | 2522 | 0 | EL6021_M179 |  | U32
SOR6104 | MESURE 1 CONCENTRATION LIE DETECTEUR CL8-2-1 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 332 | NA | 12450 | NA | 16416 | 322 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6204 | MESURE 2 CONCENTRATION LIE DETECTEUR CL8-2-2 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 333 | NA | 12451 | NA | 16416 | 324 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SPASMA1134 | SPARE SER MA 1134 (SOR6105) | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 334 | NA | 12452 | NA | 16416 | 326 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SPASMA0367 | SPARE SER 0367 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1104 | NA | 13555 | NA | 16416 | 2532 | 0 | EL6021_M179 |  | U16
SPASMA0368 | SPARE SER 0368 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1105 | NA | 13556 | NA | 16416 | 2534 | 0 | EL6021_M179 |  | U16
SPASMA0369 | SPARE SER 0369 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1106 | NA | 13557 | NA | 16416 | 2536 | 0 | EL6021_M179 |  | U16
SPASMA0370 | SPARE SER 0370 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1107 | NA | 13558 | NA | 16416 | 2538 | 0 | EL6021_M179 |  | U16
SPASMA0371 | SPARE SER 0371 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1108 | NA | 13559 | NA | 16416 | 2540 | 0 | EL6021_M179 |  | U16
SPASMA0372 | SPARE SER 0372 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1109 | NA | 13560 | NA | 16416 | 2542 | 0 | EL6021_M179 |  | U16
SPASMA0373 | SPARE SER 0373 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1110 | NA | 13561 | NA | 16416 | 2544 | 0 | EL6021_M179 |  | U16
SPASMA0374 | SPARE SER 0374 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1111 | NA | 13562 | NA | 16416 | 2546 | 0 | EL6021_M179 |  | U16
SOR6106 | MESURE 1 CONCENTRATION LIE DETECTEUR CL8-3-1 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 336 | NA | 12454 | NA | 16416 | 330 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6206 | MESURE 2 CONCENTRATION LIE DETECTEUR CL8-3-2 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 337 | NA | 12455 | NA | 16416 | 332 | 0 | EL6021_M176 |  | U16 |  | Eliminazione del segnale SOR6101 e aggiunta spare SPASMA1134
SOR6108 | MESURE 1 CONCENTRATION LIE DETECTEUR CL8-4-1 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 340 | NA | 12458 | NA | 16416 | 338 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6208 | MESURE 2 CONCENTRATION LIE DETECTEUR CL8-4-2 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 341 | NA | 12459 | NA | 16416 | 340 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6109 | MESURE 1 CONCENTRATION LIE LOCAL 501 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 342 | NA | 12460 | NA | 16416 | 342 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6209 | MESURE 2 CONCENTRATION LIE LOCAL 501 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 100 |  |  | 0 | 25 |  |  | S;F;D | [13 empty] | NOT | 1000 | SZP6004 | DG65 | Detection Vapeurs Toxiques (DVT) | CCS | 1 |  |  | 343 | NA | 12461 | NA | 16416 | 344 | 0 | EL6021_M176 |  | U16 |  | moltiplicati per 10000, per passare da ppm a %
SPASMA0375 | SPARE SER 0375 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1118 | NA | 13569 | NA | 16416 | 2560 | 0 | EL6021_M179 |  | U16
SPASMA0376 | SPARE SER 0376 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1119 | NA | 13570 | NA | 16416 | 2562 | 0 | EL6021_M179 |  | U16
SPASMA0377 | SPARE SER 0377 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1120 | NA | 13571 | NA | 16416 | 2564 | 0 | EL6021_M179 |  | U16
HPR6310 | PRESSION HELIUM LIGNE 200B VERS P80 | MA | N | RES | 1 | F |  |  | BAR | 0.01 | 0 | 4 |  |  | 0.4 | 4 |  |  | F | [13 empty] | NOT | 1000 |  | MG68;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 106 | NA | 12622 | NA | 16416 | 666 | 0 | EL6021_M177 |  | I16 |  | In base a info date da Massimiliano su range misura su PLC
RPR6305 | PRESSION RESEAU AIR PORTIQUE MOBILE | MA | N | RES | 1 | F |  | 8 | BAR | 0.01 | 0 | 10 |  |  | 1 | 10 |  |  | F | [13 empty] | NOT | 1000 |  | MG68;VG01 | Moyens Generaux VEGA (MG); Process Fluide et Energie VEGA (VG) | CCS | 3 |  |  | 109 | NA | 12625 | NA | 16416 | 672 | 0 | EL6021_M177 |  | I16 |  | In base a info date da Massimiliano su range misura su PLC
EIR6003T1 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Itrip tripping currents 1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1136 | NA | 13587 | NA | 16416 | 2596 | 0 | EL6021_M179 |  | U32
EIR6003T2 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Itrip tripping currents 2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1138 | NA | 13589 | NA | 16416 | 2600 | 0 | EL6021_M179 |  | U32
EIR6003T3 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Itrip tripping currents 3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1140 | NA | 13591 | NA | 16416 | 2604 | 0 | EL6021_M179 |  | U32
SOR6003 | CONCENTRATION UDMH/N2H4 LOCAL 501 NIV29.200 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 113 | NA | 12629 | NA | 16416 | 680 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6004 | CONCENTRATION N2H4 321-1 PANNEAUX ERGOLS NIV 37.000 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 114 | NA | 12630 | NA | 16416 | 682 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6005 | CONCENTRATION UDMH U300-3 PANNEAUX ERGOLS NIV 37.000 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 115 | NA | 12631 | NA | 16416 | 684 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SPASMA0378 | SPARE SER 0378 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1154 | NA | 13596 | NA | 16416 | 2614 | 0 | EL6021_M179 |  | U16
SPASMA0379 | SPARE SER 0379 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1155 | NA | 13597 | NA | 16416 | 2616 | 0 | EL6021_M179 |  | U16
SPASMA0380 | SPARE SER 0380 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1156 | NA | 13598 | NA | 16416 | 2618 | 0 | EL6021_M179 |  | U16
SPASMA0381 | SPARE SER 0381 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1157 | NA | 13599 | NA | 16416 | 2620 | 0 | EL6021_M179 |  | U16
SPASMA0382 | SPARE SER 0382 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1158 | NA | 13600 | NA | 16416 | 2622 | 0 | EL6021_M179 |  | U16
SPASMA0383 | SPARE SER 0383 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1159 | NA | 13601 | NA | 16416 | 2624 | 0 | EL6021_M179 |  | U16
SPASMA0384 | SPARE SER 0384 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1160 | NA | 13602 | NA | 16416 | 2626 | 0 | EL6021_M179 |  | U16
SPASMA0385 | SPARE SER 0385 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1161 | NA | 13603 | NA | 16416 | 2628 | 0 | EL6021_M179 |  | U16
SOR6006 | CONCENTRATION UDMH LOCAL 601 NIV31.800 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 116 | NA | 12632 | NA | 16416 | 686 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6007 | CONCENTRATION UDMH/N2H4 AMBIANCE | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6102D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 117 | NA | 12633 | NA | 16416 | 688 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6008 | MESURE FUITE UDMH REMP. AVUM | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 450 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 118 | NA | 12634 | NA | 16416 | 690 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6009 | MESURE FUITE UDMH REMP. AVUM | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 450 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 119 | NA | 12635 | NA | 16416 | 692 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6010 | MESURE FUITE UDMH COIFFE | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 450 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 120 | NA | 12636 | NA | 16416 | 694 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6011 | MESURE FUITE N2H4 REMP. AVUM | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 450 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 121 | NA | 12637 | NA | 16416 | 696 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SPASMA0386 | SPARE SER 0386 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1168 | NA | 13610 | NA | 16416 | 2642 | 0 | EL6021_M179 |  | U16
SPASMA0387 | SPARE SER 0387 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1169 | NA | 13611 | NA | 16416 | 2644 | 0 | EL6021_M179 |  | U16
SPASMA0388 | SPARE SER 0388 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1170 | NA | 13612 | NA | 16416 | 2646 | 0 | EL6021_M179 |  | U16
SOR6012 | MESURE FUITE N2H4 REMP. AVUM | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 450 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 122 | NA | 12638 | NA | 16416 | 698 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
SOR6013 | MESURE FUITE N2H4 COIFFE | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 500 |  |  |  | 450 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 123 | NA | 12639 | NA | 16416 | 700 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a % | MOD
EIR6004T1 | CAT.I 1D60 TO TGBT ZLV (1D61) Itrip tripping currents 1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1186 | NA | 13628 | NA | 16416 | 2678 | 0 | EL6021_M179 |  | U32
EIR6004T2 | CAT.I 1D60 TO TGBT ZLV (1D61) Itrip tripping currents 2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1188 | NA | 13630 | NA | 16416 | 2682 | 0 | EL6021_M179 |  | U32
EIR6004T3 | CAT.I 1D60 TO TGBT ZLV (1D61) Itrip tripping currents 3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1190 | NA | 13632 | NA | 16416 | 2686 | 0 | EL6021_M179 |  | U32
SOR6014 | CONCENTRATION N2O4 LOCAL 501 DVT NIV 29.200 CL8-3 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 124 | NA | 12640 | NA | 16416 | 702 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6015 | CONCENTRATION N2O4 LOCAL 701 NIV 34.400 CL8-3 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 125 | NA | 12641 | NA | 16416 | 704 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6016 | CONCENTRATION N2O4 N200-3 PANNEAUX ERGOLS NIV 37.000 CL8-3 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 126 | NA | 12642 | NA | 16416 | 706 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SPASMA0389 | SPARE SER 0389 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1204 | NA | 13637 | NA | 16416 | 2696 | 0 | EL6021_M179 |  | U16
SPASMA0390 | SPARE SER 0390 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1205 | NA | 13638 | NA | 16416 | 2698 | 0 | EL6021_M179 |  | U16
SPASMA0391 | SPARE SER 0391 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1206 | NA | 13639 | NA | 16416 | 2700 | 0 | EL6021_M179 |  | U16
SPASMA0392 | SPARE SER 0392 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1207 | NA | 13640 | NA | 16416 | 2702 | 0 | EL6021_M179 |  | U16
SPASMA0393 | SPARE SER 0393 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1208 | NA | 13641 | NA | 16416 | 2704 | 0 | EL6021_M179 |  | U16
SPASMA0394 | SPARE SER 0394 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1209 | NA | 13642 | NA | 16416 | 2706 | 0 | EL6021_M179 |  | U16
SPASMA0395 | SPARE SER 0395 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1210 | NA | 13643 | NA | 16416 | 2708 | 0 | EL6021_M179 |  | U16
SPASMA0396 | SPARE SER 0396 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1211 | NA | 13644 | NA | 16416 | 2710 | 0 | EL6021_M179 |  | U16
SOR6017 | CONCENTRATION N2O4 LOCAL 701 NIV 34.400 CL8-3 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 127 | NA | 12643 | NA | 16416 | 708 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6018 | CONCENTRATION N2O4 AMBIANCE CL8-3 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 128 | NA | 12644 | NA | 16416 | 710 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6019 | MESURE FUITE N2O4 REMP. AVUM CL8-4 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6108D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 129 | NA | 12645 | NA | 16416 | 712 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6020 | MESURE FUITE N2O4 REMP. AVUM CL8-4 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6108D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 130 | NA | 12646 | NA | 16416 | 714 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
SOR6021 | MESURE FUITE N2O4 COIFFE CL8-4 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6108D | DG64 | Detection Vapeurs Toxiques (DVT) | CCS | 3 |  |  | 131 | NA | 12647 | NA | 16416 | 716 | 0 | EL6021_M177 |  | I16 |  | moltiplicati per 10000, per passare da ppm a %
VPR6601 | PRESSION DIFFERENTIEL HALL INTEG VS 601 | MA | N | RES | 1 | C |  |  | BAR | 0,001x - 10,008 |  |  |  |  | -10 | 10 |  |  | C | [13 empty] | NOT | 1000 | ZZN6014 | HVAC15 | HVAC | CCS | 3 |  |  | 132 | NA | 12648 | NA | 16416 | 718 | 0 | EL6021_M177 |  | I16 |  | In base a info date da Massimiliano su range misura su PLC
SPASMA0397 | SPARE SER 0397 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1218 | NA | 13651 | NA | 16416 | 2724 | 0 | EL6021_M179 |  | U16
SPASMA0398 | SPARE SER 0398 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1219 | NA | 13652 | NA | 16416 | 2726 | 0 | EL6021_M179 |  | U16
SPASMA0399 | SPARE SER 0399 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1220 | NA | 13653 | NA | 16416 | 2728 | 0 | EL6021_M179 |  | U16
VPR6701 | PRESSION DIFFERENTIEL HALL INTEG VS 701 | MA | N | RES | 1 | C |  |  | BAR | 0,001x - 10,008 |  |  |  |  | -10 | 10 |  |  | C | [13 empty] | NOT | 1000 | ZZN6014 | HVAC15 | HVAC | CCS | 3 |  |  | 133 | NA | 12649 | NA | 16416 | 720 | 0 | EL6021_M177 |  | I16 |  | In base a info date da Massimiliano su range misura su PLC
VPR6001 | PRESSION DIFFERENTIEL HALL INTEG VS EXTER | MA | N | RES | 1 | C |  |  | BAR | 0,001x - 10,008 |  |  |  |  | -10 | 10 |  |  | C | [13 empty] | NOT | 1000 | ZZN6014 | HVAC15 | HVAC | CCS | 3 |  |  | 134 | NA | 12650 | NA | 16416 | 722 | 0 | EL6021_M177 |  | I16 |  | In base a info date da Massimiliano su range misura su PLC
EIR6142T1 | CAT.I 1D60 TO 1D42 Itrip tripping currents 1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1236 | NA | 13669 | NA | 16416 | 2760 | 0 | EL6021_M179 |  | U32
EIR6142T2 | CAT.I 1D60 TO 1D42 Itrip tripping currents 2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1238 | NA | 13671 | NA | 16416 | 2764 | 0 | EL6021_M179 |  | U32
EIR6142T3 | CAT.I 1D60 TO 1D42 Itrip tripping currents 3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1240 | NA | 13673 | NA | 16416 | 2768 | 0 | EL6021_M179 |  | U32
SOR6022 | MESURE FUITE N2O4 N200-8 PANNEAUX ERGOLS NIV. 39.600 CL8-3 | MA | N | RES | 1 | S;F;D |  |  | ppm | 0.1 | 0 | 0.45 |  |  |  | 0.01 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6106D | DG64 | Detection Vapeurs Toxiques (DVT) | NEW | 3 |  |  | 135 | NA | 12651 | NA | 16416 | 724 | 0 | EL6021_M177 |  | I16 |  | NUOVO SEGNALE VEGA C
SOR6023 | MESURE FUITE UDMH U300-8 PANNEAUX ERGOLS NIV. 39.600 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 6500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | NEW | 3 |  |  | 136 | NA | 12652 | NA | 16416 | 726 | 0 | EL6021_M177 |  | I16 |  | NUOVO SEGNALE VEGA C
SOR6024 | MESURE FUITE N2H4 321-8 PANNEAUX ERGOLS NIV. 39.600 | MA | N | RES | 1 | S;F;D |  |  | % | 1 | 0 | 6500 |  |  |  | 9 |  |  | S;F;D | [13 empty] | NOT | 1000 | SAV6104D | DG64 | Detection Vapeurs Toxiques (DVT) | NEW | 3 |  |  | 137 | NA | 12653 | NA | 16416 | 728 | 0 | EL6021_M177 |  | I16 |  | NUOVO SEGNALE VEGA C
SPASMA0400 | SPARE SER 0400 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1254 | NA | 13678 | NA | 16416 | 2778 | 0 | EL6021_M179 |  | U16
SPASMA0401 | SPARE SER 0401 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1255 | NA | 13679 | NA | 16416 | 2780 | 0 | EL6021_M179 |  | U16
SPASMA0402 | SPARE SER 0402 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1256 | NA | 13680 | NA | 16416 | 2782 | 0 | EL6021_M179 |  | U16
SPASMA0403 | SPARE SER 0403 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1257 | NA | 13681 | NA | 16416 | 2784 | 0 | EL6021_M179 |  | U16
SPASMA0404 | SPARE SER 0404 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1258 | NA | 13682 | NA | 16416 | 2786 | 0 | EL6021_M179 |  | U16
SPASMA0405 | SPARE SER 0405 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1259 | NA | 13683 | NA | 16416 | 2788 | 0 | EL6021_M179 |  | U16
SPASMA0406 | SPARE SER 0406 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1260 | NA | 13684 | NA | 16416 | 2790 | 0 | EL6021_M179 |  | U16
SPASMA0407 | SPARE SER 0407 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1261 | NA | 13685 | NA | 16416 | 2792 | 0 | EL6021_M179 |  | U16
AQR6301 | DEBIT RESEAU AZOTE 250B ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | NM3H | FORM | 0 | 400 |  |  | 0 | 400 |  |  | F | [9 empty] | FORM | ((1/2048)*x+4)*25 - 100 |  |  | NOT |  |  | MG68;VG03;VMC05 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13020 | 0 | 16416 | 1462 | 0 | EL3124_M172 | 1(+) - 2(-) | I16 |  | In base a info date da Massimiliano su field equipment
HQR6301 | DEBIT RESEAU HELIUM 200B ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | NM3H | FORM | 0 | 400 |  |  | 0 | 400 |  |  | F | [9 empty] | FORM | ((1/2048)*x+4)*25 - 100 |  |  | NOT | 1000 |  | MG68;VG03 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13021 | 0 | 16416 | 1464 | 0 | EL3124_M172 | 5(+) - 6(-) | I16 |  | In base a info date da Massimiliano su field equipment
ONR6301 | MESURE NIVEAU D'EAU 1 CUVE 175M3 ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | m | FORM | 0 | 7 |  |  | 0.5 | 3.5 |  |  | F | [9 empty] | FORM | ((((1/2048)*x+4)-4)/2,2857) |  |  | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13022 | 0 | 16416 | 1466 | 0 | EL3124_M172 | 3(+) - 4(-) | I16 |  | Non è chiaro, scalata solo in relazione a dati fluidica
ONR6302 | MESURE NIVEAU D'EAU 2 CUVE 175M3 ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | m | FORM | 0 | 7 |  |  | 0.5 | 3.5 |  |  | F | [9 empty] | FORM | ((((1/2048)*x+4)-4)/2,2857) |  |  | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13023 | 0 | 16416 | 1468 | 0 | EL3124_M172 | 7(+) - 8(-) | I16 |  | Non è chiaro, scalata solo in relazione a dati fluidica
OOR6301 | MESURE PH TRAITEMENT EFFLUENT CARNEAU VEGA | MA | O | FIL | 1 | F |  | 8 | % | FORM | -2 | 16 |  |  | -2 | 16 |  |  | F | [9 empty] | FORM | (((1/2048)*x+4)*1,125) - 6,5 |  |  | NOT | 1000 |  | MG65;VG04 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13024 | 0 | 16416 | 1470 | 0 | EL3124_M173 | 1(+) - 2(-) | I16 |  | In assenza di info, messo 1. è strano che unità di misura sia % per un ph
RPD6301 | DELTA P RESEAU AIR ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | BAR | FORM | 0 | 1 |  |  |  | 0.2 |  |  | F | [9 empty] | FORM | ((((1/2048)*x+4)-4)/16) |  |  | NOT | 1000 |  | MG68;VG03 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13025 | 0 | 16416 | 1472 | 0 | EL3124_M173 | 5(+) - 6(-) | I16 |  | In base a info date da Massimiliano su field equipment
SPASMA0408 | SPARE SER 0408 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1268 | NA | 13692 | NA | 16416 | 2806 | 0 | EL6021_M179 |  | U16
SPASMA0409 | SPARE SER 0409 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1269 | NA | 13693 | NA | 16416 | 2808 | 0 | EL6021_M179 |  | U16
SPASMA0410 | SPARE SER 0410 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 5 |  |  | 1270 | NA | 13694 | NA | 16416 | 2810 | 0 | EL6021_M179 |  | U16
RPR6301 | PRESSION RESEAU AIR ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | BAR | FORM | 0 | 10 |  |  | 0 | 6.6 |  |  | F | [9 empty] | FORM | ((((1/2048)*x+4)-4)/1.6) |  |  | NOT | 1000 |  | MG68;VG03 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13026 | 0 | 16416 | 1474 | 0 | EL3124_M173 | 3(+) - 4(-) | I16 |  | In base a info date da Massimiliano su field equipment
RQR6301 | DEBIT RESEAU AIR ZLV VEGA | MA | O | FIL | 1 | F |  | 8 | NM3H | FORM | 0 | 4000 |  |  | 0 | 4000 |  |  | F | [9 empty] | FORM | (((1/2048)*x+4)*250) - 1000 |  |  | NOT | 1000 |  | MG68;VG03 | Moyens Generaux (MG); Process Fluide et Energie VEGA (VG) | CCS | [5 empty] | 13027 | 0 | 16416 | 1476 | 0 | EL3124_M173 | 7(+) - 8(-) | I16 |  | In base a info date da Massimiliano su field equipment
EIR6242T1 | CAT.II 1D60 TO 1D42 Itrip tripping currents 1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1286 | NA | 13710 | NA | 16416 | 2842 | 0 | EL6021_M179 |  | U32
EIR6242T2 | CAT.II 1D60 TO 1D42 Itrip tripping currents 2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1288 | NA | 13712 | NA | 16416 | 2846 | 0 | EL6021_M179 |  | U32
EIR6242T3 | CAT.II 1D60 TO 1D42 Itrip tripping currents 3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1290 | NA | 13714 | NA | 16416 | 2850 | 0 | EL6021_M179 |  | U32
EZC6160 | PLC 1D60 WATCHDOG | MA |  | RES | 1 | A |  |  | A |  | 0 | 65535 |  |  | 0 | 32767 | [16 empty] | POL | 6000 |  | E68;E69 | Energie 1D60 VEGA (E) |  | 5 |  |  | 1300 | NA | 13716 | NA | 16416 | 2854 | 0 | EL6021_M179 |  | UINT
SPASCR0630 | SPARE SER 0630 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3049 | NA | 13848 | NA | 16416 | 3118 | 0 | EL6021_M180 |  | UINT
EIR6081I1 | TGBT ZLV ARRIVEE TM 7002 CAT.II Phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3070 | NA | 13139 | NA | 16416 | 1700 | 0 | EL6021_M178 |  | INT
EIR6081I2 | TGBT ZLV ARRIVEE TM 7002 CAT.II Phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3071 | NA | 13140 | NA | 16416 | 1702 | 0 | EL6021_M178 |  | INT
EIR6081I3 | TGBT ZLV ARRIVEE TM 7002 CAT.II Phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3072 | NA | 13141 | NA | 16416 | 1704 | 0 | EL6021_M178 |  | INT
EUR608112 | TGBT ZLV ARRIVEE TM 7002 CAT.II Line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3073 | NA | 13142 | NA | 16416 | 1706 | 0 | EL6021_M178 |  | INT
CPR6004F3 | VEGA BUNKER PLC : PRESSURE HOT WATER PUMP M04 (BUNKER/GANTRY) | MA |  | RES | 1 | C |  |  | Kpa | 0.1 | 0 | 1000 | [20 empty] | POL | 6000 | VZC6126Z17 | HVAC03 | HVAC |  | 6 |  |  | 3054 | NA | 13853 | NA | 16416 | 3128 | 0 | EL6021_M180 |  | INT
SPASMA0631 | SPARE SER 0631 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3055 | NA | 13854 | NA | 16416 | 3130 | 0 | EL6021_M180 |  | INT
EUR608123 | TGBT ZLV ARRIVEE TM 7002 CAT.II Line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3074 | NA | 13143 | NA | 16416 | 1708 | 0 | EL6021_M178 |  | INT
EUR608131 | TGBT ZLV ARRIVEE TM 7002 CAT.II Line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3075 | NA | 13144 | NA | 16416 | 1710 | 0 | EL6021_M178 |  | INT
EUR6081V1 | TGBT ZLV ARRIVEE TM 7002 CAT.II Phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3076 | NA | 13145 | NA | 16416 | 1712 | 0 | EL6021_M178 |  | INT
GQR6001F1 | VEGA BUNKER PLC : FLOW RETURN COLD WATER BUNKER | MA |  | RES | 1 | C |  |  | m3/H | 1 | 0 | 1000 | [20 empty] | POL | 6000 | VZC6126Z21 | HVAC03 | HVAC |  | 6 |  |  | 3059 | NA | 13858 | NA | 16416 | 3138 | 0 | EL6021_M180 |  | INT
GQR6034F2 | VEGA BUNKER PLC : FLOW RETURN COLD WATER GANTRY | MA |  | RES | 1 | C |  |  | m3/H | 1 | 0 | 1000 | [20 empty] | POL | 6000 | VZC6126Z22 | HVAC03 | HVAC |  | 6 |  |  | 3060 | NA | 13859 | NA | 16416 | 3140 | 0 | EL6021_M180 |  | INT
VTR6001T | VEGA BUNKER PLC : TEMPERATURE AFTER COOL BATTERY FAN CTA M01 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z13 | HVAC04 | HVAC |  | 6 |  |  | 3061 | NA | 13860 | NA | 16416 | 3142 | 0 | EL6021_M180 |  | INT
VTR6001S | VEGA BUNKER PLC : PULSE TEMPERATURE FAN CTA M01 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z14 | HVAC04;VMC05 | HVAC |  | 6 |  |  | 3062 | NA | 13861 | NA | 16416 | 3144 | 0 | EL6021_M180 |  | INT
VTR6000E | VEGA BUNKER PLC : TEMPERATURE OUTSIDE | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z27 | HVAC04;HVAC13;HVAC14 | HVAC |  | 6 |  |  | 3063 | NA | 13862 | NA | 16416 | 3146 | 0 | EL6021_M180 |  | INT
GWR6001G | VEGA BUNKER PLC : POWER CHILLER 1 | MA |  | RES | 1 | C |  |  | KW | 1 | 0 | 100 | [20 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3064 | NA | 13863 | NA | 16416 | 3148 | 0 | EL6021_M180 |  | INT
GTR6001G1 | VEGA BUNKER PLC : TEMPERATURE INPUT CHILLER 1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3065 | NA | 13864 | NA | 16416 | 3150 | 0 | EL6021_M180 |  | INT
GTR6001G2 | VEGA BUNKER PLC : TEMPERATURE OUTPUT CHILLER 1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3066 | NA | 13865 | NA | 16416 | 3152 | 0 | EL6021_M180 |  | INT
GTR6001G3 | VEGA BUNKER PLC : TEMPERATURE INPUT DRY COOLER CHILLER 1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3067 | NA | 13866 | NA | 16416 | 3154 | 0 | EL6021_M180 |  | INT
SPASMA0632 | SPARE SER 0632 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3068 | NA | 13867 | NA | 16416 | 3156 | 0 | EL6021_M180 |  | INT
GWR6002G | VEGA BUNKER PLC : POWER CHILLER 2 | MA |  | RES | 1 | C |  |  | KW | 1 | 0 | 100 | [20 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3069 | NA | 13868 | NA | 16416 | 3158 | 0 | EL6021_M180 |  | INT
GTR6002G1 | VEGA BUNKER PLC : TEMPERATURE INPUT CHILLER 2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3070 | NA | 13869 | NA | 16416 | 3160 | 0 | EL6021_M180 |  | INT
GTR6002G2 | VEGA BUNKER PLC : TEMPERATURE OUTPUT CHILLER 2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3071 | NA | 13870 | NA | 16416 | 3162 | 0 | EL6021_M180 |  | INT
GTR6002G3 | VEGA BUNKER PLC : TEMPERATURE INPUT DRY COOLER (SENSOR NOT AVAILABLE) CHILLER 2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6012DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3072 | NA | 13871 | NA | 16416 | 3164 | 0 | EL6021_M180 |  | INT
SPASMA0633 | SPARE SER 0633 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3073 | NA | 13872 | NA | 16416 | 3166 | 0 | EL6021_M180 |  | INT
SPASMA0634 | SPARE SER 0634 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3074 | NA | 13873 | NA | 16416 | 3168 | 0 | EL6021_M180 |  | INT
SPASMA0635 | SPARE SER 0635 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3075 | NA | 13874 | NA | 16416 | 3170 | 0 | EL6021_M180 |  | INT
SPASMA0636 | SPARE SER 0636 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3076 | NA | 13875 | NA | 16416 | 3172 | 0 | EL6021_M180 |  | INT
SPASMA0637 | SPARE SER 0637 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3077 | NA | 13876 | NA | 16416 | 3174 | 0 | EL6021_M180 |  | INT
SPASMA0638 | SPARE SER 0638 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3078 | NA | 13877 | NA | 16416 | 3176 | 0 | EL6021_M180 |  | INT
EUR6081V2 | TGBT ZLV ARRIVEE TM 7002 CAT.II Phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3077 | NA | 13146 | NA | 16416 | 1714 | 0 | EL6021_M178 |  | INT
SPASMA0639 | SPARE SER 0639 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3080 | NA | 13879 | NA | 16416 | 3180 | 0 | EL6021_M180 |  | INT
EUR6081V3 | TGBT ZLV ARRIVEE TM 7002 CAT.II Phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3078 | NA | 13147 | NA | 16416 | 1716 | 0 | EL6021_M178 |  | INT
SPASMA0640 | SPARE SER 0640 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3082 | NA | 13881 | NA | 16416 | 3184 | 0 | EL6021_M180 |  | INT
EWR6081PF | TGBT ZLV ARRIVEE TM 7002 CAT.II Power Factor | MA | N | RES | 1 | E |  |  | NA | 0.001 | -1 | 1 |  |  | -1 | 1 |  |  | E | [13 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3082 | NA | 13151 | NA | 16416 | 1724 | 0 | EL6021_M178 |  | INT
SPASMA0641 | SPARE SER 0641 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3084 | NA | 13883 | NA | 16416 | 3188 | 0 | EL6021_M180 |  | INT
EFR6081 | TGBT ZLV ARRIVEE TM 7002 CAT.II Frequency F | MA | N | RES | 1 | E |  |  | Hz | 0.01 | 23 | 67 |  |  | 23 | 67 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6081D | TGBT ZLV Arrivee TM7002 CAT II (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3083 | NA | 13152 | NA | 16416 | 1726 | 0 | EL6021_M178 |  | INT
SPASMA0642 | SPARE SER 0642 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3086 | NA | 13885 | NA | 16416 | 3192 | 0 | EL6021_M180 |  | INT
EIR6082I1 | TGBT ZLV ARRIVEE TM 7004 CAT.I Phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3090 | NA | 13159 | NA | 16416 | 1740 | 0 | EL6021_M178 |  | INT
SPASMA0643 | SPARE SER 0643 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3088 | NA | 13887 | NA | 16416 | 3196 | 0 | EL6021_M180 |  | INT
EIR6082I2 | TGBT ZLV ARRIVEE TM 7004 CAT.I Phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3091 | NA | 13160 | NA | 16416 | 1742 | 0 | EL6021_M178 |  | INT
SPASMA0644 | SPARE SER 0644 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3090 | NA | 13889 | NA | 16416 | 3200 | 0 | EL6021_M180 |  | INT
EIR6082I3 | TGBT ZLV ARRIVEE TM 7004 CAT.I Phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3092 | NA | 13161 | NA | 16416 | 1744 | 0 | EL6021_M178 |  | INT
SPASMA0645 | SPARE SER 0645 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3092 | NA | 13891 | NA | 16416 | 3204 | 0 | EL6021_M180 |  | INT
EUR608212 | TGBT ZLV ARRIVEE TM 7004 CAT.I Line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3093 | NA | 13162 | NA | 16416 | 1746 | 0 | EL6021_M178 |  | INT
SPASMA0646 | SPARE SER 0646 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3094 | NA | 13893 | NA | 16416 | 3208 | 0 | EL6021_M180 |  | INT
EUR608223 | TGBT ZLV ARRIVEE TM 7004 CAT.I Line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3094 | NA | 13163 | NA | 16416 | 1748 | 0 | EL6021_M178 |  | INT
SPASMA0647 | SPARE SER 0647 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3096 | NA | 13895 | NA | 16416 | 3212 | 0 | EL6021_M180 |  | INT
EUR608231 | TGBT ZLV ARRIVEE TM 7004 CAT.I Line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3095 | NA | 13164 | NA | 16416 | 1750 | 0 | EL6021_M178 |  | INT
SPASMA0648 | SPARE SER 0648 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3098 | NA | 13897 | NA | 16416 | 3216 | 0 | EL6021_M180 |  | INT
EUR6082V1 | TGBT ZLV ARRIVEE TM 7004 CAT.I Phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3096 | NA | 13165 | NA | 16416 | 1752 | 0 | EL6021_M178 |  | INT
SPASMA0649 | SPARE SER 0649 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3100 | NA | 13899 | NA | 16416 | 3220 | 0 | EL6021_M180 |  | INT
EUR6082V2 | TGBT ZLV ARRIVEE TM 7004 CAT.I Phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3097 | NA | 13166 | NA | 16416 | 1754 | 0 | EL6021_M178 |  | INT
SPASMA0650 | SPARE SER 0650 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3102 | NA | 13901 | NA | 16416 | 3224 | 0 | EL6021_M180 |  | INT
EUR6082V3 | TGBT ZLV ARRIVEE TM 7004 CAT.I Phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3098 | NA | 13167 | NA | 16416 | 1756 | 0 | EL6021_M178 |  | INT
SPASMA0651 | SPARE SER 0651 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3104 | NA | 13903 | NA | 16416 | 3228 | 0 | EL6021_M180 |  | INT
EWR6082PF | TGBT ZLV ARRIVEE TM 7004 CAT.I Power Factor | MA | N | RES | 1 | E |  |  | NA | 0.001 | -1 | 1 |  |  | -1 | 1 |  |  | E | [13 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3102 | NA | 13171 | NA | 16416 | 1764 | 0 | EL6021_M178 |  | INT
SPASMA0652 | SPARE SER 0652 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3106 | NA | 13905 | NA | 16416 | 3232 | 0 | EL6021_M180 |  | INT
EFR6082 | TGBT ZLV ARRIVEE TM 7004 CAT.I Frequency F | MA | N | RES | 1 | E |  |  | Hz | 0.01 | 23 | 67 |  |  | 23 | 67 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6082D | TGBT ZLV Arrivee TM7004 CAT I (E61) | Energie TGBT et UPS VEGA (E) - E61 |  | 4 |  |  | 3103 | NA | 13172 | NA | 16416 | 1766 | 0 | EL6021_M178 |  | INT
SPASMA0653 | SPARE SER 0653 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3108 | NA | 13907 | NA | 16416 | 3236 | 0 | EL6021_M180 |  | INT
EIR6083I1 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3110 | NA | 13179 | NA | 16416 | 1780 | 0 | EL6021_M178 |  | INT
SPASMA0654 | SPARE SER 0654 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3110 | NA | 13909 | NA | 16416 | 3240 | 0 | EL6021_M180 |  | INT
EIR6083I2 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3111 | NA | 13180 | NA | 16416 | 1782 | 0 | EL6021_M178 |  | INT
SPASMA0655 | SPARE SER 0655 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3112 | NA | 13911 | NA | 16416 | 3244 | 0 | EL6021_M180 |  | INT
EIR6083I3 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3112 | NA | 13181 | NA | 16416 | 1784 | 0 | EL6021_M178 |  | INT
SPASMA0656 | SPARE SER 0656 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3114 | NA | 13913 | NA | 16416 | 3248 | 0 | EL6021_M180 |  | INT
EUR608312 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3113 | NA | 13182 | NA | 16416 | 1786 | 0 | EL6021_M178 |  | INT
SPASMA0657 | SPARE SER 0657 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3116 | NA | 13915 | NA | 16416 | 3252 | 0 | EL6021_M180 |  | INT
EUR608323 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3114 | NA | 13183 | NA | 16416 | 1788 | 0 | EL6021_M178 |  | INT
SPASMA0658 | SPARE SER 0658 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3118 | NA | 13917 | NA | 16416 | 3256 | 0 | EL6021_M180 |  | INT
SPASMA0659 | SPARE SER 0659 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3119 | NA | 13918 | NA | 16416 | 3258 | 0 | EL6021_M180 |  | INT
SPASMA0660 | SPARE SER 0660 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3120 | NA | 13919 | NA | 16416 | 3260 | 0 | EL6021_M180 |  | INT
SPASMA0661 | SPARE SER 0661 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3121 | NA | 13920 | NA | 16416 | 3262 | 0 | EL6021_M180 |  | INT
SPASMA0662 | SPARE SER 0662 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3122 | NA | 13921 | NA | 16416 | 3264 | 0 | EL6021_M180 |  | INT
SPASMA0663 | SPARE SER 0663 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3123 | NA | 13922 | NA | 16416 | 3266 | 0 | EL6021_M180 |  | INT
SPASMA0664 | SPARE SER 0664 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3124 | NA | 13923 | NA | 16416 | 3268 | 0 | EL6021_M180 |  | INT
EUR608331 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3115 | NA | 13184 | NA | 16416 | 1790 | 0 | EL6021_M178 |  | INT
SPASMA0665 | SPARE SER 0665 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3126 | NA | 13925 | NA | 16416 | 3272 | 0 | EL6021_M180 |  | INT
EUR6083V1 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3116 | NA | 13185 | NA | 16416 | 1792 | 0 | EL6021_M178 |  | INT
SPASMA0666 | SPARE SER 0666 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3128 | NA | 13927 | NA | 16416 | 3276 | 0 | EL6021_M180 |  | INT
EUR6083V2 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3117 | NA | 13186 | NA | 16416 | 1794 | 0 | EL6021_M178 |  | INT
SPASMA0667 | SPARE SER 0667 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3130 | NA | 13929 | NA | 16416 | 3280 | 0 | EL6021_M180 |  | INT
EUR6083V3 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3118 | NA | 13187 | NA | 16416 | 1796 | 0 | EL6021_M178 |  | INT
SPASMA0668 | SPARE SER 0668 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3132 | NA | 13931 | NA | 16416 | 3284 | 0 | EL6021_M180 |  | INT
EWR6083PF | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Power Factor | MA | N | RES | 1 | E |  |  | NA | 0.001 | -1 | 1 |  |  | -1 | 1 |  |  | E | [13 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3122 | NA | 13191 | NA | 16416 | 1804 | 0 | EL6021_M178 |  | INT
SPASMA0669 | SPARE SER 0669 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3134 | NA | 13933 | NA | 16416 | 3288 | 0 | EL6021_M180 |  | INT
EFR6083 | TGBT-C ZLV ARRIVEE TM 7001 CAT.II Frequency F | MA | N | RES | 1 | E |  |  | Hz | 0.01 | 23 | 67 |  |  | 23 | 67 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6083D | TGBT ZLV CLIM Arrivee TM7001 CAT II (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3123 | NA | 13192 | NA | 16416 | 1806 | 0 | EL6021_M178 |  | INT
SPASMA0670 | SPARE SER 0670 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3136 | NA | 13935 | NA | 16416 | 3292 | 0 | EL6021_M180 |  | INT
CER6000 | VEGA BUNKER PLC : OPENNING POURCENTAGE HOT WATER CONTROL VALVE HOT WATER PRODUCTION | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6126K10 |  |  |  | 6 |  |  | 3137 | NA | 13936 | NA | 16416 | 3294 | 0 | EL6021_M180 |  | INT
GER6001T | VEGA BUNKER PLC : OPENNING POURCENTAGE COLD WATER CONTROL VALVE FAN CTA M01 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6126K10 | HVAC04 | HVAC |  | 6 |  |  | 3138 | NA | 13937 | NA | 16416 | 3296 | 0 | EL6021_M180 |  | INT
CER6001T | VEGA BUNKER PLC : OPENNING POURCENTAGE HOT WATER CONTROL VALVE FAN CTA M01 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6126K10 | HVAC04 | HVAC |  | 6 |  |  | 3139 | NA | 13938 | NA | 16416 | 3298 | 0 | EL6021_M180 |  | INT
GGC6126G1 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) CHILLER | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 3 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3140 | NA | 13939 | NA | 16416 | 3300 | 0 | EL6021_M180 |  | INT
GGC6126G2 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) CHILLER | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 3 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3141 | NA | 13940 | NA | 16416 | 3302 | 0 | EL6021_M180 |  | INT
GGC6126G3 | VEGA BUNKER PLC : PRIORITY ORDER 3 (STANDBY) CHILLER | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 3 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3142 | NA | 13941 | NA | 16416 | 3304 | 0 | EL6021_M180 |  | INT
EIR6084I1 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3130 | NA | 13199 | NA | 16416 | 1820 | 0 | EL6021_M178 |  | INT
EIR6084I2 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3131 | NA | 13200 | NA | 16416 | 1822 | 0 | EL6021_M178 |  | INT
SPASMA0671 | SPARE SER 0671 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3145 | NA | 13944 | NA | 16416 | 3310 | 0 | EL6021_M180 |  | INT
GGC6012F21 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) SUPPLY COLD WATER GANTRY | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3146 | NA | 13945 | NA | 16416 | 3312 | 0 | EL6021_M180 |  | INT
GGC6012F22 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) SUPPLY COLD WATER GANTRY | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3147 | NA | 13946 | NA | 16416 | 3314 | 0 | EL6021_M180 |  | INT
GGC6045F11 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) SUPPLY COLD WATER BUNKER | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3148 | NA | 13947 | NA | 16416 | 3316 | 0 | EL6021_M180 |  | INT
GGC6045F12 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) SUPPLY COLD WATER BUNKER | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3149 | NA | 13948 | NA | 16416 | 3318 | 0 | EL6021_M180 |  | INT
CGC6045F31 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) SUPPLY HOT WATER BUNKER/GANTRY | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3150 | NA | 13949 | NA | 16416 | 3320 | 0 | EL6021_M180 |  | INT
CGC6045F32 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) SUPPLY HOT WATER BUNKER/GANTRY | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3151 | NA | 13950 | NA | 16416 | 3322 | 0 | EL6021_M180 |  | INT
VGC6126T1 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) CTA | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3152 | NA | 13951 | NA | 16416 | 3324 | 0 | EL6021_M180 |  | INT
VGC6126T2 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) CTA | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3153 | NA | 13952 | NA | 16416 | 3326 | 0 | EL6021_M180 |  | INT
VGC6002A1 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) AC CABINET (SCHNEIDER) 002 | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3154 | NA | 13953 | NA | 16416 | 3328 | 0 | EL6021_M180 |  | INT
VGC6002A2 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) AC CABINET (SCHNEIDER) 002 | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3155 | NA | 13954 | NA | 16416 | 3330 | 0 | EL6021_M180 |  | INT
VGC6004A1 | VEGA BUNKER PLC : PRIORITY ORDER 1 (NORMAL) AC CABINET (SCHNEIDER) 004 | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 0 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3156 | NA | 13955 | NA | 16416 | 3332 | 0 | EL6021_M180 |  | INT
VGC6004A2 | VEGA BUNKER PLC : PRIORITY ORDER 2 (SAFE) AC CABINET (SCHNEIDER) 004 | MA |  | RES | 1 | C |  |  | NA | 1 | 2 | 2 | [20 empty] | POL | 6000 | VZC6126D | HVAC02 | HVAC |  | 6 |  |  | 3157 | NA | 13956 | NA | 16416 | 3334 | 0 | EL6021_M180 |  | INT
SPASMA0672 | SPARE SER 0672 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3158 | NA | 13957 | NA | 16416 | 3336 | 0 | EL6021_M180 |  | INT
SPASMA0673 | SPARE SER 0673 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3159 | NA | 13958 | NA | 16416 | 3338 | 0 | EL6021_M180 |  | INT
VZC6126W1 | VEGA BUNKER PLC X80-1 : WATCHDOG | MA |  | RES | 1 | A |  |  | NA |  | 0 | 65535 | [20 empty] | POL | 6000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01);HVAC01 | HVAC |  | 6 |  |  | 3160 | NA | 13959 | NA | 16416 | 3340 | 0 | EL6021_M180 |  | INT
VZC6126W2 | VEGA BUNKER PLC X80-2 : WATCHDOG | MA |  | RES | 1 | A |  |  | NA |  | 0 | 65535 | [20 empty] | POL | 6000 | VZC6126D | CV0B X80 HVAC Bunker PLC Infos (HVAC01);HVAC01 | HVAC |  | 6 |  |  | 3161 | NA | 13960 | NA | 16416 | 3342 | 0 | EL6021_M180 |  | INT
VTR6002T | VEGA BUNKER PLC : TEMPERATURE AFTER COOL BATTERY FAN CTA M02 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z25 | HVAC04 | HVAC |  | 6 |  |  | 3180 | NA | 13979 | NA | 16416 | 3380 | 0 | EL6021_M180 |  | INT
VTR6002S | VEGA BUNKER PLC : PULSE TEMPERATURE FAN CTA M02 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z26 | HVAC04 | HVAC |  | 6 |  |  | 3181 | NA | 13980 | NA | 16416 | 3382 | 0 | EL6021_M180 |  | INT
SPASMA0674 | SPARE SER 0674 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3182 | NA | 13981 | NA | 16416 | 3384 | 0 | EL6021_M180 |  | INT
SPASMA0675 | SPARE SER 0675 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3183 | NA | 13982 | NA | 16416 | 3386 | 0 | EL6021_M180 |  | INT
GWR6003G | VEGA BUNKER PLC : POWER CHILLER 3 | MA |  | RES | 1 | C |  |  | KW | 1 | 0 | 100 | [20 empty] | POL | 6000 | GGF6003DC | Details Groupes Froids (HVAC03) | HVAC |  | 6 |  |  | 3184 | NA | 13983 | NA | 16416 | 3388 | 0 | EL6021_M180 |  | INT
GTR6003G1 | VEGA BUNKER PLC : TEMPERATURE INPUT CHILLER 3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6003DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3185 | NA | 13984 | NA | 16416 | 3390 | 0 | EL6021_M180 |  | INT
GTR6003G2 | VEGA BUNKER PLC : TEMPERATURE OUTPUT CHILLER 3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6003DC | Details Groupes Froids (HVAC03);HVAC03 | HVAC |  | 6 |  |  | 3186 | NA | 13985 | NA | 16416 | 3392 | 0 | EL6021_M180 |  | INT
GTR6003G3 | VEGA BUNKER PLC : TEMPERATURE INPUT DRY COOLER CHILLER 3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | GGF6003DC | HVAC03 | HVAC |  | 6 |  |  | 3187 | NA | 13986 | NA | 16416 | 3394 | 0 | EL6021_M180 |  | INT
SPASMA0676 | SPARE SER 0676 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3188 | NA | 13987 | NA | 16416 | 3396 | 0 | EL6021_M180 |  | INT
SPASMA0677 | SPARE SER 0677 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3189 | NA | 13988 | NA | 16416 | 3398 | 0 | EL6021_M180 |  | INT
SPASMA0678 | SPARE SER 0678 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3190 | NA | 13989 | NA | 16416 | 3400 | 0 | EL6021_M180 |  | INT
SPASMA0679 | SPARE SER 0679 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3191 | NA | 13990 | NA | 16416 | 3402 | 0 | EL6021_M180 |  | INT
SPASMA0680 | SPARE SER 0680 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3192 | NA | 13991 | NA | 16416 | 3404 | 0 | EL6021_M180 |  | INT
SPASMA0681 | SPARE SER 0681 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3193 | NA | 13992 | NA | 16416 | 3406 | 0 | EL6021_M180 |  | INT
EIR6084I3 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3132 | NA | 13201 | NA | 16416 | 1824 | 0 | EL6021_M178 |  | INT
SPASMA0682 | SPARE SER 0682 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3195 | NA | 13994 | NA | 16416 | 3410 | 0 | EL6021_M180 |  | INT
EUR608412 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3133 | NA | 13202 | NA | 16416 | 1826 | 0 | EL6021_M178 |  | INT
SPASMA0683 | SPARE SER 0683 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3197 | NA | 13996 | NA | 16416 | 3414 | 0 | EL6021_M180 |  | INT
EUR608423 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3134 | NA | 13203 | NA | 16416 | 1828 | 0 | EL6021_M178 |  | INT
SPASMA0684 | SPARE SER 0684 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3199 | NA | 13998 | NA | 16416 | 3418 | 0 | EL6021_M180 |  | INT
EUR608431 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3135 | NA | 13204 | NA | 16416 | 1830 | 0 | EL6021_M178 |  | INT
SPASMA0685 | SPARE SER 0685 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3201 | NA | 14000 | NA | 16416 | 3422 | 0 | EL6021_M180 |  | INT
EUR6084V1 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3136 | NA | 13205 | NA | 16416 | 1832 | 0 | EL6021_M178 |  | INT
SPASMA0686 | SPARE SER 0686 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3203 | NA | 14002 | NA | 16416 | 3426 | 0 | EL6021_M180 |  | INT
EUR6084V2 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3137 | NA | 13206 | NA | 16416 | 1834 | 0 | EL6021_M178 |  | INT
SPASMA0687 | SPARE SER 0687 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3205 | NA | 14004 | NA | 16416 | 3430 | 0 | EL6021_M180 |  | INT
EUR6084V3 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 32767 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3138 | NA | 13207 | NA | 16416 | 1836 | 0 | EL6021_M178 |  | INT
SPASMA0688 | SPARE SER 0688 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3207 | NA | 14006 | NA | 16416 | 3434 | 0 | EL6021_M180 |  | INT
EWR6084PF | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Power Factor | MA | N | RES | 1 | E |  |  | NA | 0.001 | -1 | 1 |  |  | -1 | 1 |  |  | E | [13 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3142 | NA | 13211 | NA | 16416 | 1844 | 0 | EL6021_M178 |  | INT
SPASMA0689 | SPARE SER 0689 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3209 | NA | 14008 | NA | 16416 | 3438 | 0 | EL6021_M180 |  | INT
EFR6084 | TGBT-C ZLV ARRIVEE TM 7003 CAT.I Frequency F | MA | N | RES | 1 | E |  |  | Hz | 0.01 | 23 | 67 |  |  | 23 | 67 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6084D | TGBT ZLV CLIM Arrivee TM7003 CAT I (E62) | Energie TGBT et UPS VEGA (E) - E62 |  | 4 |  |  | 3143 | NA | 13212 | NA | 16416 | 1846 | 0 | EL6021_M178 |  | INT
SPASMA0690 | SPARE SER 0690 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3211 | NA | 14010 | NA | 16416 | 3442 | 0 | EL6021_M180 |  | INT
EIR6091I1 | TGBT CAT.IIIA Phase current I1 | MA | N | RES | 1 | E |  |  | A | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3150 | NA | 13219 | NA | 16416 | 1860 | 0 | EL6021_M178 |  | I32
SPASMA0691 | SPARE SER 0691 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3213 | NA | 14012 | NA | 16416 | 3446 | 0 | EL6021_M180 |  | INT
EIR6091I2 | TGBT CAT.IIIA Phase current I2 | MA | N | RES | 1 | E |  |  | A | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3152 | NA | 13221 | NA | 16416 | 1864 | 0 | EL6021_M178 |  | I32
SPASMA0692 | SPARE SER 0692 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3215 | NA | 14014 | NA | 16416 | 3450 | 0 | EL6021_M180 |  | INT
EIR6091I3 | TGBT CAT.IIIA Phase current I3 | MA | N | RES | 1 | E |  |  | A | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3154 | NA | 13223 | NA | 16416 | 1868 | 0 | EL6021_M178 |  | I32
SPASMA0693 | SPARE SER 0693 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3217 | NA | 14016 | NA | 16416 | 3454 | 0 | EL6021_M180 |  | INT
EUR609112 | TGBT CAT.IIIA Line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3156 | NA | 13225 | NA | 16416 | 1872 | 0 | EL6021_M178 |  | I32
SPASMA0694 | SPARE SER 0694 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3219 | NA | 14018 | NA | 16416 | 3458 | 0 | EL6021_M180 |  | INT
EUR609123 | TGBT CAT.IIIA Line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3158 | NA | 13227 | NA | 16416 | 1876 | 0 | EL6021_M178 |  | I32
SPASMA0695 | SPARE SER 0695 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3221 | NA | 14020 | NA | 16416 | 3462 | 0 | EL6021_M180 |  | INT
EUR609131 | TGBT CAT.IIIA Line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3160 | NA | 13229 | NA | 16416 | 1880 | 0 | EL6021_M178 |  | I32
SPASMA0696 | SPARE SER 0696 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3223 | NA | 14022 | NA | 16416 | 3466 | 0 | EL6021_M180 |  | INT
EUR6091V1 | TGBT CAT.IIIA Phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3162 | NA | 13231 | NA | 16416 | 1884 | 0 | EL6021_M178 |  | I32
SPASMA0697 | SPARE SER 0697 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3225 | NA | 14024 | NA | 16416 | 3470 | 0 | EL6021_M180 |  | INT
EUR6091V2 | TGBT CAT.IIIA Phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3164 | NA | 13233 | NA | 16416 | 1888 | 0 | EL6021_M178 |  | I32
SPASMA0698 | SPARE SER 0698 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3227 | NA | 14026 | NA | 16416 | 3474 | 0 | EL6021_M180 |  | INT
SPASMA0699 | SPARE SER 0699 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3229 | NA | 14028 | NA | 16416 | 3478 | 0 | EL6021_M180 |  | INT
EUR6091V3 | TGBT CAT.IIIA Phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3166 | NA | 13235 | NA | 16416 | 1892 | 0 | EL6021_M178 |  | I32
SPASMA0700 | SPARE SER 0700 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3231 | NA | 14030 | NA | 16416 | 3482 | 0 | EL6021_M180 |  | INT
EFR6091 | TGBT CAT.IIIA Frequency F | MA | N | RES | 1 | E |  |  | Hz | 0.01 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3168 | NA | 13237 | NA | 16416 | 1896 | 0 | EL6021_M178 |  | I32
SPASMA0701 | SPARE SER 0701 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3233 | NA | 14032 | NA | 16416 | 3486 | 0 | EL6021_M180 |  | INT
EWR6091S | TGBT CAT.IIIA Total Apparent Power S | MA | N | RES | 1 | E |  |  | kVA | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3174 | NA | 13243 | NA | 16416 | 1908 | 0 | EL6021_M178 |  | I32
SPASMA0702 | SPARE SER 0702 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3235 | NA | 14034 | NA | 16416 | 3490 | 0 | EL6021_M180 |  | INT
EWR6091PF | TGBT CAT.IIIA Power Factor | MA | N | RES | 1 | E |  |  | NA | 0.01 | -1 | 1 |  |  | -1 | 1 |  |  | E | [13 empty] | POL | 6000 | ESY6091D | Arrivee TGBT CAT IIIA (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3176 | NA | 13245 | NA | 16416 | 1912 | 0 | EL6021_M178 |  | I32
SPASMA0703 | SPARE SER 0703 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3237 | NA | 14036 | NA | 16416 | 3494 | 0 | EL6021_M180 |  | INT
EIR6092I1 | TGBT CAT.IIIB Phase current I1 | MA | N | RES | 1 | E |  |  | A | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3190 | NA | 13259 | NA | 16416 | 1940 | 0 | EL6021_M178 |  | I32
SPASMA0704 | SPARE SER 0704 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3241 | NA | 14040 | NA | 16416 | 3502 | 0 | EL6021_M180 |  | INT
EIR6092I2 | TGBT CAT.IIIB Phase current I2 | MA | N | RES | 1 | E |  |  | A | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3192 | NA | 13261 | NA | 16416 | 1944 | 0 | EL6021_M178 |  | I32
SPASMA0705 | SPARE SER 0705 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3243 | NA | 14042 | NA | 16416 | 3506 | 0 | EL6021_M180 |  | INT
EIR6092I3 | TGBT CAT.IIIB Phase current I3 | MA | N | RES | 1 | E |  |  | A | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3194 | NA | 13263 | NA | 16416 | 1948 | 0 | EL6021_M178 |  | I32
SPASMA0706 | SPARE SER 0706 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3245 | NA | 14044 | NA | 16416 | 3510 | 0 | EL6021_M180 |  | INT
EUR609212 | TGBT CAT.IIIB Line to line voltage U12 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3196 | NA | 13265 | NA | 16416 | 1952 | 0 | EL6021_M178 |  | I32
SPASMA0707 | SPARE SER 0707 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3247 | NA | 14046 | NA | 16416 | 3514 | 0 | EL6021_M180 |  | INT
EUR609223 | TGBT CAT.IIIB Line to line voltage U23 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3198 | NA | 13267 | NA | 16416 | 1956 | 0 | EL6021_M178 |  | I32
SPASMA0708 | SPARE SER 0708 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3249 | NA | 14048 | NA | 16416 | 3518 | 0 | EL6021_M180 |  | INT
GER6002T | VEGA BUNKER PLC : OPENING POURCENTAGE COLD WATER CONTROL VALVE FAN CTA M02 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6126K34 | HVAC04 | HVAC |  | 6 |  |  | 3250 | NA | 14049 | NA | 16416 | 3520 | 0 | EL6021_M180 |  | INT
CER6002T | VEGA BUNKER PLC : OPENING POURCENTAGE HOT WATER CONTROL VALVE FAN CTA M02 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6126K34 | HVAC04 | HVAC |  | 6 |  |  | 3251 | NA | 14050 | NA | 16416 | 3522 | 0 | EL6021_M180 |  | INT
EUR609231 | TGBT CAT.IIIB Line to line voltage U31 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3200 | NA | 13269 | NA | 16416 | 1960 | 0 | EL6021_M178 |  | I32
SPASMA0709 | SPARE SER 0709 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3253 | NA | 14052 | NA | 16416 | 3526 | 0 | EL6021_M180 |  | INT
EUR6092V1 | TGBT CAT.IIIB Phase voltage V1 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3202 | NA | 13271 | NA | 16416 | 1964 | 0 | EL6021_M178 |  | I32
SPASMA1127 | SPARE SER 0710 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3255 | NA | 14054 | NA | 16416 | 3530 | 0 | EL6021_M180 |  | INT
EUR6092V2 | TGBT CAT.IIIB Phase voltage V2 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3204 | NA | 13273 | NA | 16416 | 1968 | 0 | EL6021_M178 |  | I32
SPASMA0710 | SPARE SER 0710 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 6 |  |  | 3257 | NA | 14056 | NA | 16416 | 3534 | 0 | EL6021_M180 |  | INT
EUR6092V3 | TGBT CAT.IIIB Phase voltage V3 | MA | N | RES | 1 | E |  |  | V | 0.001 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3206 | NA | 13275 | NA | 16416 | 1972 | 0 | EL6021_M178 |  | I32
EFR6092 | TGBT CAT.IIIB Frequency F | MA | N | RES | 1 | E |  |  | Hz | 0.01 | 0 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3208 | NA | 13277 | NA | 16416 | 1976 | 0 | EL6021_M178 |  | I32
VTR6102R | VEGA GANTRY PLC : TEMPERATURE RETURN AIR FAN CTA P03 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z1 | HVAC14 | HVAC |  | 7 |  |  | 3050 | NA | 14197 | NA | 16416 | 3816 | 0 | EL6021_M181 |  | INT
VHR6102R | VEGA GANTRY PLC : HYGROMETRY RETURN AIR FAN CTA P03 | MA |  | RES | 1 | C |  |  | %Hr | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6401Z2 | HVAC14 | HVAC |  | 7 |  |  | 3051 | NA | 14198 | NA | 16416 | 3818 | 0 | EL6021_M181 |  | INT
EWR6092S | TGBT CAT.IIIB Total Apparent Power S | MA | N | RES | 1 | E |  |  | kVA | 0.001 | -2150000000 | 2150000000 |  |  | 0 |  |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3214 | NA | 13283 | NA | 16416 | 1988 | 0 | EL6021_M178 |  | I32
EWR6092PF | TGBT CAT.IIIB Power Factor | MA | N | RES | 1 | E |  |  | NA | 0.01 | -1 | 1 |  |  | -1 | 1 |  |  | E | [13 empty] | POL | 6000 | ESY6092D | Arrivee TGBT CAT IIIB (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3216 | NA | 13285 | NA | 16416 | 1992 | 0 | EL6021_M178 |  | I32
VTR6401T1 | VEGA GANTRY PLC : DEW POINT TEMPERATURE FAN CTA P01 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z5 | HVAC13 | HVAC |  | 7 |  |  | 3054 | NA | 14201 | NA | 16416 | 3824 | 0 | EL6021_M181 |  | INT
VTR6401S1 | VEGA GANTRY PLC : PULSE TEMPERATURE FAN CTA P01 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z6 | HVAC13 | HVAC |  | 7 |  |  | 3055 | NA | 14202 | NA | 16416 | 3826 | 0 | EL6021_M181 |  | INT
VTR6102T | VEGA GANTRY PLC : DEW POINT TEMPERATURE FAN CTA P03 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z7 | HVAC14 | HVAC |  | 7 |  |  | 3056 | NA | 14203 | NA | 16416 | 3828 | 0 | EL6021_M181 |  | INT
VTR6102S | VEGA GANTRY PLC : PULSE TEMPERATURE FAN CTA P03 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z8 | HVAC14 | HVAC |  | 7 |  |  | 3057 | NA | 14204 | NA | 16416 | 3830 | 0 | EL6021_M181 |  | INT
EIR6071I1 | Onduleur IIIA-1 UL7001 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3230 | NA | 13299 | NA | 16416 | 2020 | 0 | EL6021_M178 |  | UINT
EIR6071I2 | Onduleur IIIA-1 UL7001 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3231 | NA | 13300 | NA | 16416 | 2022 | 0 | EL6021_M178 |  | UINT
VER6102C1 | VEGA GANTRY PLC : POSITION COMMAND FRESH AIR MOTORISED DAMPER 102.1 (CTA 3) | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6401Z11 | HVAC14 | HVAC |  | 7 |  |  | 3060 | NA | 14207 | NA | 16416 | 3836 | 0 | EL6021_M181 |  | INT
VER6102C3 | VEGA GANTRY PLC : POSITION COMMAND RETURN AIR MOTORISED DAMPER 102.3 (CTA 3) | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6401Z12 | HVAC14 | HVAC |  | 7 |  |  | 3061 | NA | 14208 | NA | 16416 | 3838 | 0 | EL6021_M181 |  | INT
SPASMA0888 | SPARE SER 0888 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3062 | NA | 14209 | NA | 16416 | 3840 | 0 | EL6021_M181 |  | INT
SPASMA0889 | SPARE SER 0889 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3063 | NA | 14210 | NA | 16416 | 3842 | 0 | EL6021_M181 |  | INT
SPASMA0890 | SPARE SER 0890 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3064 | NA | 14211 | NA | 16416 | 3844 | 0 | EL6021_M181 |  | INT
VTR6502V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 502.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3065 | NA | 14212 | NA | 16416 | 3846 | 0 | EL6021_M181 |  | INT
SPASMA0891 | SPARE SER 0891 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3066 | NA | 14213 | NA | 16416 | 3848 | 0 | EL6021_M181 |  | INT
VTR6401V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 401.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3067 | NA | 14214 | NA | 16416 | 3850 | 0 | EL6021_M181 |  | INT
SPASMA0892 | SPARE SER 0892 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3068 | NA | 14215 | NA | 16416 | 3852 | 0 | EL6021_M181 |  | INT
VTR6301V2 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 301.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3069 | NA | 14216 | NA | 16416 | 3854 | 0 | EL6021_M181 |  | INT
SPASMA0893 | SPARE SER 0893 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3070 | NA | 14217 | NA | 16416 | 3856 | 0 | EL6021_M181 |  | INT
VTR6202V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 202.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3071 | NA | 14218 | NA | 16416 | 3858 | 0 | EL6021_M181 |  | INT
SPASMA0894 | SPARE SER 0894 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3072 | NA | 14219 | NA | 16416 | 3860 | 0 | EL6021_M181 |  | INT
VTR6102V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 102.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3073 | NA | 14220 | NA | 16416 | 3862 | 0 | EL6021_M181 |  | INT
SPASMA0895 | SPARE SER 0895 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3074 | NA | 14221 | NA | 16416 | 3864 | 0 | EL6021_M181 |  | INT
GER6401T1 | VEGA GANTRY PLC : OPENING POURCENTAGE COLD WATER VALVE FAN CTA P01 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC13 | HVAC |  | 7 |  |  | 3075 | NA | 14222 | NA | 16416 | 3866 | 0 | EL6021_M181 |  | INT
CER6401T1 | VEGA GANTRY PLC : OPENING POURCENTAGE HOT WATER VALVE FAN CTA P01 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC13 | HVAC |  | 7 |  |  | 3076 | NA | 14223 | NA | 16416 | 3868 | 0 | EL6021_M181 |  | INT
GER6102T | VEGA GANTRY PLC : OPENING POURCENTAGE COLD WATER VALVE FAN CTA P03 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3077 | NA | 14224 | NA | 16416 | 3870 | 0 | EL6021_M181 |  | INT
CER6102T | VEGA GANTRY PLC : OPENING POURCENTAGE HOT WATER VALVE FAN CTA P03 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3078 | NA | 14225 | NA | 16416 | 3872 | 0 | EL6021_M181 |  | INT
VER6102N | VEGA GANTRY PLC : OPENING POURCENTAGE FRESH AIR MOTORISED DAMPER FAN CTA P03 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3079 | NA | 14226 | NA | 16416 | 3874 | 0 | EL6021_M181 |  | INT
VER6102R | VEGA GANTRY PLC : OPENING POURCENTAGE RETURN AIR MOTORISED DAMPER FAN CTA P03 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3080 | NA | 14227 | NA | 16416 | 3876 | 0 | EL6021_M181 |  | INT
VTR6101V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 101.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC1 | HVAC18 | HVAC |  | 7 |  |  | 3081 | NA | 14228 | NA | 16416 | 3878 | 0 | EL6021_M181 |  | INT
SPASMA0896 | SPARE SER 0896 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3082 | NA | 14229 | NA | 16416 | 3880 | 0 | EL6021_M181 |  | INT
SPASMA0897 | SPARE SER 0897 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3083 | NA | 14230 | NA | 16416 | 3882 | 0 | EL6021_M181 |  | INT
VGC6401T1 | VEGA GANTRY PLC : PRIORITY ORDER 1 (NORMAL) CTA | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6401D | HVAC02 | HVAC |  | 7 |  |  | 3084 | NA | 14231 | NA | 16416 | 3884 | 0 | EL6021_M181 |  | INT
VGC6401T2 | VEGA GANTRY PLC : PRIORITY ORDER 2 (SAFE) CTA | MA |  | RES | 1 | C |  |  | NA | 1 | 0 | 2 | [20 empty] | POL | 6000 | VZC6401D | HVAC02 | HVAC |  | 7 |  |  | 3085 | NA | 14232 | NA | 16416 | 3886 | 0 | EL6021_M181 |  | INT
SPASMA0898 | SPARE SER 0898 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3086 | NA | 14233 | NA | 16416 | 3888 | 0 | EL6021_M181 |  | INT
SPASMA0899 | SPARE SER 0899 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3087 | NA | 14234 | NA | 16416 | 3890 | 0 | EL6021_M181 |  | INT
SPASMA0900 | SPARE SER 0900 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3088 | NA | 14235 | NA | 16416 | 3892 | 0 | EL6021_M181 |  | INT
SPASMA0901 | SPARE SER 0901 | MA | N | RES | [28 empty] | POL | 10000 |  |  |  |  | 7 |  |  | 3089 | NA | 14236 | NA | 16416 | 3894 | 0 | EL6021_M181 |  | INT
VZC6401W1 | VEGA GANTRY PLC X80-1 : WATCHDOG | MA |  | RES | 1 | A |  |  | NA |  | 0 | 65535 | [20 empty] | POL | 6000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01);HVAC01 | HVAC |  | 7 |  |  | 3090 | NA | 14237 | NA | 16416 | 3896 | 0 | EL6021_M181 |  | INT
VZC6401W2 | VEGA GANTRY PLC X80-2 : WATCHDOG | MA |  | RES | 1 | A |  |  | NA |  | 0 | 65535 | [20 empty] | POL | 6000 | VZC6401D | CV0G X80 HVAC Gantry PLC Infos (HVAC01);HVAC01 | HVAC |  | 7 |  |  | 3091 | NA | 14238 | NA | 16416 | 3898 | 0 | EL6021_M181 |  | INT
VER6201C1 | VEGA GANTRY PLC : POSITION COMMAND FRESH AIR MOTORISED DAMPER FAN CTA P04 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6401Z15 | HVAC14 | HVAC |  | 7 |  |  | 3182 | NA | 14329 | NA | 16416 | 4080 | 0 | EL6021_M181 |  | INT
VER6201C4 | VEGA GANTRY PLC : POSITION COMMAND RETURN AIR MOTORISED DAMPER FAN CTA P04 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 | VZC6401Z16 | HVAC14 | HVAC |  | 7 |  |  | 3183 | NA | 14330 | NA | 16416 | 4082 | 0 | EL6021_M181 |  | INT
VTR6401T2 | VEGA GANTRY PLC : DEW POINT TEMPERATURE FAN CTA P02 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z17 | HVAC13 | HVAC |  | 7 |  |  | 3184 | NA | 14331 | NA | 16416 | 4084 | 0 | EL6021_M181 |  | INT
VTR6401S2 | VEGA GANTRY PLC : PULSE TEMPERATURE FAN CTA P02 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z18 | HVAC13 | HVAC |  | 7 |  |  | 3185 | NA | 14332 | NA | 16416 | 4086 | 0 | EL6021_M181 |  | INT
VTR6202T | VEGA GANTRY PLC : DEW POINT TEMPERATURE FAN CTA P04 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z19 | HVAC14 | HVAC |  | 7 |  |  | 3186 | NA | 14333 | NA | 16416 | 4088 | 0 | EL6021_M181 |  | INT
VTR6202S | VEGA GANTRY PLC : PULSE TEMPERATURE FAN CTA P04 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z20 | HVAC14 | HVAC |  | 7 |  |  | 3187 | NA | 14334 | NA | 16416 | 4090 | 0 | EL6021_M181 |  | INT
SPASMA0902 | SPARE SER 0902 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3188 | NA | 14335 | NA | 16416 | 4092 | 0 | EL6021_M181 |  | INT
SPASMA0903 | SPARE SER 0903 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3189 | NA | 14336 | NA | 16416 | 4094 | 0 | EL6021_M181 |  | INT
SPASMA0904 | SPARE SER 0904 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3190 | NA | 14337 | NA | 16416 | 4096 | 0 | EL6021_M181 |  | INT
SPASMA0905 | SPARE SER 0905 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3191 | NA | 14338 | NA | 16416 | 4098 | 0 | EL6021_M181 |  | INT
VTR6501V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 501.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3192 | NA | 14339 | NA | 16416 | 4100 | 0 | EL6021_M181 |  | INT
SPASMA0906 | SPARE SER 0906 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3193 | NA | 14340 | NA | 16416 | 4102 | 0 | EL6021_M181 |  | INT
VTR6801V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 801.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3194 | NA | 14341 | NA | 16416 | 4104 | 0 | EL6021_M181 |  | INT
SPASMA0907 | SPARE SER 0907 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3195 | NA | 14342 | NA | 16416 | 4106 | 0 | EL6021_M181 |  | INT
VTR6301V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 301.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3196 | NA | 14343 | NA | 16416 | 4108 | 0 | EL6021_M181 |  | INT
SPASMA0908 | SPARE SER 0908 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3197 | NA | 14344 | NA | 16416 | 4110 | 0 | EL6021_M181 |  | INT
VTR6201V1 | VEGA GANTRY PLC : RETURN TEMPERATURE FAN COIL (CAREL) 201.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6401DC2 | HVAC18 | HVAC |  | 7 |  |  | 3198 | NA | 14345 | NA | 16416 | 4112 | 0 | EL6021_M181 |  | INT
SPASMA0909 | SPARE SER 0909 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3199 | NA | 14346 | NA | 16416 | 4114 | 0 | EL6021_M181 |  | INT
SPASMA0910 | SPARE SER 0910 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3200 | NA | 14347 | NA | 16416 | 4116 | 0 | EL6021_M181 |  | INT
SPASMA0911 | SPARE SER 0911 | MA | N | RES | [28 empty] | POL | [5 empty] | 7 |  |  | 3201 | NA | 14348 | NA | 16416 | 4118 | 0 | EL6021_M181 |  | INT
GER6401T2 | VEGA GANTRY PLC : OPENING POURCENTAGE COLD WATER VALVE FAN CTA P02 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC13 | HVAC |  | 7 |  |  | 3202 | NA | 14349 | NA | 16416 | 4120 | 0 | EL6021_M181 |  | INT
CER6401T2 | VEGA GANTRY PLC : OPENING POURCENTAGE HOT WATER VALVE FAN CTA P02 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC13 | HVAC |  | 7 |  |  | 3203 | NA | 14350 | NA | 16416 | 4122 | 0 | EL6021_M181 |  | INT
GER6202T | VEGA GANTRY PLC : OPENING POURCENTAGE COLD WATER VALVE FAN CTA P04 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3204 | NA | 14351 | NA | 16416 | 4124 | 0 | EL6021_M181 |  | INT
CER6202T | VEGA GANTRY PLC : OPENING POURCENTAGE HOT WATER VALVE FAN CTA P04 | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3205 | NA | 14352 | NA | 16416 | 4126 | 0 | EL6021_M181 |  | INT
VER6202R | VEGA GANTRY PLC : OPENING POURCENTAGE RETURN AIR MOTORISED DAMPER 201.4 (CTA 4) | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3206 | NA | 14353 | NA | 16416 | 4128 | 0 | EL6021_M181 |  | INT
VER6202N | VEGA GANTRY PLC : OPENING POURCENTAGE FRESH AIR MOTORISED DAMPER 201.1 (CTA 4) | MA |  | RES | 1 | C |  |  | % | 1 | 0 | 100 | [20 empty] | POL | 6000 |  | HVAC14 | HVAC |  | 7 |  |  | 3207 | NA | 14354 | NA | 16416 | 4130 | 0 | EL6021_M181 |  | INT
QKF6201 | état connexion accéléromètre MG niv. 21200, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 10 | [8 empty] | U4
QKG6201 | état accéléromètre MG niv. 21200, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 10 | [8 empty] | U4
QKJ6201 | état opérationnel accéléromètre MG niv. 21200, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 10 | [8 empty] | U4
QAX6201 | accélération X MG niveau 21200, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 11 | [8 empty] | I16
QAY6201 | accélération Y MG niveau 21200, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 12 | [8 empty] | I16
QAZ6201 | accélération Z MG niveau 21200, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 13 | [8 empty] | I16
QIM6201 | Inclinomètre MG niveau 21200, faisceau 1 est, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 14 | [8 empty] | I16
QKF6202 | état connexion accéléromètre MG niv. 21200, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 15 | [8 empty] | U4
QKG6202 | état accéléromètre MG niv. 21200, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 15 | [8 empty] | U4
QKJ6202 | état opérationnel accéléromètre MG niv. 21200, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 15 | [8 empty] | U4
QAX6202 | accélération X MG niveau 21200, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 16 | [8 empty] | I16
QAY6202 | accélération Y MG niveau 21200, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 17 | [8 empty] | I16
QAZ6202 | accélération Z MG niveau 21200, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 18 | [8 empty] | I16
QIM6202 | Inclinomètre MG niveau 21200, faisceau 2 ouest, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 19 | [8 empty] | I16
QKF6203 | état connexion accéléromètre MG niv. 26600, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 20 | [8 empty] | U4
QKG6203 | état accéléromètre MG niv. 26600, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 20 | [8 empty] | U4
QKJ6203 | état opérationnel accéléromètre MG niv. 26600, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 20 | [8 empty] | U4
QAX6203 | accélération X MG niveau 26600, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 21 | [8 empty] | I16
QAY6203 | accélération Y MG niveau 26600, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 22 | [8 empty] | I16
QAZ6203 | accélération Z MG niveau 26600, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 23 | [8 empty] | I16
QIM6203 | inclinomètre MG niveau 26600, faisceau 1 est, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 24 | [8 empty] | I16
QKF6204 | état connexion accéléromètre MG niv. 26600, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 25 | [8 empty] | U4
QKG6204 | état accéléromètre MG niv. 26600, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 25 | [8 empty] | U4
QKJ6204 | état opérationnel accéléromètre MG niv. 26600, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 25 | [8 empty] | U4
QAX6204 | accélération X MG niveau 26600, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 26 | [8 empty] | I16
QAY6204 | accélération Y MG niveau 26600, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 27 | [8 empty] | I16
QAZ6204 | accélération Z MG niveau 26600, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 28 | [8 empty] | I16
QIM6204 | inclinomètre MG niveau 26600, faisceau 2 ouest, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 29 | [8 empty] | I16
QKF6205 | état connexion accéléromètre MG niv. 31800, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 30 | [8 empty] | U4
QKG6205 | état accéléromètre MG niv. 31800, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 30 | [8 empty] | U4
QKJ6205 | état opérationnel accéléromètre MG niv. 31800, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 30 | [8 empty] | U4
QAX6205 | accélération X MG niveau 31800, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 31 | [8 empty] | I16
QAY6205 | accélération Y MG niveau 31800, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 32 | [8 empty] | I16
QAZ6205 | accélération Z MG niveau 31800, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 33 | [8 empty] | I16
QIM6205 | inclinomètre MG niveau 31800, faisceau 1 est, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 34 | [8 empty] | I16
QKF6206 | état connexion accéléromètre MG niv. 31800, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 35 | [8 empty] | U4
QKG6206 | état accéléromètre MG niv. 31800, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 35 | [8 empty] | U4
QKJ6206 | état opérationnel accéléromètre MG niv. 31800, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 35 | [8 empty] | U4
QAX6206 | accélération X MG niveau 31800, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 36 | [8 empty] | I16
QAY6206 | accélération Y MG niveau 31800, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 37 | [8 empty] | I16
QAZ6206 | accélération Z MG niveau 31800, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 38 | [8 empty] | I16
QIM6206 | Inclinomètre MG niveau 31800, faisceau 2 ouest, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 39 | [8 empty] | I16
QKF6207 | état connexion accéléromètre MG niv. 39600, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 40 | [8 empty] | U4
QKG6207 | état accéléromètre MG niv. 39600, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 40 | [8 empty] | U4
QKJ6207 | état opérationnel accéléromètre MG niv. 39600, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 40 | [8 empty] | U4
QAX6207 | accélération X MG niveau 39600, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 41 | [8 empty] | I16
QAY6207 | accélération Y MG niveau 39600, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 42 | [8 empty] | I16
QAZ6207 | accélération Z MG niveau 39600, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 43 | [8 empty] | I16
QIM6207 | inclinomètre MG niveau 39600, faisceau 1 est, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 44 | [8 empty] | I16
QKF6208 | état connexion accéléromètre MG niv. 39600, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 45 | [8 empty] | U4
QKG6208 | état accéléromètre MG niv. 39600, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 45 | [8 empty] | U4
QKJ6208 | état opérationnel accéléromètre MG niv. 39600, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 45 | [8 empty] | U4
QAX6208 | accélération X MG niveau 39600, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 46 | [8 empty] | I16
QAY6208 | accélération Y MG niveau 39600, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 47 | [8 empty] | I16
QAZ6208 | accélération Z MG niveau 39600, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 48 | [8 empty] | I16
QIM6208 | inclinomètre MG niveau 39600, faisceau 2 ouest, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 49 | [8 empty] | I16
QKF6209 | état connexion accéléromètre MG niv. 47400, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 50 | [8 empty] | U4
QKG6209 | état accéléromètre MG niv. 47400, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 50 | [8 empty] | U4
QKJ6209 | état opérationnel accéléromètre MG niv. 47400, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 50 | [8 empty] | U4
QAX6209 | accélération X MG niveau 47400, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 51 | [8 empty] | I16
QAY6209 | accélération Y MG niveau 47400, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 52 | [8 empty] | I16
QAZ6209 | accélération Z MG niveau 47400, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 53 | [8 empty] | I16
QIM6209 | inclinomètre MG niveau 47400, faisceau 1 est, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 54 | [8 empty] | I16
QKF6210 | état connexion accéléromètre MG niv. 47400, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 55 | [8 empty] | U4
QKG6210 | état accéléromètre MG niv. 47400, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 55 | [8 empty] | U4
QKJ6210 | état opérationnel accéléromètre MG niv. 47400, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 55 | [8 empty] | U4
QAX6210 | accélération X MG niveau 47400, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 56 | [8 empty] | I16
QAY6210 | accélération Y MG niveau 47400, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 57 | [8 empty] | I16
QAZ6210 | accélération Z MG niveau 47400, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 58 | [8 empty] | I16
QIM6210 | inclinomètre MG niveau 47400, faisceau 2 ouest, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 59 | [8 empty] | I16
QKF6211 | état connexion accéléromètre MG niv. 54000, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 60 | [8 empty] | U4
QKG6211 | état accéléromètre MG niv. 54000, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 60 | [8 empty] | U4
QKJ6211 | état opérationnel accéléromètre MG niv. 54000, faisceau 1 est | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 60 | [8 empty] | U4
QAX6211 | accélération X MG niveau 54000, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 61 | [8 empty] | I16
QAY6211 | accélération Y MG niveau 54000, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 62 | [8 empty] | I16
QAZ6211 | accélération Z MG niveau 54000, faisceau 1 est, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 63 | [8 empty] | I16
QIM6211 | inclinomètre MG niveau 54000, faisceau 1 est, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 64 | [8 empty] | I16
QKF6212 | état connexion accéléromètre MG niv. 54000, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 65 | [8 empty] | U4
QKG6212 | état accéléromètre MG niv. 54000, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 65 | [8 empty] | U4
QKJ6212 | état opérationnel accéléromètre MG niv. 54000, faisceau 2 ouest | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 65 | [8 empty] | U4
QAX6212 | accélération X MG niveau 54000, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 66 | [8 empty] | I16
QAY6212 | accélération Y MG niveau 54000, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 67 | [8 empty] | I16
QAZ6212 | accélération Z MG niveau 54000, faisceau 2 ouest, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 68 | [8 empty] | I16
QIM6212 | inclinomètre MG niveau 54000, faisceau 2 ouest, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 69 | [8 empty] | I16
QKF6713 | état connexion accéléromètre MAST niv. 21200, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 70 | [8 empty] | U4
QKG6713 | état accéléromètre MAST niv. 21200, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 70 | [8 empty] | U4
QKJ6713 | état opérationnel accéléromètre MAST niv. 21200, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 70 | [8 empty] | U4
QAX6713 | accélération X MAST niveau 21200, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 71 | [8 empty] | I16
QAY6713 | accélération Y MAST niveau 21200, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 72 | [8 empty] | I16
QAZ6713 | accélération Z MAST niveau 21200, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 73 | [8 empty] | I16
QIM6713 | inclinomètre MAST niveau 21200, façade nord, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 74 | [8 empty] | I16
QKF6714 | état connexion accéléromètre MAST niv. 29200, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 75 | [8 empty] | U4
QKG6714 | état accéléromètre MAST niv. 29200, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 75 | [8 empty] | U4
QKJ6714 | état opérationnel accéléromètre MAST niv. 29200, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 75 | [8 empty] | U4
QAX6714 | accélération X MAST niveau 29200, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 76 | [8 empty] | I16
QAY6714 | accélération Y MAST niveau 29200, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 77 | [8 empty] | I16
QAZ6714 | accélération Z MAST niveau 29200, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 78 | [8 empty] | I16
QIM6714 | inclinomètre MAST niveau 29200, façade nord, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 79 | [8 empty] | I16
QKF6715 | état connexion accéléromètre MAST niv. 37000, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 80 | [8 empty] | U4
QKG6715 | état accéléromètre MAST niv. 37000, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 80 | [8 empty] | U4
QKJ6715 | état opérationnel accéléromètre MAST niv. 37000, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 80 | [8 empty] | U4
QAX6715 | accélération X MAST niveau 37000, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 81 | [8 empty] | I16
QAY6715 | accélération Y MAST niveau 37000, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 82 | [8 empty] | I16
QAZ6715 | accélération Z MAST niveau 37000, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 83 | [8 empty] | I16
QIM6715 | inclinomètre MAST niveau 37000, façade nord, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 84 | [8 empty] | I16
QKF6716 | état connexion accéléromètre MAST niv. 44800, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 85 | [8 empty] | U4
QKG6716 | état accéléromètre MAST niv. 44800, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 85 | [8 empty] | U4
QKJ6716 | état opérationnel accéléromètre MAST niv. 44800, façade nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 85 | [8 empty] | U4
QAX6716 | accélération X MAST niveau 44800, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 86 | [8 empty] | I16
QAY6716 | accélération Y MAST niveau 44800, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 87 | [8 empty] | I16
QAZ6716 | accélération Z MAST niveau 44800, façade nord, | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 88 | [8 empty] | I16
QIM6716 | inclinomètre MAST niveau 44800, façade nord, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 89 | [8 empty] | I16
QKF6117 | état connexion accéléromètre Massif pipes R100-1_P1 panneau O 800-3 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 90 | [8 empty] | U4
QKG6117 | état accéléromètre Massif pipes R100-1_P1 panneau O 800-3 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 90 | [8 empty] | U4
QKJ6117 | état opérationnel accéléromètre Massif pipes R100-1_P1 panneau O 800-3 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 90 | [8 empty] | U4
QAX6117 | accélération X Massif pipes R100-1_P1 panneau O 800-3 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 91 | [8 empty] | I16
QAY6117 | accélération Y Massif pipes R100-1_P1 panneau O 800-3 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 92 | [8 empty] | I16
QAZ6117 | accélération Z Massif pipes R100-1_P1 panneau O 800-3 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 93 | [8 empty] | I16
QIM6117 | inclinomètre BUNKER des pipes R100-1_P1, panneau O 800-3, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 94 | [8 empty] | I16
QKF6118 | état connexion accéléromètre Massif pipes R100-1_P2 panneau HA 600-1 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 95 | [8 empty] | U4
QKG6118 | état accéléromètre Massif pipes R100-1_P2 panneau HA 600-1 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 95 | [8 empty] | U4
QKJ6118 | état opérationnel accéléromètre Massif pipes R100-1_P2 panneau HA 600-1 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 95 | [8 empty] | U4
QAX6118 | accélération X Massif pipes R100-1_P2 panneau HA 600-1 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 96 | [8 empty] | I16
QAY6118 | accélération Y Massif pipes R100-1_P2 panneau HA 600-1 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 97 | [8 empty] | I16
QAZ6118 | accélération Z Massif pipes R100-1_P2 panneau HA 600-1 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 98 | [8 empty] | I16
QIM6118 | inclinomètre BUNKER des pipes R100-1_P2, panneau HA 600-1, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 99 | [8 empty] | I16
QKF6119 | état connexion accéléromètre Massif pipes R100-1_P3 panneau R 700-3 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 100 | [8 empty] | U4
QKG6119 | état accéléromètre Massif pipes R100-1_P3 panneau R 700-3 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 100 | [8 empty] | U4
QKJ6119 | état opérationnel accéléromètre Massif pipes R100-1_P3 panneau R 700-3 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 100 | [8 empty] | U4
QAX6119 | accélération X Massif pipes R100-1_P3 panneau R 700-3 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 101 | [8 empty] | I16
QAY6119 | accélération Y Massif pipes R100-1_P3 panneau R 700-3 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 102 | [8 empty] | I16
QAZ6119 | accélération Z Massif pipes R100-1_P3 panneau R 700-3 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 103 | [8 empty] | I16
QIM6119 | inclinomètre BUNKER des pipes R100-1_P3, panneau R 700-3, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 104 | [8 empty] | I16
QKF6120 | état connexion accéléromètre Massif pipes R100-1_P4 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 105 | [8 empty] | U4
QKG6120 | état accéléromètre Massif pipes R100-1_P4 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 105 | [8 empty] | U4
QKJ6120 | état opérationnel accéléromètre Massif pipes R100-1_P4 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 105 | [8 empty] | U4
QAX6120 | accélération X Massif pipes R100-1_P4 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 106 | [8 empty] | I16
QAY6120 | accélération Y Massif pipes R100-1_P4 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 107 | [8 empty] | I16
QAZ6120 | accélération Z Massif pipes R100-1_P4 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 108 | [8 empty] | I16
QIM6120 | inclinomètre BUNKER des pipes R100-1_P4, panneau R 700-4, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 109 | [8 empty] | I16
QKF6121 | état connexion accéléromètre Massif pipes R100-1_P5 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 110 | [8 empty] | U4
QKG6121 | état accéléromètre Massif pipes R100-1_P5 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 110 | [8 empty] | U4
QKJ6121 | état opérationnel accéléromètre Massif pipes R100-1_P5 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 110 | [8 empty] | U4
QAX6121 | accélération X Massif pipes R100-1_P5 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 111 | [8 empty] | I16
QAY6121 | accélération Y Massif pipes R100-1_P5 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 112 | [8 empty] | I16
QAZ6121 | accélération Z Massif pipes R100-1_P5 panneau R 700-4 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 113 | [8 empty] | I16
QIM6121 | inclinomètre BUNKER des pipes R100-1_P5, panneau R 700-4, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 114 | [8 empty] | I16
QKF6122 | état connexion accéléromètre Massif mur R100-1_WALL | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 115 | [8 empty] | U4
QKG6122 | état accéléromètre Massif mur R100-1_WALL | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 115 | [8 empty] | U4
QKJ6122 | état opérationnel accéléromètre Massif mur R100-1_WALL | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 115 | [8 empty] | U4
QAX6122 | accélération X Massif mur R100-1_WALL | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 116 | [8 empty] | I16
QAY6122 | accélération Y Massif mur R100-1_WALL | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 117 | [8 empty] | I16
QAZ6122 | accélération Z Massif mur R100-1_WALL | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 118 | [8 empty] | I16
QIM6122 | inclinomètre BUNKER mur, R100-1_WALL, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 119 | [8 empty] | I16
QKF6123 | état connexion accéléromètre Massif R100-1_PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 120 | [8 empty] | U4
QKG6123 | état accéléromètre Massif R100-1_PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 120 | [8 empty] | U4
QKJ6123 | état opérationnel accéléromètre Massif R100-1_PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 120 | [8 empty] | U4
QAX6123 | accélération X Massif R100-1_PILLAR | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 121 | [8 empty] | I16
QAY6123 | accélération Y Massif R100-1_PILLAR | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 122 | [8 empty] | I16
QAZ6123 | accélération Z Massif R100-1_PILLAR | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 123 | [8 empty] | I16
QIM6123 | inclinomètre BUNKER R100-1_PILLAR, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 124 | [8 empty] | I16
QKF6124 | état connexion accéléromètre Massif rack 1 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 125 | [8 empty] | U4
QKG6124 | état accéléromètre Massif rack 1 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 125 | [8 empty] | U4
QKJ6124 | état opérationnel accéléromètre Massif rack 1 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 125 | [8 empty] | U4
QAX6124 | accélération X Massif rack 1 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 126 | [8 empty] | I16
QAY6124 | accélération Y Massif rack 1 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 127 | [8 empty] | I16
QAZ6124 | accélération Z Massif rack 1 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 128 | [8 empty] | I16
QIM6124 | inclinomètre BUNKER armoire électrique R103, rack1, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 129 | [8 empty] | I16
QKF6125 | état connexion accéléromètre Massif rack 2 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 130 | [8 empty] | U4
QKG6125 | état accéléromètre Massif rack 2 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 130 | [8 empty] | U4
QKJ6125 | état opérationnel accéléromètre Massif rack 2 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 130 | [8 empty] | U4
QAX6125 | accélération X Massif rack 2 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 131 | [8 empty] | I16
QAY6125 | accélération Y Massif rack 2 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 132 | [8 empty] | I16
QAZ6125 | accélération Z Massif rack 2 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 133 | [8 empty] | I16
QIM6125 | inclinomètre BUNKER armoire électrique R103, rack2, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 134 | [8 empty] | I16
QKF6126 | état connexion accéléromètre Massif rack 3 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 135 | [8 empty] | U4
QKG6126 | état accéléromètre Massif rack 3 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 135 | [8 empty] | U4
QKJ6126 | état opérationnel accéléromètre Massif rack 3 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 135 | [8 empty] | U4
QAX6126 | accélération X Massif rack 3 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 136 | [8 empty] | I16
QAY6126 | accélération Y Massif rack 3 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 137 | [8 empty] | I16
QAZ6126 | accélération Z Massif rack 3 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 138 | [8 empty] | I16
QIM6126 | inclinomètre BUNKER armoire électrique R103, rack3, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 139 | [8 empty] | I16
QKF6127 | état connexion accéléromètre Massif rack 4 R103 nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 140 | [8 empty] | U4
QKG6127 | état accéléromètre Massif rack 4 R103 nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 140 | [8 empty] | U4
QKJ6127 | état opérationnel accéléromètre Massif rack 4 R103 nord | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 140 | [8 empty] | U4
QAX6127 | accélération X Massif rack 4 R103 nord | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 141 | [8 empty] | I16
QAY6127 | accélération Y Massif rack 4 R103 nord | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 142 | [8 empty] | I16
QAZ6127 | accélération Z Massif rack 4 R103 nord | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 143 | [8 empty] | I16
QIM6127 | inclinomètre BUNKER armoire électrique R103, rack 4 nord, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 144 | [8 empty] | I16
QKF6128 | état connexion accéléromètre Massif rack 4 R103 sud | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 145 | [8 empty] | U4
QKG6128 | état accéléromètre Massif rack 4 R103 sud | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 145 | [8 empty] | U4
QKJ6128 | état opérationnel accéléromètre Massif rack 4 R103 sud | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 145 | [8 empty] | U4
QAX6128 | accélération X Massif rack 4 R103 sud | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 146 | [8 empty] | I16
QAY6128 | accélération Y Massif rack 4 R103 sud | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 147 | [8 empty] | I16
QAZ6128 | accélération Z Massif rack 4 R103 sud | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 148 | [8 empty] | I16
QIM6128 | inclinomètre BUNKER armoire électrique R103, rack 4 au sud, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 149 | [8 empty] | I16
QKF6129 | état connexion accéléromètre Massif mur 1 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 150 | [8 empty] | U4
QKG6129 | état accéléromètre Massif mur 1 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 150 | [8 empty] | U4
QKJ6129 | état opérationnel accéléromètre Massif mur 1 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 150 | [8 empty] | U4
QAX6129 | accélération X Massif mur 1 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 151 | [8 empty] | I16
QAY6129 | accélération Y Massif mur 1 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 152 | [8 empty] | I16
QAZ6129 | accélération Z Massif mur 1 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 153 | [8 empty] | I16
QIM6129 | inclinomètre BUNKER mur 1, R103, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 154 | [8 empty] | I16
QKF6130 | état connexion accéléromètre Massif mur 2 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 155 | [8 empty] | U4
QKG6130 | état accéléromètre Massif mur 2 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 155 | [8 empty] | U4
QKJ6130 | état opérationnel accéléromètre Massif mur 2 R103 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 155 | [8 empty] | U4
QAX6130 | accélération X Massif mur 2 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 156 | [8 empty] | I16
QAY6130 | accélération Y Massif mur 2 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 157 | [8 empty] | I16
QAZ6130 | accélération Z Massif mur 2 R103 | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 158 | [8 empty] | I16
QIM6130 | inclinomètre BUNKER mur 2, R103, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM62BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 159 | [8 empty] | I16
QKF6231 | état connexion accéléromètre MG CRANE TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 160 | [8 empty] | U4
QKG6231 | état accéléromètre MG CRANE TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 160 | [8 empty] | U4
QKJ6231 | état opérationnel accéléromètre MG CRANE TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 160 | [8 empty] | U4
QAX6231 | accélération X MG CRANE TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 161 | [8 empty] | I16
QAY6231 | accélération Y MG CRANE TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 162 | [8 empty] | I16
QAZ6231 | accélération Z MG CRANE TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 163 | [8 empty] | I16
QIM6231 | inclinomètre MG CRANE TCMS faisceau SE, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 164 | [8 empty] | I16
QKF6232 | état connexion accéléromètre MG CRANE TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 165 | [8 empty] | U4
QKG6232 | état accéléromètre MG CRANE TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 165 | [8 empty] | U4
QKJ6232 | état opérationnel accéléromètre MG CRANE TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 165 | [8 empty] | U4
QAX6232 | accélération X MG CRANE TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 166 | [8 empty] | I16
QAY6232 | accélération Y MG CRANE TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 167 | [8 empty] | I16
QAZ6232 | accélération Z MG CRANE TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 168 | [8 empty] | I16
QIM6232 | inclinomètre MG CRANE TCMS faisceau SW, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 169 | [8 empty] | I16
QKF6233 | état connexion accéléromètre MG CRANE TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 170 | [8 empty] | U4
QKG6233 | état accéléromètre MG CRANE TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 170 | [8 empty] | U4
QKJ6233 | état opérationnel accéléromètre MG CRANE TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 170 | [8 empty] | U4
QAX6233 | accélération X MG CRANE TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 171 | [8 empty] | I16
QAY6233 | accélération Y MG CRANE TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 172 | [8 empty] | I16
QAZ6233 | accélération Z MG CRANE TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 173 | [8 empty] | I16
QIM6233 | inclinomètre MG CRANE TCMS faisceau NE, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 174 | [8 empty] | I16
QKF6234 | état connexion accéléromètre MG CRANE TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 175 | [8 empty] | U4
QKG6234 | état accéléromètre MG CRANE TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 175 | [8 empty] | U4
QKJ6234 | état opérationnel accéléromètre MG CRANE TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 175 | [8 empty] | U4
QAX6234 | accélération X MG CRANE TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 176 | [8 empty] | I16
QAY6234 | accélération Y MG CRANE TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 177 | [8 empty] | I16
QAZ6234 | accélération Z MG CRANE TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | g | 1000 | -1.5 | 1.5 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 178 | [8 empty] | I16
QIM6234 | inclinomètre MG CRANE TCMS faisceau NW, inclinaison X Y | MA | N | TIP | 1 | H |  |  | deg | 0.01 | -15 | 15 | [20 empty] | SHM |  |  | SHM61TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 179 | [8 empty] | I16
QKF6235 | état connexion accéléromètre MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 180 | [8 empty] | U4
QKG6235 | état accéléromètre MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 180 | [8 empty] | U4
QKJ6235 | état opérationnel accéléromètre MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 180 | [8 empty] | U4
QAL6235 | accélération AXIAL MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 181 | [8 empty] | I16
QKF6236 | état connexion accéléromètre MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 185 | [8 empty] | U4
QKG6236 | état accéléromètre MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 185 | [8 empty] | U4
QKJ6236 | état opérationnel accéléromètre MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 185 | [8 empty] | U4
QAK6236 | accélération RADIAL MG TMS roue motrice NE | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 186 | [8 empty] | I16
QKF6237 | état connexion accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 190 | [8 empty] | U4
QKG6237 | état accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 190 | [8 empty] | U4
QKJ6237 | état opérationnel accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 190 | [8 empty] | U4
QAL6237 | accélération AXIAL MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 191 | [8 empty] | I16
QKF6238 | état connexion accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 195 | [8 empty] | U4
QKG6238 | état accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 195 | [8 empty] | U4
QKJ6238 | état opérationnel accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 195 | [8 empty] | U4
QAK6238 | accélération RADIAL MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 196 | [8 empty] | I16
QKF6239 | état connexion accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 200 | [8 empty] | U4
QKG6239 | état accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 200 | [8 empty] | U4
QKJ6239 | état opérationnel accéléromètre MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 200 | [8 empty] | U4
QAL6239 | accélération AXIAL MG TMS roue motrice NW | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 201 | [8 empty] | I16
QKF6240 | état connexion accéléromètre MG TMS roue motrice SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 205 | [8 empty] | U4
QKG6240 | état accéléromètre MG TMS roue motrice SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 205 | [8 empty] | U4
QKJ6240 | état opérationnel accéléromètre MG TMS roue motrice SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 205 | [8 empty] | U4
QAK6240 | accélération RADIAL MG TMS roue motrice SE | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 206 | [8 empty] | I16
QKF6241 | état connexion accéléromètre MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 210 | [8 empty] | U4
QKG6241 | état accéléromètre MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 210 | [8 empty] | U4
QKJ6241 | état opérationnel accéléromètre MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 210 | [8 empty] | U4
QAL6241 | accélération AXIAL MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 211 | [8 empty] | I16
QKF6242 | état connexion accéléromètre MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 215 | [8 empty] | U4
QKG6242 | état accéléromètre MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 215 | [8 empty] | U4
QKJ6242 | état opérationnel accéléromètre MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 215 | [8 empty] | U4
QAK6242 | accélération RADIAL MG TMS roue motrice SW | MA | N | TIP | 1 | H |  |  | NA | 10 | [22 empty] | SHM |  |  | SHM61TMS | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 216 | [8 empty] | I16
QKF6243 | état connexion transd. de pression MG niv. 26600 Clad NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 220 | [8 empty] | U4
QKG6243 | état transd. de pression MG niv. 26600 Clad NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 220 | [8 empty] | U4
QKJ6243 | état operationnel transd. de pression MG niv. 26600 Clad NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 220 | [8 empty] | U4
QPM6243 | pression MG niv. 26600 Clad NE | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 221 | [8 empty] | I16
QKF6244 | état connexion transd. de pression MG niv. 26600 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 225 | [8 empty] | U4
QKG6244 | état transd. de pression MG niv. 26600 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 225 | [8 empty] | U4
QKJ6244 | état operationnel transd. de pression MG niv. 26600 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 225 | [8 empty] | U4
QPM6244 | pression MG niv. 26600 Clad NW | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 226 | [8 empty] | I16
QKF6245 | état connexion transd. de pression MG niv. 39600 Clad NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 230 | [8 empty] | U4
QKG6245 | état transd. de pression MG niv. 39600 Clad NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 230 | [8 empty] | U4
QKJ6245 | état operationnel transd. de pression MG niv. 39600 Clad NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 230 | [8 empty] | U4
QPM6245 | pression MG niv. 39600 Clad NE | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 231 | [8 empty] | I16
QKF6246 | état connexion transd. de pression MG niv. 39600 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 235 | [8 empty] | U4
QKG6246 | état transd. de pression MG niv. 39600 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 235 | [8 empty] | U4
QKJ6246 | état operationnel transd. de pression MG niv. 39600 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 235 | [8 empty] | U4
QPM6246 | pression MG niv. 39600 Clad NW | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM64MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 236 | [8 empty] | I16
QKF6247 | état connexion transd. de pression MG niv. 54000 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 240 | [8 empty] | U4
QKG6247 | état transd. de pression MG niv. 54000 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 240 | [8 empty] | U4
QKJ6247 | état operationnel transd. de pression MG niv. 54000 Clad NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 240 | [8 empty] | U4
QPM6247 | pression MG niv. 54000 Clad NW | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 241 | [8 empty] | I16
QKF6248 | état connexion transd. de pression MG cossway direction NS | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 245 | [8 empty] | U4
QKG6248 | état transd. de pression MG cossway direction NS | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 245 | [8 empty] | U4
QKJ6248 | état operationnel transd. de pression MG cossway direction NS | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 245 | [8 empty] | U4
QPM6248 | pression MG cossway direction NS | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 246 | [8 empty] | I16
QKF6249 | état connexion transd. de pression MG cossway direction EW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 250 | [8 empty] | U4
QKG6249 | état transd. de pression MG cossway direction EW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 250 | [8 empty] | U4
QKJ6249 | état operationnel transd. de pression MG cossway direction EW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 250 | [8 empty] | U4
QPM6249 | pression MG cossway direction EW | MA | N | TIP | 1 | H |  |  | kPa | 1000 | 0 | 100 | [20 empty] | SHM |  |  | SHM68MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 251 | [8 empty] | I16
QKF6250 | état connexion capteur de Température MAST niv. 21200 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 255 | [8 empty] | U4
QKG6250 | état capteur de Température MAST niv. 21200 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 255 | [8 empty] | U4
QKJ6250 | état capteur de Température MAST niv. 21200 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 255 | [8 empty] | U4
QTM6250 | Température MAST niv. 21200 façade N | MA | N | TIP | 1 | H |  |  | °C | 1 | -40 | 350 | [13 empty] | 1 | 0 | [5 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 256 | [8 empty] | I16
QKF6251 | état connexion capteur de Température MAST niv. 29200 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 260 | [8 empty] | U4
QKG6251 | état capteur de Température MAST niv. 29200 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 260 | [8 empty] | U4
QKJ6251 | état operationnel capteur de Température MAST niv. 29200 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 260 | [8 empty] | U4
QTM6251 | Température MAST niv. 29200 façade N | MA | N | TIP | 1 | H |  |  | °C | 1 | -40 | 350 | [13 empty] | 1 | 0 | [5 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 261 | [8 empty] | I16
QKF6252 | état connexion capteur de Température MAST niv. 37000 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 265 | [8 empty] | U4
QKG6252 | état capteur de Température MAST niv. 37000 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 265 | [8 empty] | U4
QKJ6252 | état operationnel capteur de Température MAST niv. 37000 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 265 | [8 empty] | U4
QTM6252 | Température MAST niv. 37000 façade N | MA | N | TIP | 1 | H |  |  | °C | 1 | -40 | 350 | [13 empty] | 1 | 0 | [5 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 266 | [8 empty] | I16
QKF6253 | état connexion capteur de Température MAST niv. 44800 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 270 | [8 empty] | U4
QKG6253 | état capteur de Température MAST niv. 44800 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 270 | [8 empty] | U4
QKJ6253 | état operationnel capteur de Température MAST niv. 44800 façade N | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 270 | [8 empty] | U4
QTM6253 | Température MAST niv. 44800 façade N | MA | N | TIP | 1 | H |  |  | °C | 1 | -40 | 350 | [13 empty] | 1 | 0 | [5 empty] | SHM |  |  | SHM62MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 271 | [8 empty] | I16
QKF6254 | état connexion capteur de Deformation MG niv. 18400 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 275 | [8 empty] | U4
QKG6254 | état capteur de Deformation MG niv. 18400 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 275 | [8 empty] | U4
QKJ6254 | état operationnel capteur de Deformation MG niv. 18400 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 275 | [8 empty] | U4
QEM6254 | Déformation optique max MG niv. 18400 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 276 | [8 empty] | I16
QEN6254 | Déformation optique min MG niv. 18400 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 277 | [8 empty] | I16
QKF6255 | état connexion capteur de Deformation MG niv. 18400 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 280 | [8 empty] | U4
QKG6255 | état capteur de Deformation MG niv. 18400 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 280 | [8 empty] | U4
QKJ6255 | état operationnel capteur de Deformation MG niv. 18400 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 280 | [8 empty] | U4
QEM6255 | Déformation optique max MG niv. 18400 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 281 | [8 empty] | I16
QEN6255 | Déformation optique min MG niv. 18400 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 282 | [8 empty] | I16
QKF6256 | état connexion capteur de Deformation MG niv. 24000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 285 | [8 empty] | U4
QKG6256 | état capteur de Deformation MG niv. 24000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 285 | [8 empty] | U4
QKJ6256 | état operationnel capteur de Deformation MG niv. 24000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 285 | [8 empty] | U4
QEM6256 | Déformation optique max MG niv. 24000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 286 | [8 empty] | I16
QEN6256 | Déformation optique min MG niv. 24000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 287 | [8 empty] | I16
QKF6257 | état connexion capteur de Deformation MG niv. 24000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 290 | [8 empty] | U4
QKG6257 | état capteur de Deformation MG niv. 24000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 290 | [8 empty] | U4
QKJ6257 | état operationnel capteur de Deformation MG niv. 24000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 290 | [8 empty] | U4
QEM6257 | Déformation optique max MG niv. 24000 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 291 | [8 empty] | I16
QEN6257 | Déformation optique min MG niv. 24000 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 292 | [8 empty] | I16
QKF6258 | état connexion capteur de Deformation MG niv. 29200 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 295 | [8 empty] | U4
QKG6258 | état capteur de Deformation MG niv. 29200 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 295 | [8 empty] | U4
QKJ6258 | état operationnel capteur de Deformation MG niv. 29200 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 295 | [8 empty] | U4
QEM6258 | Déformation optique max MG niv. 29200 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 296 | [8 empty] | I16
QEN6258 | Déformation optique min MG niv. 29200 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 297 | [8 empty] | I16
QKF6259 | état connexion capteur de Deformation MG niv. 29200 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 300 | [8 empty] | U4
QKG6259 | état capteur de Deformation MG niv. 29200 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 300 | [8 empty] | U4
QKJ6259 | état operationnel capteur de Deformation MG niv. 29200 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 300 | [8 empty] | U4
QEM6259 | Déformation optique max MG niv. 29200 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 301 | [8 empty] | I16
QEN6259 | Déformation optique min MG niv. 29200 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 302 | [8 empty] | I16
QKF6260 | état connexion capteur de Deformation MG niv. 37000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 305 | [8 empty] | U4
QKG6260 | état capteur de Deformation MG niv. 37000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 305 | [8 empty] | U4
QKJ6260 | état operationnel capteur de Deformation MG niv. 37000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 305 | [8 empty] | U4
QEM6260 | Déformation optique max MG niv. 37000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 306 | [8 empty] | I16
QEN6260 | Déformation optique min MG niv. 37000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 307 | [8 empty] | I16
QKF6261 | état connexion capteur de Deformation MG niv. 37000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 310 | [8 empty] | U4
QKG6261 | état capteur de Deformation MG niv. 37000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 310 | [8 empty] | U4
QKJ6261 | état operationnel capteur de Deformation MG niv. 37000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 310 | [8 empty] | U4
QEM6261 | Déformation optique max MG niv. 37000 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 311 | [8 empty] | I16
QEN6261 | Déformation optique min MG niv. 37000 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM63MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 312 | [8 empty] | I16
QKF6262 | état connexion capteur de Deformation MG niv. 42200 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 315 | [8 empty] | U4
QKG6262 | état capteur de Deformation MG niv. 42200 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 315 | [8 empty] | U4
QKJ6262 | état operationnel capteur de Deformation MG niv. 42200 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 315 | [8 empty] | U4
QEM6262 | Déformation optique max MG niv. 42200 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 316 | [8 empty] | I16
QEN6262 | Déformation optique min MG niv. 42200 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 317 | [8 empty] | I16
QKF6263 | état connexion capteur de Deformation MG niv. 42200 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 320 | [8 empty] | U4
QKG6263 | état capteur de Deformation MG niv. 42200 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 320 | [8 empty] | U4
QKJ6263 | état operationnel capteur de Deformation MG niv. 42200 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 320 | [8 empty] | U4
QEM6263 | Déformation optique max MG niv. 42200 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 321 | [8 empty] | I16
QEN6263 | Déformation optique min MG niv. 42200 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 322 | [8 empty] | I16
QKF6264 | état connexion capteur de Deformation MG niv. 47400 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 325 | [8 empty] | U4
QKG6264 | état capteur de Deformation MG niv. 47400 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 325 | [8 empty] | U4
QKJ6264 | état operationnel capteur de Deformation MG niv. 47400 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 325 | [8 empty] | U4
QEM6264 | Déformation optique max MG niv. 47400 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 326 | [8 empty] | I16
QEN6264 | Déformation optique min MG niv. 47400 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 327 | [8 empty] | I16
QKF6265 | état connexion capteur de Deformation MG niv. 47400 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 330 | [8 empty] | U4
QKG6265 | état capteur de Deformation MG niv. 47400 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 330 | [8 empty] | U4
QKJ6265 | état operationnel capteur de Deformation MG niv. 47400 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 330 | [8 empty] | U4
QEM6265 | Déformation optique max MG niv. 47400 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 331 | [8 empty] | I16
QEN6265 | Déformation optique min MG niv. 47400 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 332 | [8 empty] | I16
QKF6266 | état connexion capteur de Deformation MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 335 | [8 empty] | U4
QKG6266 | état capteur de Deformation MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 335 | [8 empty] | U4
QKJ6266 | état operationnel capteur de Deformation MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 335 | [8 empty] | U4
QEM6266 | Déformation optique max MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 336 | [8 empty] | I16
QEN6266 | Déformation optique min MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 337 | [8 empty] | I16
QKF6267 | état connexion capteur de Deformation MG niv. 47400 SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 340 | [8 empty] | U4
QKG6267 | état capteur de Deformation MG niv. 47400 SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 340 | [8 empty] | U4
QKJ6267 | état operationnel capteur de Deformation MG niv. 47400 SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 340 | [8 empty] | U4
QEM6267 | Déformation optique max MG niv. 47400 SW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 341 | [8 empty] | I16
QEN6267 | Déformation optique min MG niv. 47400 SW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM65MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 342 | [8 empty] | I16
QKF6268 | état connexion capteur de Deformation MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 345 | [8 empty] | U4
QKG6268 | état capteur de Deformation MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 345 | [8 empty] | U4
QKJ6268 | état operationnel capteur de Deformation MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 345 | [8 empty] | U4
QEM6268 | Déformation optique max MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 346 | [8 empty] | I16
QEN6268 | Déformation optique min MG niv. 54000 NE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 347 | [8 empty] | I16
QKF6269 | état connexion capteur de Deformation MG niv. 54000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 350 | [8 empty] | U4
QKG6269 | état capteur de Deformation MG niv. 54000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 350 | [8 empty] | U4
QKJ6269 | état operationnel capteur de Deformation MG niv. 54000 NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 350 | [8 empty] | U4
QEM6269 | Déformation optique max MG niv. 54000 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 351 | [8 empty] | I16
QEN6269 | Déformation optique min MG niv. 54000 NW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 352 | [8 empty] | I16
QKF6270 | état connexion capteur de Deformation MG niv. 54000 SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 355 | [8 empty] | U4
QKG6270 | état capteur de Deformation MG niv. 54000 SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 355 | [8 empty] | U4
QKJ6270 | état operationnel capteur de Deformation MG niv. 54000 SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 355 | [8 empty] | U4
QEM6270 | Déformation optique max MG niv. 54000 SE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 356 | [8 empty] | I16
QEN6270 | Déformation optique min MG niv. 54000 SE | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 357 | [8 empty] | I16
QKF6271 | état connexion capteur de Deformation MG niv. 54000 SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 360 | [8 empty] | U4
QKG6271 | état capteur de Deformation MG niv. 54000 SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 360 | [8 empty] | U4
QKJ6271 | état operationnel capteur de Deformation MG niv. 54000 SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 360 | [8 empty] | U4
QEM6271 | Déformation optique max MG niv. 54000 SW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 361 | [8 empty] | I16
QEN6271 | Déformation optique min MG niv. 54000 SW | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 362 | [8 empty] | I16
QKF6272 | état connexion capteur de Deformation MG niv. 18400 NE PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 365 | [8 empty] | U4
QKG6272 | état capteur de Deformation MG niv. 18400 NE PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 365 | [8 empty] | U4
QKJ6272 | état operationnel capteur de Deformation MG niv. 18400 NE PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 365 | [8 empty] | U4
QEM6272 | Déformation optique max MG niv. 18400 NE PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 366 | [8 empty] | I16
QEN6272 | Déformation optique min MG niv. 18400 NE PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 367 | [8 empty] | I16
QKF6273 | état connexion capteur de Deformation MG niv. 18400 NW PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 370 | [8 empty] | U4
QKG6273 | état capteur de Deformation MG niv. 18400 NW PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 370 | [8 empty] | U4
QKJ6273 | état operationnel capteur de Deformation MG niv. 18400 NW PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 370 | [8 empty] | U4
QEM6273 | Déformation optique max MG niv. 18400 NW PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 371 | [8 empty] | I16
QEN6273 | Déformation optique min MG niv. 18400 NW PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 372 | [8 empty] | I16
QKF6274 | état connexion capteur de Deformation MG niv. 18400 SE PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 375 | [8 empty] | U4
QKG6274 | état capteur de Deformation MG niv. 18400 SE PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 375 | [8 empty] | U4
QKJ6274 | état operationnel capteur de Deformation MG niv. 18400 SE PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 375 | [8 empty] | U4
QEM6274 | Déformation optique max MG niv. 18400 SE PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 376 | [8 empty] | I16
QEN6274 | Déformation optique min MG niv. 18400 SE PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 377 | [8 empty] | I16
QKF6275 | état connexion capteur de Deformation MG niv. 18400 SW PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 380 | [8 empty] | U4
QKG6275 | état capteur de Deformation MG niv. 18400 SW PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 380 | [8 empty] | U4
QKJ6275 | état operationnel capteur de Deformation MG niv. 18400 SW PILLAR | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 380 | [8 empty] | U4
QEM6275 | Déformation optique max MG niv. 18400 SW PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 381 | [8 empty] | I16
QEN6275 | Déformation optique min MG niv. 18400 SW PILLAR | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 382 | [8 empty] | I16
QKF6276 | état connexion capteur de Deformation MG niv. 50000 NE platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 385 | [8 empty] | U4
QKG6276 | état capteur de Deformation MG niv. 50000 NE platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 385 | [8 empty] | U4
QKJ6276 | état operationnel capteur de Deformation MG niv. 50000 NE platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 385 | [8 empty] | U4
QEM6276 | Déformation optique max MG niv. 50000 NE platform | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 386 | [8 empty] | I16
QEN6276 | Déformation optique min MG niv. 50000 NE platform | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 387 | [8 empty] | I16
QKF6277 | état connexion capteur de Deformation MG niv. 50000 NW platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 390 | [8 empty] | U4
QKG6277 | état capteur de Deformation MG niv. 50000 NW platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 390 | [8 empty] | U4
QKJ6277 | état operationnel capteur de Deformation MG niv. 50000 NW platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 390 | [8 empty] | U4
QEM6277 | Déformation optique max MG niv. 50000 NW platform (1/2) | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 391 | [8 empty] | I16
QEN6277 | Déformation optique min MG niv. 50000 NW platform (1/2) | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 392 | [8 empty] | I16
QKF6278 | état connexion capteur de Deformation MG niv. 50000 NW platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 395 | [8 empty] | U4
QKG6278 | état capteur de Deformation MG niv. 50000 NW platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 395 | [8 empty] | U4
QKJ6278 | état operationnel capteur de Deformation MG niv. 50000 NW platform | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 395 | [8 empty] | U4
QEM6278 | Déformation optique max MG niv. 50000 NW platform (2/2) | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 396 | [8 empty] | I16
QEN6278 | Déformation optique min MG niv. 50000 NW platform (2/2) | MA | N | TIP | 1 | H |  |  | µε | 1000 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM66MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 397 | [8 empty] | I16
QKF6279 | état connexion capteur de Deformation CRANE MG TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 400 | [8 empty] | U4
QKG6279 | état capteur de Deformation CRANE MG TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 400 | [8 empty] | U4
QKJ6279 | état operationnel capteur de Deformation CRANE MG TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 400 | [8 empty] | U4
QEM6279 | Déformation optique max CRANE MG TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 401 | [8 empty] | I16
QEN6279 | Déformation optique min CRANE MG TCMS faisceau NE | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 402 | [8 empty] | I16
QKF6280 | état connexion capteur de Deformation CRANE MG TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 405 | [8 empty] | U4
QKG6280 | état capteur de Deformation CRANE MG TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 405 | [8 empty] | U4
QKJ6280 | état operationnel capteur de Deformation CRANE MG TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 405 | [8 empty] | U4
QEM6280 | Déformation optique max CRANE MG TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 406 | [8 empty] | I16
QEN6280 | Déformation optique min CRANE MG TCMS faisceau NW | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 407 | [8 empty] | I16
QKF6281 | état connexion capteur de Deformation CRANE MG TCMS faisceau CE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 410 | [8 empty] | U4
QKG6281 | état capteur de Deformation CRANE MG TCMS faisceau CE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 410 | [8 empty] | U4
QKJ6281 | état operationnel capteur de Deformation CRANE MG TCMS faisceau CE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 410 | [8 empty] | U4
QEM6281 | Déformation optique max CRANE MG TCMS faisceau CE | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 411 | [8 empty] | I16
QEN6281 | Déformation optique min CRANE MG TCMS faisceau CE | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 412 | [8 empty] | I16
QKF6282 | état connexion capteur de Deformation CRANE MG TCMS faisceau CW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 415 | [8 empty] | U4
QKG6282 | état capteur de Deformation CRANE MG TCMS faisceau CW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 415 | [8 empty] | U4
QKJ6282 | état operationnel capteur de Deformation CRANE MG TCMS faisceau CW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 415 | [8 empty] | U4
QEM6282 | Déformation optique max CRANE MG TCMS faisceau CW | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 416 | [8 empty] | I16
QEN6282 | Déformation optique min CRANE MG TCMS faisceau CW | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 417 | [8 empty] | I16
QKF6283 | état connexion capteur de Deformation CRANE MG TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 420 | [8 empty] | U4
QKG6283 | état capteur de Deformation CRANE MG TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 420 | [8 empty] | U4
QKJ6283 | état operationnel capteur de Deformation CRANE MG TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 420 | [8 empty] | U4
QEM6283 | Déformation optique max CRANE MG TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 421 | [8 empty] | I16
QEN6283 | Déformation optique min CRANE MG TCMS faisceau SE | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 422 | [8 empty] | I16
QKF6284 | état connexion capteur de Deformation CRANE MG TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 425 | [8 empty] | U4
QKG6284 | état capteur de Deformation CRANE MG TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 425 | [8 empty] | U4
QKJ6284 | état operationnel capteur de Deformation CRANE MG TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 425 | [8 empty] | U4
QEM6284 | Déformation optique max CRANE MG TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 426 | [8 empty] | I16
QEN6284 | Déformation optique min CRANE MG TCMS faisceau SW | MA | N | TIP | 1 | H |  |  | µε | 10 | -1500 | 1500 | [20 empty] | SHM |  |  | SHM62TC | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 427 | [8 empty] | I16
QKF6285 | état connexion sonomètre MG COSS niv. 14400 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 430 | [8 empty] | U4
QKG6285 | état capteur sonomètre MG COSS niv. 14400 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 430 | [8 empty] | U4
QKJ6285 | état operationnel sonomètre MG COSS niv. 14400 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 430 | [8 empty] | U4
QSM6285 | Pression acoustique max sonomètre MG COSS niv. 14400 | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 160 | [20 empty] | SHM |  |  | SHM61MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 431 | [8 empty] | I16
QKF6286 | état connexion sonomètre MG ROOF niv. 54000 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 435 | [8 empty] | U4
QKG6286 | état capteur sonomètre MG ROOF niv. 54000 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 435 | [8 empty] | U4
QKJ6286 | état operationnel sonomètre MG ROOF niv. 54000 | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 435 | [8 empty] | U4
QSM6286 | Pression acoustique max sonomètre MG ROOF niv. 54000 | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 160 | [20 empty] | SHM |  |  | SHM67MG | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 436 | [8 empty] | I16
QKF6187 | état connexion sonomètre Massif R103 SHM rack | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 440 | [8 empty] | U4
QKG6187 | état capteur sonomètre Massif R103 SHM rack | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 440 | [8 empty] | U4
QKJ6187 | état operationnel sonomètre Massif R103 SHM rack | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 440 | [8 empty] | U4
QSM6187 | Pression acoustique max sonomètre Massif R103 SHM rack | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 140 | [20 empty] | SHM |  |  | SHM63BU | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 441 | [8 empty] | I16
QKF6788 | état connexion sonomètre MAST niv. 39600 1E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 445 | [8 empty] | U4
QKG6788 | état capteur sonomètre MAST niv. 39600 1E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 445 | [8 empty] | U4
QKJ6788 | état operationnel sonomètre MAST niv. 39600 1E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 445 | [8 empty] | U4
QSM6788 | Pression acoustique max sonomètre MAST niv. 39600 1E | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 184 | [20 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 446 | [8 empty] | I16
QKF6789 | état connexion sonomètre MAST niv. 39600 2E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 450 | [8 empty] | U4
QKG6789 | état capteur sonomètre MAST niv. 39600 2E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 450 | [8 empty] | U4
QKJ6789 | état operationnel sonomètre MAST niv. 39600 2E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 450 | [8 empty] | U4
QSM6789 | Pression acoustique max sonomètre MAST niv. 39600 2E | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 184 | [20 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 451 | [8 empty] | I16
QKF6790 | état connexion sonomètre MAST niv. 39600 3E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 455 | [8 empty] | U4
QKG6790 | état capteur sonomètre MAST niv. 39600 3E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 455 | [8 empty] | U4
QKJ6790 | état operationnel sonomètre MAST niv. 39600 3E | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 455 | [8 empty] | U4
QSM6790 | Pression acoustique max sonomètre MAST niv. 39600 3E | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 184 | [20 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 456 | [8 empty] | I16
QKF6791 | état connexion sonomètre MAST niv. 39600 1W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 460 | [8 empty] | U4
QKG6791 | état capteur sonomètre MAST niv. 39600 1W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 460 | [8 empty] | U4
QKJ6791 | état operationnel sonomètre MAST niv. 39600 1W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 460 | [8 empty] | U4
QSM6791 | Pression acoustique max sonomètre MAST niv. 39600 1W | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 184 | [20 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 461 | [8 empty] | I16
QKF6792 | état connexion sonomètre MAST niv. 39600 2W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 465 | [8 empty] | U4
QKG6792 | état capteur sonomètre MAST niv. 39600 2W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 465 | [8 empty] | U4
QKJ6792 | état operationnel sonomètre MAST niv. 39600 2W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 465 | [8 empty] | U4
QSM6792 | Pression acoustique max sonomètre MAST niv. 39600 2W | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 184 | [20 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 466 | [8 empty] | I16
QKF6793 | état connexion sonomètre MAST niv. 39600 3W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 470 | [8 empty] | U4
QKG6793 | état capteur sonomètre MAST niv. 39600 3W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 470 | [8 empty] | U4
QKJ6793 | état operationnel sonomètre MAST niv. 39600 3W | MA | N | TIP | 1 | H |  |  | NA | [7 empty] | 0 | [15 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 470 | [8 empty] | U4
QSM6793 | Pression acoustique max sonomètre MAST niv. 39600 3W | MA | N | TIP | 1 | H |  |  | dB | 100 | 0 | 184 | [20 empty] | SHM |  |  | SHM61MA | Structural Health Monitoring (SHM) | NEW | 8 |  |  | 471 | [8 empty] | I16
QIM6201VA | Valeur inclinaison MAX MG niveau 21200, faisceau 1 est | MA | N | CAL | 1 | H |  |  | DEG |  | 15 | -15 | [16 empty] | FORM | QIM6201 % 100 | QIM6201 |  | SNMP |  |  | SHM62MG | Structural Health Monitoring (SHM) | NEW | [12 empty] | STRING
QIM6202VA | Valeur inclinaison MAX MG niveau 21200, faisceau 2 ouest | MA | N | CAL | 1 | H |  |  | DEG |  | 15 | -15 | [16 empty] | FORM | QIM6202 % 100 | QIM6202 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6203VA | Valeur inclinaison MAX MG niveau 26600, faisceau 1 est | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6203 % 100 | QIM6203 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6204VA | Valeur inclinaison MAX MG niveau 26600, faisceau 2 ouest | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6204 % 100 | QIM6204 |  |  |  |  | SHM62MG | Structural Health Monitoring (SHM)
QIM6205VA | Valeur inclinaison MAX MG niveau 31800, faisceau 1 est | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6205 % 100 | QIM6205 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6206VA | Valeur inclinaison MAX MG niveau 31800, faisceau 2 ouest | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6206 % 100 | QIM6206 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6207VA | Valeur inclinaison MAX MG niveau 39600, faisceau 1 est | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6207 % 100 | QIM6207 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6208VA | Valeur inclinaison MAX MG niveau 39600, faisceau 2 ouest | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6208 % 100 | QIM6208 |  |  |  |  | SHM64MG | Structural Health Monitoring (SHM)
QIM6209VA | Valeur inclinaison MAX MG niveau 47400, faisceau 1 est | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6209 % 100 | QIM6209 |  |  |  |  | SHM65MG | Structural Health Monitoring (SHM)
QIM6210VA | Valeur inclinaison MAX MG niveau 47400, faisceau 2 ouest | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6210 % 100 | QIM6210 |  |  |  |  | SHM65MG | Structural Health Monitoring (SHM)
QIM6211VA | Valeur inclinaison MAX MG niveau 54000, faisceau 1 est | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6211 % 100 | QIM6211 |  |  |  |  | SHM67MG | Structural Health Monitoring (SHM)
QIM6212VA | Valeur inclinaison MAX MG niveau 54000, faisceau 2 ouest | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6212 % 100 | QIM6212 |  |  |  |  | SHM67MG | Structural Health Monitoring (SHM)
QIM6713VA | Valeur inclinaison MAX MAST niveau 21200, façade nord | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6713 % 100 | QIM6713 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6714VA | Valeur inclinaison MAX MAST niveau 29200, façade nord | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6714 % 100 | QIM6714 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6715VA | Valeur inclinaison MAX MAST niveau 37000, façade nord | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6715 % 100 | QIM6715 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6716VA | Valeur inclinaison MAX MAST niveau 44800, façade nord | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6716 % 100 | QIM6716 |  |  |  |  | SHM62MA | Structural Health Monitoring (SHM)
QIM6117VA | Valeur inclinaison MAX BUNKER des pipes R100-1_P1, panneau O 800-3 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6117 % 100 | QIM6117 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6118VA | Valeur inclinaison MAX BUNKER des pipes R100-1_P2, panneau HA 600-1 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6118 % 100 | QIM6118 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6119VA | Valeur inclinaison MAX BUNKER des pipes R100-1_P3, panneau R 700-3 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6119 % 100 | QIM6119 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6120VA | Valeur inclinaison MAX BUNKER des pipes R100-1_P4, panneau R 700-4 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6120 % 100 | QIM6120 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6121VA | Valeur inclinaison MAX BUNKER des pipes R100-1_P5, panneau R 700-4 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6121 % 100 | QIM6121 |  |  |  |  | SHM61BU | Structural Health Monitoring (SHM)
QIM6122VA | Valeur inclinaison MAX BUNKER mur, R100-1_WALL | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6122 % 100 | QIM6122 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6123VA | Valeur inclinaison MAX BUNKER R100-1_PILLAR | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6123 % 100 | QIM6123 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6124VA | Valeur inclinaison MAX BUNKER armoire électrique R103, rack1 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6124 % 100 | QIM6124 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6125VA | Valeur inclinaison MAX BUNKER armoire électrique R103, rack2 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6125 % 100 | QIM6125 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6126VA | Valeur inclinaison MAX BUNKER armoire électrique R103, rack3 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6126 % 100 | QIM6126 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6127VA | Valeur inclinaison MAX BUNKER armoire électrique R103, rack 4 nord | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6127 % 100 | QIM6127 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6128VA | Valeur inclinaison MAX BUNKER armoire électrique R103, rack 4 au sud | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6128 % 100 | QIM6128 |  |  |  |  | SHM63BU | Structural Health Monitoring (SHM)
QIM6129VA | Valeur inclinaison MAX BUNKER mur 1, R103 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6129 % 100 | QIM6129 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6130VA | Valeur inclinaison MAX BUNKER mur 2, R103 | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6130 % 100 | QIM6130 |  |  |  |  | SHM62BU | Structural Health Monitoring (SHM)
QIM6231VA | Valeur inclinaison MAX MG CRANE TCMS faisceau SE | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6231 % 100 | QIM6231 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
QIM6232VA | Valeur inclinaison MAX MG CRANE TCMS faisceau SW | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6232 % 100 | QIM6232 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
QIM6233VA | Valeur inclinaison MAX MG CRANE TCMS faisceau NE | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6233 % 100 | QIM6233 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
QIM6234VA | Valeur inclinaison MAX MG CRANE TCMS faisceau NW | MA | N | CAL | 1 | H |  |  | DEG |  | -15 | 15 | [16 empty] | FORM | QIM6234 % 100 | QIM6234 |  |  |  |  | SHM61TC | Structural Health Monitoring (SHM)
EWR6021R | TD CAT II PORTIQUE 1602-101-21 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6021V1*EIR6021I1 + EUR6021V2*EIR6021I2 + EUR6021V3*EIR6021I3)*EWR6021PF | [5 empty] | TD CAT II 1602 101 21 (E67) | Energy TD Bunker
EWR6021Q | TD CAT II PORTIQUE 1602-101-21 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6021V1*EIR6021I1 + EUR6021V2*EIR6021I2 + EUR6021V3*EIR6021I3)*sin[arcos(EWR6021PF)] | [5 empty] | TD CAT II 1602 101 21 (E67) | Energy TD Bunker
EWR6021S | TD CAT II PORTIQUE 1602-101-21 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6021V1*EIR6021I1 + EUR6021V2*EIR6021I2 + EUR6021V3*EIR6021I3) | [5 empty] | TD CAT II 1602 101 21 (E67) | Energy TD Bunker
EWR6020R | TD CAT II PORTIQUE 1602-101-20 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6020V1*EIR6020I1 + EUR6020V2*EIR6020I2 + EUR6020V3*EIR6020I3)*EWR6020PF | [5 empty] | TD CAT II 1602 101 20 (E67) | Energy TD Bunker
EWR6020Q | TD CAT II PORTIQUE 1602-101-20 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6020V1*EIR6020I1 + EUR6020V2*EIR6020I2 + EUR6020V3*EIR6020I3)*sin[arcos(EWR6020PF)] | [5 empty] | TD CAT II 1602 101 20 (E67) | Energy TD Bunker
EWR6020S | TD CAT II PORTIQUE 1602-101-20 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6020V1*EIR6020I1 + EUR6020V2*EIR6020I2 + EUR6020V3*EIR6020I3) | [5 empty] | TD CAT II 1602 101 20 (E67) | Energy TD Bunker
EWR6230R | TDGA 1602-101-30 Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6230V1*EIR6230I1 + EUR6230V2*EIR6230I2 + EUR6230V3*EIR6230I3)*EWR6230PF | [5 empty] | TDGA 1602 101 30 CAT IIIA (E67) | Energy TD Bunker
EWR6230Q | TDGA 1602-101-30 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6230V1*EIR6230I1 + EUR6230V2*EIR6230I2 + EUR6230V3*EIR6230I3)*sin[arcos(EWR6230PF)] | [5 empty] | TDGA 1602 101 30 CAT IIIA (E67) | Energy TD Bunker
EWR6230S | TDGA 1602-101-30 Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6230V1*EIR6230I1 + EUR6230V2*EIR6230I2 + EUR6230V3*EIR6230I3) | [5 empty] | TDGA 1602 101 30 CAT IIIA (E67) | Energy TD Bunker
EWR6231R | TDGA 1602-101-31 Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6231V1*EIR6231I1 + EUR6231V2*EIR6231I2 + EUR6231V3*EIR6231I3)*EWR6231PF | [5 empty] | TDGA 1602 101 31 CAT IIIB (E67) | Energy TD Bunker
EWR6231Q | TDGA 1602-101-31 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6231V1*EIR6231I1 + EUR6231V2*EIR6231I2 + EUR6231V3*EIR6231I3)*sin[arcos(EWR6231PF)] | [5 empty] | TDGA 1602 101 31 CAT IIIB (E67) | Energy TD Bunker
EWR6231S | TDGA 1602-101-31 Total Active Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6231V1*EIR6231I1 + EUR6231V2*EIR6231I2 + EUR6231V3*EIR6231I3) | [5 empty] | TDGA 1602 101 31 CAT IIIB (E67) | Energy TD Bunker
EWR6430R | TDGA 1602-201-30 Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6430V1*EIR6430I1 + EUR6430V2*EIR6430I2 + EUR6430V3*EIR6430I3)*EWR6430PF | [5 empty] | TDGA 1602 201 30 CAT IIIA (E67) | Energy TD Bunker
EWR6430Q | TDGA 1602-201-30 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6430V1*EIR6430I1 + EUR6430V2*EIR6430I2 + EUR6430V3*EIR6430I3)*sin[arcos(EWR6430PF)] | [5 empty] | TDGA 1602 201 30 CAT IIIA (E67) | Energy TD Bunker
EWR6430S | TDGA 1602-201-30 Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6430V1*EIR6430I1 + EUR6430V2*EIR6430I2 + EUR6430V3*EIR6430I3) | [5 empty] | TDGA 1602 201 30 CAT IIIA (E67) | Energy TD Bunker
EWR6431R | TDGA 1602-201-31 Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6431V1*EIR6431I1 + EUR6431V2*EIR6431I2 + EUR6431V3*EIR6431I3)*EWR6431PF | [5 empty] | TDGA 1602 201 31 CAT IIIB (E67) | Energy TD Bunker
EWR6431Q | TDGA 1602-201-31 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6431V1*EIR6431I1 + EUR6431V2*EIR6431I2 + EUR6431V3*EIR6431I3)*sin[arcos(EWR6431PF)] | [5 empty] | TDGA 1602 201 31 CAT IIIB (E67) | Energy TD Bunker
EWR6431S | TDGA 1602-201-31 Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6431V1*EIR6431I1 + EUR6431V2*EIR6431I2 + EUR6431V3*EIR6431I3) | [5 empty] | TDGA 1602 201 31 CAT IIIB (E67) | Energy TD Bunker
EWR6530R | TDGA 1602-501-30 Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6530V1*EIR6530I1 + EUR6530V2*EIR6530I2 + EUR6530V3*EIR6530I3)*EWR6530PF | [5 empty] | TDGA 1602 501 30 CAT IIIA (E67) | Energy TD Bunker
EWR6530Q | TDGA 1602-501-30 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6530V1*EIR6530I1 + EUR6530V2*EIR6530I2 + EUR6530V3*EIR6530I3)*sin[arcos(EWR6530PF)] | [5 empty] | TDGA 1602 501 30 CAT IIIA (E67) | Energy TD Bunker
EWR6530S | TDGA 1602-501-30 Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6530V1*EIR6530I1 + EUR6530V2*EIR6530I2 + EUR6530V3*EIR6530I3) | [5 empty] | TDGA 1602 501 30 CAT IIIA (E67) | Energy TD Bunker
EWR6531R | TDGA 1602-501-31 Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6531V1*EIR6531I1 + EUR6531V2*EIR6531I2 + EUR6531V3*EIR6531I3)*EWR6531PF | [5 empty] | TDGA 1602 501 31 CAT IIIB (E67) | Energy TD Bunker
EWR6531Q | TDGA 1602-501-31 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6531V1*EIR6531I1 + EUR6531V2*EIR6531I2 + EUR6531V3*EIR6531I3)*sin[arcos(EWR6531PF)] | [5 empty] | TDGA 1602 501 31 CAT IIIB (E67) | Energy TD Bunker
EWR6531S | TDGA 1602-501-31 Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6531V1*EIR6531I1 + EUR6531V2*EIR6531I2 + EUR6531V3*EIR6531I3) | [5 empty] | TDGA 1602 501 31 CAT IIIB (E67) | Energy TD Bunker
EWR6630R | TDGA 1602-502-30 Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6630V1*EIR6630I1 + EUR6630V2*EIR6630I2 + EUR6630V3*EIR6630I3)*EWR6630PF | [5 empty] | TDGA 1602 502 30 CAT IIIA (E67) | Energy TD Bunker
EWR6630Q | TDGA 1602-502-30 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6630V1*EIR6630I1 + EUR6630V2*EIR6630I2 + EUR6630V3*EIR6630I3)*sin[arcos(EWR6630PF)] | [5 empty] | TDGA 1602 502 30 CAT IIIA (E67) | Energy TD Bunker
EWR6630S | TDGA 1602-502-30 Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6630V1*EIR6630I1 + EUR6630V2*EIR6630I2 + EUR6630V3*EIR6630I3) | [5 empty] | TDGA 1602 502 30 CAT IIIA (E67) | Energy TD Bunker
EWR6631R | TDGA 1602-502-31 Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6631V1*EIR6631I1 + EUR6631V2*EIR6631I2 + EUR6631V3*EIR6631I3)*EWR6631PF | [5 empty] | TDGA 1602 502 31 CAT IIIB (E67) | Energy TD Bunker
EWR6631Q | TDGA 1602-502-31 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6631V1*EIR6631I1 + EUR6631V2*EIR6631I2 + EUR6631V3*EIR6631I3)*sin[arcos(EWR6631PF)] | [5 empty] | TDGA 1602 502 31 CAT IIIB (E67) | Energy TD Bunker
EWR6631S | TDGA 1602-502-31 Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6631V1*EIR6631I1 + EUR6631V2*EIR6631I2 + EUR6631V3*EIR6631I3) | [5 empty] | TDGA 1602 502 31 CAT IIIB (E67) | Energy TD Bunker
EWR6702AR | TD AXIMA 1602-401-002 Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6702AV1*EIR6702AI1)*EWR6702APF | [5 empty] | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energy TD Bunker
EWR6702AQ | TD AXIMA 1602-401-002 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6702AV1*EIR6702AI1 )*sin[arcos(EWR6702APF)] | [5 empty] | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energy TD Bunker
EWR6702AS | TD AXIMA 1602-401-002 Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6702AV1*EIR6702AI1 ) | [5 empty] | TD AXIMA 1602 401 002 CAT IIIA (E67) | Energy TD Bunker
EWR6702BR | TD AXIMA 1602-401-002 Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6702BV1*EIR6702BI1 )*EWR6702BPF | [5 empty] | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energy TD Bunker
EWR6702BQ | TD AXIMA 1602-401-002 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6702BV1*EIR6702BI1)*sin[arcos(EWR6702BPF)] | [5 empty] | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energy TD Bunker
EWR6702BS | TD AXIMA 1602-401-002 Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6702BV1*EIR6702BI1 ) | [5 empty] | TD AXIMA 1602 401 002 CAT IIIB (E67) | Energy TD Bunker
EWR6701R | TD AXIMA 1602-401-001 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6701V1*EIR6701I1 + EUR6701V2*EIR6701I2 + EUR6701V3*EIR6701I3)*EWR6701PF | [5 empty] | TD AXIMA 1602 401 001 CAT II (E67) | Energy TD Bunker
EWR6701Q | TD AXIMA 1602-401-001 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6701V1*EIR6701I1 + EUR6701V2*EIR6701I2 + EUR6701V3*EIR6701I3)*sin[arcos(EWR6701PF)] | [5 empty] | TD AXIMA 1602 401 001 CAT II (E67) | Energy TD Bunker
EWR6701S | TD AXIMA 1602-401-001 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6701V1*EIR6701I1 + EUR6701V2*EIR6701I2 + EUR6701V3*EIR6701I3) | [5 empty] | TD AXIMA 1602 401 001 CAT II (E67) | Energy TD Bunker
EWR6703R | TD AXIMA 1602-401-003 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6703V1*EIR6703I1 + EUR6703V2*EIR6703I2 + EUR6703V3*EIR6703I3)*EWR6703PF | [5 empty] | TD AXIMA 1602 401 003 CAT II (E67) | Energy TD Bunker
EWR6703Q | TD AXIMA 1602-401-003 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6703V1*EIR6703I1 + EUR6703V2*EIR6703I2 + EUR6703V3*EIR6703I3)*sin[arcos(EWR6703PF)] | [5 empty] | TD AXIMA 1602 401 003 CAT II (E67) | Energy TD Bunker
EWR6703S | TD AXIMA 1602-401-003 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6703V1*EIR6703I1 + EUR6703V2*EIR6703I2 + EUR6703V3*EIR6703I3) | [5 empty] | TD AXIMA 1602 401 003 CAT II (E67) | Energy TD Bunker
EWR6832R | TD3 Local 101 IIIA 1602-101-32 Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6832V1*EIR6832I1 + EUR6832V2*EIR6832I2 + EUR6832V3*EIR6832I3)*EWR6832PF | [5 empty] | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energy TD Bunker
EWR6832Q | TD3 Local 101 IIIA 1602-101-32 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6832V1*EIR6832I1 + EUR6832V2*EIR6832I2 + EUR6832V3*EIR6832I3)*sin[arcos(EWR6832PF)] | [5 empty] | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energy TD Bunker
EWR6832S | TD3 Local 101 IIIA 1602-101-32 Total Apparent Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6832V1*EIR6832I1 + EUR6832V2*EIR6832I2 + EUR6832V3*EIR6832I3) | [5 empty] | TD3 Local 101 1602 101 32 CAT IIIA (E67) | Energy TD Bunker
EWR6833R | TD3 Local 101 IIIB 1602-101-33 Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR6833V1*EIR6833I1 + EUR6833V2*EIR6833I2 + EUR6833V3*EIR6833I3)*EWR6833PF | [5 empty] | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energy TD Bunker
EWR6833Q | TD3 Local 101 IIIB 1602-101-33 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR6833V1*EIR6833I1 + EUR6833V2*EIR6833I2 + EUR6833V3*EIR6833I3)*sin[arcos(EWR6833PF)] | [5 empty] | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energy TD Bunker
EWR6833S | TD3 Local 101 IIIB 1602-101-33 Total Apparent Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR6833V1*EIR6833I1 + EUR6833V2*EIR6833I2 + EUR6833V3*EIR6833I3) | [5 empty] | TD3 Local 101 1602 101 33 CAT IIIB (E67) | Energy TD Bunker
EIR6071I3 | Onduleur IIIA-1 UL7001 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3232 | NA | 13301 | NA | 16416 | 2024 | 0 | EL6021_M178 |  | UINT
EUR6071UB | Onduleur IIIA-1 UL7001 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 500 |  |  | 0 | 500 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3239 | NA | 13308 | NA | 16416 | 2038 | 0 | EL6021_M178 |  | UINT
EFR6071 | Onduleur IIIA-1 UL7001 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 49 | 61 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6071D1 | Onduleur IIIA 1 UL7001 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3241 | NA | 13310 | NA | 16416 | 2042 | 0 | EL6021_M178 |  | UINT
EIR6072I1 | Onduleur IIIA-2 UL7002 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3250 | NA | 13319 | NA | 16416 | 2060 | 0 | EL6021_M178 |  | UINT
EIR6072I2 | Onduleur IIIA-2 UL7002 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3251 | NA | 13320 | NA | 16416 | 2062 | 0 | EL6021_M178 |  | UINT
EIR6072I3 | Onduleur IIIA-2 UL7002 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3252 | NA | 13321 | NA | 16416 | 2064 | 0 | EL6021_M178 |  | UINT
EUR6072UB | Onduleur IIIA-2 UL7002 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 500 |  |  | 0 | 500 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3259 | NA | 13328 | NA | 16416 | 2078 | 0 | EL6021_M178 |  | UINT
EFR6072 | Onduleur IIIA-2 UL7002 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 49 | 61 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6072D1 | Onduleur IIIA 2 UL7002 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3261 | NA | 13330 | NA | 16416 | 2082 | 0 | EL6021_M178 |  | UINT
EIR6073I1 | Onduleur IIIB-1 UL7003 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3270 | NA | 13339 | NA | 16416 | 2100 | 0 | EL6021_M178 |  | UINT
EIR6073I2 | Onduleur IIIB-1 UL7003 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3271 | NA | 13340 | NA | 16416 | 2102 | 0 | EL6021_M178 |  | UINT
EIR6073I3 | Onduleur IIIB-1 UL7003 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3272 | NA | 13341 | NA | 16416 | 2104 | 0 | EL6021_M178 |  | UINT
EUR6073UB | Onduleur IIIB-1 UL7003 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 500 |  |  | 0 | 500 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3279 | NA | 13348 | NA | 16416 | 2118 | 0 | EL6021_M178 |  | UINT
EFR6073 | Onduleur IIIB-1 UL7003 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 49 | 61 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6073D1 | Onduleur IIIB 1 UL7003 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3281 | NA | 13350 | NA | 16416 | 2122 | 0 | EL6021_M178 |  | UINT
EIR6074I1 | Onduleur IIIB-2 UL7004 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3290 | NA | 13359 | NA | 16416 | 2140 | 0 | EL6021_M178 |  | UINT
EIR6074I2 | Onduleur IIIB-2 UL7004 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3291 | NA | 13360 | NA | 16416 | 2142 | 0 | EL6021_M178 |  | UINT
EIR6074I3 | Onduleur IIIB-2 UL7004 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 115 |  |  | 0 | 115 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3292 | NA | 13361 | NA | 16416 | 2144 | 0 | EL6021_M178 |  | UINT
EUR6074UB | Onduleur IIIB-2 UL7004 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 500 |  |  | 0 | 500 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3299 | NA | 13368 | NA | 16416 | 2158 | 0 | EL6021_M178 |  | UINT
EFR6074 | Onduleur IIIB-2 UL7004 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 49 | 61 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6074D1 | Onduleur IIIB 2 UL7004 (E63) | Energie TGBT et UPS VEGA (E) - E63 |  | 4 |  |  | 3301 | NA | 13370 | NA | 16416 | 2162 | 0 | EL6021_M178 |  | UINT
EIR6075I1 | Onduleur III CUB UL7005 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3310 | NA | 13379 | NA | 16416 | 2180 | 0 | EL6021_M178 |  | UINT
EIR6075I2 | Onduleur III CUB UL7005 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3311 | NA | 13380 | NA | 16416 | 2182 | 0 | EL6021_M178 |  | UINT
EIR6075I3 | Onduleur III CUB UL7005 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3312 | NA | 13381 | NA | 16416 | 2184 | 0 | EL6021_M178 |  | UINT
EUR6075UB | Onduleur III CUB UL7005 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 450 |  |  | 0 | 450 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3319 | NA | 13388 | NA | 16416 | 2198 | 0 | EL6021_M178 |  | UINT
EFR6075 | Onduleur III CUB UL7005 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 49 | 61 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6075D1 | Onduleur III CUB UL7005 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3321 | NA | 13390 | NA | 16416 | 2202 | 0 | EL6021_M178 |  | UINT
EIR6076I1 | Onduleur III CUH UL7006 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3330 | NA | 13399 | NA | 16416 | 2220 | 0 | EL6021_M178 |  | UINT
EIR6076I2 | Onduleur III CUH UL7006 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3331 | NA | 13400 | NA | 16416 | 2222 | 0 | EL6021_M178 |  | UINT
EIR6076I3 | Onduleur III CUH UL7006 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3332 | NA | 13401 | NA | 16416 | 2224 | 0 | EL6021_M178 |  | UINT
EUR6076UB | Onduleur III CUH UL7006 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 450 |  |  | 0 | 450 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3339 | NA | 13408 | NA | 16416 | 2238 | 0 | EL6021_M178 |  | UINT
EFR6076 | Onduleur III CUH UL7006 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 49 | 61 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6076D1 | Onduleur III CUH UL7006 (E64) | Energie TGBT et UPS VEGA (E) - E64 |  | 4 |  |  | 3341 | NA | 13410 | NA | 16416 | 2242 | 0 | EL6021_M178 |  | UINT
EIR6077I1 | Frequency Converter UL7007 Output phase current I1 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3350 | NA | 13419 | NA | 16416 | 2260 | 0 | EL6021_M178 |  | UINT
EIR6077I2 | Frequency Converter UL7007 Output phase current I2 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3351 | NA | 13420 | NA | 16416 | 2262 | 0 | EL6021_M178 |  | UINT
EIR6077I3 | Frequency Converter UL7007 Output phase current I3 | MA | N | RES | 1 | E |  |  | A | 1 | 0 | 28 |  |  | 0 | 28 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3352 | NA | 13421 | NA | 16416 | 2264 | 0 | EL6021_M178 |  | UINT
EUR6077UB | Frequency Converter UL7007 Battery voltage UB | MA | N | RES | 1 | E |  |  | V | 1 | 0 | 450 |  |  | 0 | 450 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3359 | NA | 13428 | NA | 16416 | 2278 | 0 | EL6021_M178 |  | UINT
EFR6077 | Frequency Converter UL7007 Output Frequency | MA | N | RES | 1 | E |  |  | Hz | 1 | 59 | 61 |  |  | 59 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6077D1 | Convertisseur 60Hz UL7007 (E65) | Energie TGBT et UPS VEGA (E) - E65 |  | 4 |  |  | 3361 | NA | 13430 | NA | 16416 | 2282 | 0 | EL6021_M178 |  | UINT
EIR6001I1 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase current I1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1001 | NA | 13468 | NA | 16416 | 2358 | 0 | EL6021_M179 |  | U16
EIR6001I2 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase current I2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1002 | NA | 13469 | NA | 16416 | 2360 | 0 | EL6021_M179 |  | U16
EIR6001I3 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase current I3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1003 | NA | 13470 | NA | 16416 | 2362 | 0 | EL6021_M179 |  | U16
EUR600121 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase to phase voltage U21 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1012 | NA | 13479 | NA | 16416 | 2380 | 0 | EL6021_M179 |  | U16
EUR600132 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase to phase voltage U32 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1013 | NA | 13480 | NA | 16416 | 2382 | 0 | EL6021_M179 |  | U16
EUR600113 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase to phase voltage U13 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1014 | NA | 13481 | NA | 16416 | 2384 | 0 | EL6021_M179 |  | U16
EUR6001V1 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase-to-neutral Voltage V1 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1015 | NA | 13482 | NA | 16416 | 2386 | 0 | EL6021_M179 |  | U16
EUR6001V2 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase-to-neutral Voltage V2 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1016 | NA | 13483 | NA | 16416 | 2388 | 0 | EL6021_M179 |  | U16
EUR6001V3 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Phase-to-neutral Voltage V3 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1017 | NA | 13484 | NA | 16416 | 2390 | 0 | EL6021_M179 |  | U16
EFR6001 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Frequency | MA |  | RES | 1 | E |  |  | Hz | 0.01 | 20 | 80 |  |  | 49 | 51 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1021 | NA | 13488 | NA | 16416 | 2398 | 0 | EL6021_M179 |  | U16
EWR6001 | CAT.II 1D60 TO TGBT-C ZLV (1D61) Active power P | MA |  | RES | 1 | E |  |  | kW | 1 | 0 | 640 |  |  | 0 | 640 |  |  | E | [13 empty] | POL | 6000 | ESY6001D | DEPART TYPE 2 CAT II 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1022 | NA | 13489 | NA | 16416 | 2400 | 0 | EL6021_M179 |  | U16
EIR6002I1 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase current I1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1051 | NA | 13511 | NA | 16416 | 2444 | 0 | EL6021_M179 |  | U16
EIR6002I2 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase current I2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1052 | NA | 13512 | NA | 16416 | 2446 | 0 | EL6021_M179 |  | U16
EIR6002I3 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase current I3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1053 | NA | 13513 | NA | 16416 | 2448 | 0 | EL6021_M179 |  | U16
EUR600221 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase to phase voltage U21 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1062 | NA | 13522 | NA | 16416 | 2466 | 0 | EL6021_M179 |  | U16
EUR600232 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase to phase voltage U32 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1063 | NA | 13523 | NA | 16416 | 2468 | 0 | EL6021_M179 |  | U16
EUR600213 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase to phase voltage U13 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1064 | NA | 13524 | NA | 16416 | 2470 | 0 | EL6021_M179 |  | U16
EUR6002V1 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase-to-neutral Voltage V1 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1065 | NA | 13525 | NA | 16416 | 2472 | 0 | EL6021_M179 |  | U16
EUR6002V2 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase-to-neutral Voltage V2 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1066 | NA | 13526 | NA | 16416 | 2474 | 0 | EL6021_M179 |  | U16
EUR6002V3 | CAT.II 1D60 TO TGBT ZLV (1D61) Phase-to-neutral Voltage V3 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1067 | NA | 13527 | NA | 16416 | 2476 | 0 | EL6021_M179 |  | U16
EFR6002 | CAT.II 1D60 TO TGBT ZLV (1D61) Frequency | MA |  | RES | 1 | E |  |  | Hz | 0.01 | 20 | 80 |  |  | 49 | 51 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1071 | NA | 13531 | NA | 16416 | 2484 | 0 | EL6021_M179 |  | U16
EWR6002 | CAT.II 1D60 TO TGBT ZLV (1D61) Active power P | MA |  | RES | 1 | E |  |  | kW | 1 | 0 | 640 |  |  | 0 | 640 |  |  | E | [13 empty] | POL | 6000 | ESY6002D | DEPART TYPE 2 CAT II 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1072 | NA | 13532 | NA | 16416 | 2486 | 0 | EL6021_M179 |  | U16
EIR6003I1 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase current I1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1101 | NA | 13552 | NA | 16416 | 2526 | 0 | EL6021_M179 |  | U16
EIR6003I2 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase current I2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1102 | NA | 13553 | NA | 16416 | 2528 | 0 | EL6021_M179 |  | U16
EIR6003I3 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase current I3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1103 | NA | 13554 | NA | 16416 | 2530 | 0 | EL6021_M179 |  | U16
EUR600321 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase to phase voltage U21 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1112 | NA | 13563 | NA | 16416 | 2548 | 0 | EL6021_M179 |  | U16
EUR600332 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase to phase voltage U32 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1113 | NA | 13564 | NA | 16416 | 2550 | 0 | EL6021_M179 |  | U16
EUR600313 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase to phase voltage U13 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1114 | NA | 13565 | NA | 16416 | 2552 | 0 | EL6021_M179 |  | U16
EUR6003V1 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase-to-neutral Voltage V1 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1115 | NA | 13566 | NA | 16416 | 2554 | 0 | EL6021_M179 |  | U16
EUR6003V2 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase-to-neutral Voltage V2 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1116 | NA | 13567 | NA | 16416 | 2556 | 0 | EL6021_M179 |  | U16
EUR6003V3 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Phase-to-neutral Voltage V3 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1117 | NA | 13568 | NA | 16416 | 2558 | 0 | EL6021_M179 |  | U16
EFR6003 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Frequency | MA |  | RES | 1 | E |  |  | Hz | 0.01 | 20 | 80 |  |  | 49 | 51 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1121 | NA | 13572 | NA | 16416 | 2566 | 0 | EL6021_M179 |  | U16
EWR6003 | CAT.I 1D60 TO TGBT-C ZLV (1D61) Active power P | MA |  | RES | 1 | E |  |  | kW | 1 | 0 | 640 |  |  | 0 | 640 |  |  | E | [13 empty] | POL | 6000 | ESY6003D | DEPART TYPE 2 CAT I 1D60 VERS TGBT C ZLV 1D61 (E69) | Energie 1D60 VEGA (E) - E69 |  | 5 |  |  | 1122 | NA | 13573 | NA | 16416 | 2568 | 0 | EL6021_M179 |  | U16
EIR6004I1 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase current I1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1151 | NA | 13593 | NA | 16416 | 2608 | 0 | EL6021_M179 |  | U16
EIR6004I2 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase current I2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1152 | NA | 13594 | NA | 16416 | 2610 | 0 | EL6021_M179 |  | U16
EIR6004I3 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase current I3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1153 | NA | 13595 | NA | 16416 | 2612 | 0 | EL6021_M179 |  | U16
EUR600421 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase to phase voltage U21 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1162 | NA | 13604 | NA | 16416 | 2630 | 0 | EL6021_M179 |  | U16
EUR600432 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase to phase voltage U32 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1163 | NA | 13605 | NA | 16416 | 2632 | 0 | EL6021_M179 |  | U16
EUR600413 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase to phase voltage U13 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1164 | NA | 13606 | NA | 16416 | 2634 | 0 | EL6021_M179 |  | U16
EUR6004V1 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase-to-neutral Voltage V1 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1165 | NA | 13607 | NA | 16416 | 2636 | 0 | EL6021_M179 |  | U16
EUR6004V2 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase-to-neutral Voltage V2 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1166 | NA | 13608 | NA | 16416 | 2638 | 0 | EL6021_M179 |  | U16
EUR6004V3 | CAT.I 1D60 TO TGBT ZLV (1D61) Phase-to-neutral Voltage V3 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1167 | NA | 13609 | NA | 16416 | 2640 | 0 | EL6021_M179 |  | U16
EFR6004 | CAT.I 1D60 TO TGBT ZLV (1D61) Frequency | MA |  | RES | 1 | E |  |  | Hz | 0.01 | 20 | 80 |  |  | 49 | 51 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1171 | NA | 13613 | NA | 16416 | 2648 | 0 | EL6021_M179 |  | U16
EWR6004 | CAT.I 1D60 TO TGBT ZLV (1D61) Active power P | MA |  | RES | 1 | E |  |  | kW | 1 | 0 | 640 |  |  | 0 | 640 |  |  | E | [13 empty] | POL | 6000 | ESY6004D | DEPART TYPE 2 CAT I 1D60 VERS TGBT ZLV 1D61 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1172 | NA | 13614 | NA | 16416 | 2650 | 0 | EL6021_M179 |  | U16
EIR6142I1 | CAT.I 1D60 TO 1D42 Phase current I1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1201 | NA | 13634 | NA | 16416 | 2690 | 0 | EL6021_M179 |  | U16
EIR6142I2 | CAT.I 1D60 TO 1D42 Phase current I2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1202 | NA | 13635 | NA | 16416 | 2692 | 0 | EL6021_M179 |  | U16
EIR6142I3 | CAT.I 1D60 TO 1D42 Phase current I3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1203 | NA | 13636 | NA | 16416 | 2694 | 0 | EL6021_M179 |  | U16
EUR614221 | CAT.I 1D60 TO 1D42 Phase to phase voltage U21 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1212 | NA | 13645 | NA | 16416 | 2712 | 0 | EL6021_M179 |  | U16
EUR614232 | CAT.I 1D60 TO 1D42 Phase to phase voltage U32 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1213 | NA | 13646 | NA | 16416 | 2714 | 0 | EL6021_M179 |  | U16
EUR614213 | CAT.I 1D60 TO 1D42 Phase to phase voltage U13 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1214 | NA | 13647 | NA | 16416 | 2716 | 0 | EL6021_M179 |  | U16
EUR6142V1 | CAT.I 1D60 TO 1D42 Phase-to-neutral Voltage V1 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1215 | NA | 13648 | NA | 16416 | 2718 | 0 | EL6021_M179 |  | U16
EUR6142V2 | CAT.I 1D60 TO 1D42 Phase-to-neutral Voltage V2 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1216 | NA | 13649 | NA | 16416 | 2720 | 0 | EL6021_M179 |  | U16
EUR6142V3 | CAT.I 1D60 TO 1D42 Phase-to-neutral Voltage V3 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1217 | NA | 13650 | NA | 16416 | 2722 | 0 | EL6021_M179 |  | U16
EFR6142 | CAT.I 1D60 TO 1D42 Frequency | MA |  | RES | 1 | E |  |  | Hz | 0.01 | 20 | 80 |  |  | 49 | 51 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1221 | NA | 13654 | NA | 16416 | 2730 | 0 | EL6021_M179 |  | U16
EWR6142 | CAT.I 1D60 TO 1D42 Active power P | MA |  | RES | 1 | E |  |  | kW | 1 | 0 | 640 |  |  | 0 | 640 |  |  | E | [13 empty] | POL | 6000 | ESY6142D | DEPART TYPE 1 CAT I 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1222 | NA | 13655 | NA | 16416 | 2732 | 0 | EL6021_M179 |  | U16
EIR6242I1 | CAT.II 1D60 TO 1D42 Phase current I1 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1251 | NA | 13675 | NA | 16416 | 2772 | 0 | EL6021_M179 |  | U16
EIR6242I2 | CAT.II 1D60 TO 1D42 Phase current I2 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1252 | NA | 13676 | NA | 16416 | 2774 | 0 | EL6021_M179 |  | U16
EIR6242I3 | CAT.II 1D60 TO 1D42 Phase current I3 | MA |  | RES | 1 | E |  |  | A | 0.1 | 0 | 200 |  |  | 0 | 200 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1253 | NA | 13677 | NA | 16416 | 2776 | 0 | EL6021_M179 |  | U16
EUR624221 | CAT.II 1D60 TO 1D42 Phase to phase voltage U21 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1262 | NA | 13686 | NA | 16416 | 2794 | 0 | EL6021_M179 |  | U16
EUR624232 | CAT.II 1D60 TO 1D42 Phase to phase voltage U32 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1263 | NA | 13687 | NA | 16416 | 2796 | 0 | EL6021_M179 |  | U16
EUR624213 | CAT.II 1D60 TO 1D42 Phase to phase voltage U13 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 1 | 25 |  |  | 18 | 22 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1264 | NA | 13688 | NA | 16416 | 2798 | 0 | EL6021_M179 |  | U16
EUR6242V1 | CAT.II 1D60 TO 1D42 Phase-to-neutral Voltage V1 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1265 | NA | 13689 | NA | 16416 | 2800 | 0 | EL6021_M179 |  | U16
EUR6242V2 | CAT.II 1D60 TO 1D42 Phase-to-neutral Voltage V2 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1266 | NA | 13690 | NA | 16416 | 2802 | 0 | EL6021_M179 |  | U16
EUR6242V3 | CAT.II 1D60 TO 1D42 Phase-to-neutral Voltage V3 | MA |  | RES | 1 | E |  |  | KV | 0.001 | 0 | 15 |  |  | 0 | 15 |  |  | E | [6 empty] | 3 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1267 | NA | 13691 | NA | 16416 | 2804 | 0 | EL6021_M179 |  | U16
EFR6242 | CAT.II 1D60 TO 1D42 Frequency | MA |  | RES | 1 | E |  |  | Hz | 0.01 | 20 | 80 |  |  | 49 | 51 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1271 | NA | 13695 | NA | 16416 | 2812 | 0 | EL6021_M179 |  | U16
EWR6242 | CAT.II 1D60 TO 1D42 Active power P | MA |  | RES | 1 | E |  |  | kW | 1 | 0 | 640 |  |  | 0 | 640 |  |  | E | [13 empty] | POL | 6000 | ESY6242D | DEPART TYPE 1 CAT II 1D60 VERS 1D42 (E68) | Energie 1D60 VEGA (E) - E68 |  | 5 |  |  | 1272 | NA | 13696 | NA | 16416 | 2814 | 0 | EL6021_M179 |  | U16
GTR6012F2 | VEGA BUNKER PLC : TEMPERATURE SUPPLY COLD WATER GANTRY | MA |  | RES | 1 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 4 | 8 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z1 | HVAC03;HVAC13;HVAC14 | HVAC |  | 6 |  |  | 3050 | NA | 13849 | NA | 16416 | 3120 | 0 | EL6021_M180 |  | INT
GTR6034F2 | VEGA BUNKER PLC : TEMPERATURE RETURN COLD WATER GANTRY | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 7 | 18 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z2 | HVAC03;HVAC04;HVAC13;HVAC14 | HVAC |  | 6 |  |  | 3051 | NA | 13850 | NA | 16416 | 3122 | 0 | EL6021_M180 |  | INT
GTR6045F1 | VEGA BUNKER PLC : TEMPERATURE SUPPLY COLD WATER BUNKER | MA |  | RES | 1 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 4 | 8 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z3 | HVAC03;HVAC04 | HVAC |  | 6 |  |  | 3052 | NA | 13851 | NA | 16416 | 3124 | 0 | EL6021_M180 |  | INT
GTR6001F1 | VEGA BUNKER PLC : TEMPERATURE RETURN COLD WATER BUNKER | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 7 | 18 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z4 | HVAC03 | HVAC |  | 6 |  |  | 3053 | NA | 13852 | NA | 16416 | 3126 | 0 | EL6021_M180 |  | INT
CTR6045F3 | VEGA BUNKER PLC : TEMPERATURE SUPPLY HOT WATER BUNKER/GANTRY | MA |  | RES | 1 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 35 | 50 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z11 | HVAC03 | HVAC |  | 6 |  |  | 3056 | NA | 13855 | NA | 16416 | 3132 | 0 | EL6021_M180 |  | INT
CTR6034F2 | VEGA BUNKER PLC : TEMPERATURE RETURN HOT WATER GANTRY | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 40 | 70 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z12 | HVAC03 | HVAC |  | 6 |  |  | 3057 | NA | 13856 | NA | 16416 | 3134 | 0 | EL6021_M180 |  | INT
CTR6001F1 | VEGA BUNKER PLC : TEMPERATURE RETURN HOT WATER BUNKER | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 40 | 70 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6126Z9 | HVAC03 | HVAC |  | 6 |  |  | 3058 | NA | 13857 | NA | 16416 | 3136 | 0 | EL6021_M180 |  | INT
VTR6100V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 100.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3079 | NA | 13878 | NA | 16416 | 3178 | 0 | EL6021_M180 |  | INT
VTR6002V3 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 002.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3081 | NA | 13880 | NA | 16416 | 3182 | 0 | EL6021_M180 |  | INT
VTR6106V2 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 106.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3083 | NA | 13882 | NA | 16416 | 3186 | 0 | EL6021_M180 |  | INT
VTR6004V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 004.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3085 | NA | 13884 | NA | 16416 | 3190 | 0 | EL6021_M180 |  | INT
VTR6105V2 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 105.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3087 | NA | 13886 | NA | 16416 | 3194 | 0 | EL6021_M180 |  | INT
VTR6106V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 106.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3089 | NA | 13888 | NA | 16416 | 3198 | 0 | EL6021_M180 |  | INT
VTR6006V2 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 006.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3091 | NA | 13890 | NA | 16416 | 3202 | 0 | EL6021_M180 |  | INT
VTR6108V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 108.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3093 | NA | 13892 | NA | 16416 | 3206 | 0 | EL6021_M180 |  | INT
VTR6122V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 122.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3095 | NA | 13894 | NA | 16416 | 3210 | 0 | EL6021_M180 |  | INT
VTR6115V2 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 115.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3097 | NA | 13896 | NA | 16416 | 3214 | 0 | EL6021_M180 |  | INT
VTR6117V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 117.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3099 | NA | 13898 | NA | 16416 | 3218 | 0 | EL6021_M180 |  | INT
VTR6115V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 115.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3101 | NA | 13900 | NA | 16416 | 3222 | 0 | EL6021_M180 |  | INT
VTR6120V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 120.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3103 | NA | 13902 | NA | 16416 | 3226 | 0 | EL6021_M180 |  | INT
VTR6121V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 121.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3105 | NA | 13904 | NA | 16416 | 3230 | 0 | EL6021_M180 |  | INT
VTR6012V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 012.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC07 | HVAC |  | 6 |  |  | 3107 | NA | 13906 | NA | 16416 | 3234 | 0 | EL6021_M180 |  | INT
VTR6126V1 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 126.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3109 | NA | 13908 | NA | 16416 | 3238 | 0 | EL6021_M180 |  | INT
VTR6118V5 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 118.5 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3111 | NA | 13910 | NA | 16416 | 3242 | 0 | EL6021_M180 |  | INT
VTR6118V4 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 118.4 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3113 | NA | 13912 | NA | 16416 | 3246 | 0 | EL6021_M180 |  | INT
VTR6118V3 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 118.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC08 | HVAC |  | 6 |  |  | 3115 | NA | 13914 | NA | 16416 | 3250 | 0 | EL6021_M180 |  | INT
VTR6121V2 | VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) 121.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC1 | HVAC09 | HVAC |  | 6 |  |  | 3117 | NA | 13916 | NA | 16416 | 3254 | 0 | EL6021_M180 |  | INT
VTR6007A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 007.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6007DC1 | HVAC07 | HVAC |  | 6 |  |  | 3125 | NA | 13924 | NA | 16416 | 3270 | 0 | EL6021_M180 |  | INT
VTR6101A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 101.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6101DC1 | HVAC07 | HVAC |  | 6 |  |  | 3127 | NA | 13926 | NA | 16416 | 3274 | 0 | EL6021_M180 |  | INT
VTR6013A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 013.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6013DC1 | HVAC07 | HVAC |  | 6 |  |  | 3129 | NA | 13928 | NA | 16416 | 3278 | 0 | EL6021_M180 |  | INT
VTR6103A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 103.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6103DC1 | HVAC07 | HVAC |  | 6 |  |  | 3131 | NA | 13930 | NA | 16416 | 3282 | 0 | EL6021_M180 |  | INT
VTR6113A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 113.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6113DC1 | HVAC08 | HVAC |  | 6 |  |  | 3133 | NA | 13932 | NA | 16416 | 3286 | 0 | EL6021_M180 |  | INT
VTR6116A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 116.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6116DC1 | HVAC08 | HVAC |  | 6 |  |  | 3135 | NA | 13934 | NA | 16416 | 3290 | 0 | EL6021_M180 |  | INT
VTR6002A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (SCHNEIDER) 002.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6002DC1 | HVAC07 | HVAC |  | 6 |  |  | 3143 | NA | 13942 | NA | 16416 | 3306 | 0 | EL6021_M180 |  | INT
VTR6004A1 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (SCHNEIDER) 004.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6004DC1 | HVAC07 | HVAC |  | 6 |  |  | 3144 | NA | 13943 | NA | 16416 | 3308 | 0 | EL6021_M180 |  | INT
VTR6118V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 118.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3194 | NA | 13993 | NA | 16416 | 3408 | 0 | EL6021_M180 |  | INT
VTR6118V2 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 118.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3196 | NA | 13995 | NA | 16416 | 3412 | 0 | EL6021_M180 |  | INT
VTR6115V3 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 115.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3198 | NA | 13997 | NA | 16416 | 3416 | 0 | EL6021_M180 |  | INT
VTR6115V4 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 115.4 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3200 | NA | 13999 | NA | 16416 | 3420 | 0 | EL6021_M180 |  | INT
VTR6117V2 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 117.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3202 | NA | 14001 | NA | 16416 | 3424 | 0 | EL6021_M180 |  | INT
VTR6112V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 112.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3204 | NA | 14003 | NA | 16416 | 3428 | 0 | EL6021_M180 |  | INT
VTR6111V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 111.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3206 | NA | 14005 | NA | 16416 | 3432 | 0 | EL6021_M180 |  | INT
VTR6108V2 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 108.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3208 | NA | 14007 | NA | 16416 | 3436 | 0 | EL6021_M180 |  | INT
VTR6108V3 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 108.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3210 | NA | 14009 | NA | 16416 | 3440 | 0 | EL6021_M180 |  | INT
VTR6107V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 107.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3212 | NA | 14011 | NA | 16416 | 3444 | 0 | EL6021_M180 |  | INT
VTR6106V3 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 106.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3214 | NA | 14013 | NA | 16416 | 3448 | 0 | EL6021_M180 |  | INT
VTR6106V4 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 106.4 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC08 | HVAC |  | 6 |  |  | 3216 | NA | 14015 | NA | 16416 | 3452 | 0 | EL6021_M180 |  | INT
VTR6105V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 105.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3218 | NA | 14017 | NA | 16416 | 3456 | 0 | EL6021_M180 |  | INT
VTR6121V3 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 121.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC09 | HVAC |  | 6 |  |  | 3220 | NA | 14019 | NA | 16416 | 3460 | 0 | EL6021_M180 |  | INT
VTR6104V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 104.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3222 | NA | 14021 | NA | 16416 | 3464 | 0 | EL6021_M180 |  | INT
VTR6100V2 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 100.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3224 | NA | 14023 | NA | 16416 | 3468 | 0 | EL6021_M180 |  | INT
VTR6012V2 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 012.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3226 | NA | 14025 | NA | 16416 | 3472 | 0 | EL6021_M180 |  | INT
VTR6006V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 006.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3230 | NA | 14029 | NA | 16416 | 3480 | 0 | EL6021_M180 |  | INT
VTR6006V3 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 006.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3232 | NA | 14031 | NA | 16416 | 3484 | 0 | EL6021_M180 |  | INT
VTR6004V3 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 004.3 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3234 | NA | 14033 | NA | 16416 | 3488 | 0 | EL6021_M180 |  | INT
VTR6002V2 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 002.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3236 | NA | 14035 | NA | 16416 | 3492 | 0 | EL6021_M180 |  | INT
VTR6007A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 007.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6007DC2 | HVAC07 | HVAC |  | 6 |  |  | 3240 | NA | 14039 | NA | 16416 | 3500 | 0 | EL6021_M180 |  | INT
VTR6101A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 101.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6101DC2 | HVAC07 | HVAC |  | 6 |  |  | 3242 | NA | 14041 | NA | 16416 | 3504 | 0 | EL6021_M180 |  | INT
VTR6103A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 103.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6103DC2 | HVAC07 | HVAC |  | 6 |  |  | 3244 | NA | 14043 | NA | 16416 | 3508 | 0 | EL6021_M180 |  | INT
VTR6113A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 113.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6113DC2 | HVAC08 | HVAC |  | 6 |  |  | 3246 | NA | 14045 | NA | 16416 | 3512 | 0 | EL6021_M180 |  | INT
VTR6116A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) 116.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6116DC2 | HVAC08 | HVAC |  | 6 |  |  | 3248 | NA | 14047 | NA | 16416 | 3516 | 0 | EL6021_M180 |  | INT
ZVB6951VH1 | ETAT SERVER HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6952VH1 | ETAT NOTIFIER HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6953VH1 | ETAT LOGGER HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6954VH1 | ETAT WEBSOCKET HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6951VH2 | ETAT SERVER HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6952VH2 | ETAT NOTIFIER HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6953VH2 | ETAT LOGGER HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6954VH2 | ETAT WEBSOCKET HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZIS6955IH1 | ETAT IIS HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZIS6955IH2 | ETAT IIS HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZSQ6956QH1 | ETAT SQL SERVICE HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZSQ6957QH1 | ETAT SQL SERVER AGENT HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZSQ6956QH2 | ETAT SQL SERVICE HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZSQ6957QH2 | ETAT SQL SERVER AGENT HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6958VH1 | ETAT NOTIFIER COMMANDS HLCS 1 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
ZVB6958VH2 | ETAT NOTIFIER COMMANDS HLCS 2 | MA | N | INT | 0 | Z |  | R | [8 empty] | STOPPED | [18 empty] | VMC04 |  | NEW | [12 empty] | STRING
EWR6101R | TD 013 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6101V1*EIR6101I1 + EUR6101V2*EIR6101I2 + EUR6101V1*EIR6101I1)*EWR6101PF | [5 empty] | TD 1601-013-30 CAT IIIA (E70)
EWR6101Q | TD 013 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6101V1*EIR6101I1 + EUR6101V2*EIR6101I2 + EUR6101V1*EIR6101I1)*sin[arcos(EWR6101PF)] | [5 empty] | TD 1601-013-30 CAT IIIA (E70)
EWR6101S | TD 013 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6101V1*EIR6101I1 + EUR6101V2*EIR6101I2 + EUR6101V1*EIR6101I1) | [5 empty] | TD 1601-013-30 CAT IIIA (E70)
EWR6102R | TD 013 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6102V1*EIR6102I1 + EUR6102V2*EIR6102I2 + EUR6102V1*EIR6102I1)*EWR6102PF | [5 empty] | TD 1601-013-31 CAT IIIB (E70)
EWR6102Q | TD 013 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6102V1*EIR6102I1 + EUR6102V2*EIR6102I2 + EUR6102V1*EIR6102I1)*sin[arcos(EWR6102PF)] | [5 empty] | TD 1601-013-31 CAT IIIB (E70)
EWR6102S | TD 013 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6102V1*EIR6102I1 + EUR6102V2*EIR6102I2 + EUR6102V1*EIR6102I1) | [5 empty] | TD 1601-013-31 CAT IIIB (E70)
EWR6103R | TD1 004 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6103V1*EIR6103I1 + EUR6103V2*EIR6103I2 + EUR6103V1*EIR6103I1)*EWR6103PF | [5 empty] | TD1 1601-004-30 CAT IIIA (E70)
EWR6103Q | TD1 004 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6103V1*EIR6103I1 + EUR6103V2*EIR6103I2 + EUR6103V1*EIR6103I1)*sin[arcos(EWR6103PF)] | [5 empty] | TD1 1601-004-30 CAT IIIA (E70)
EWR6103S | TD1 004 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6103V1*EIR6103I1 + EUR6103V2*EIR6103I2 + EUR6103V1*EIR6103I1) | [5 empty] | TD1 1601-004-30 CAT IIIA (E70)
EWR6104R | TD2 004 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6104V1*EIR6104I1 + EUR6104V2*EIR6104I2 + EUR6104V1*EIR6104I1)*EWR6104PF | [5 empty] | TD2 1601-004-32 CAT IIIA (E70)
EWR6104Q | TD2 004 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6104V1*EIR6104I1 + EUR6104V2*EIR6104I2 + EUR6104V1*EIR6104I1)*sin[arcos(EWR6104PF)] | [5 empty] | TD2 1601-004-32 CAT IIIA (E70)
EWR6104S | TD2 004 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6104V1*EIR6104I1 + EUR6104V2*EIR6104I2 + EUR6104V1*EIR6104I1) | [5 empty] | TD2 1601-004-32 CAT IIIA (E70)
EWR6105R | TD1 004 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6105V1*EIR6105I1 + EUR6105V2*EIR6105I2 + EUR6105V1*EIR6105I1)*EWR6105PF | [5 empty] | TD1 1601-004-31 CAT IIIB (E70)
EWR6105Q | TD1 004 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6105V1*EIR6105I1 + EUR6105V2*EIR6105I2 + EUR6105V1*EIR6105I1)*sin[arcos(EWR6105PF)] | [5 empty] | TD1 1601-004-31 CAT IIIB (E70)
EWR6105S | TD1 004 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6105V1*EIR6105I1 + EUR6105V2*EIR6105I2 + EUR6105V1*EIR6105I1) | [5 empty] | TD1 1601-004-31 CAT IIIB (E70)
EWR6106R | TD2 004 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6106V1*EIR6106I1 + EUR6106V2*EIR6106I2 + EUR6106V1*EIR6106I1)*EWR6106PF | [5 empty] | TD2 1601-004-34 CAT IIIB (E70)
EWR6106Q | TD2 004 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6106V1*EIR6106I1 + EUR6106V2*EIR6106I2 + EUR6106V1*EIR6106I1)*sin[arcos(EWR6106PF)] | [5 empty] | TD2 1601-004-34 CAT IIIB (E70)
EWR6106S | TD2 004 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6106V1*EIR6106I1 + EUR6106V2*EIR6106I2 + EUR6106V1*EIR6106I1) | [5 empty] | TD2 1601-004-34 CAT IIIB (E70)
EWR6107R | TD1 103 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6107V1*EIR6107I1 + EUR6107V2*EIR6107I2 + EUR6107V1*EIR6107I1)*EWR6107PF | [5 empty] | TD1 1601-103-30 CAT IIIA (E70)
EWR6107Q | TD1 103 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6107V1*EIR6107I1 + EUR6107V2*EIR6107I2 + EUR6107V1*EIR6107I1)*sin[arcos(EWR6107PF)] | [5 empty] | TD1 1601-103-30 CAT IIIA (E70)
EWR6107S | TD1 103 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6107V1*EIR6107I1 + EUR6107V2*EIR6107I2 + EUR6107V1*EIR6107I1) | [5 empty] | TD1 1601-103-30 CAT IIIA (E70)
EWR6108R | TD2 103 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6108V1*EIR6108I1 + EUR6108V2*EIR6108I2 + EUR6108V1*EIR6108I1)*EWR6108PF | [5 empty] | TD2 1601-103-32 CAT IIIA (E70)
EWR6108Q | TD2 103 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6108V1*EIR6108I1 + EUR6108V2*EIR6108I2 + EUR6108V1*EIR6108I1)*sin[arcos(EWR6108PF)] | [5 empty] | TD2 1601-103-32 CAT IIIA (E70)
EWR6108S | TD2 103 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6108V1*EIR6108I1 + EUR6108V2*EIR6108I2 + EUR6108V1*EIR6108I1) | [5 empty] | TD2 1601-103-32 CAT IIIA (E70)
EWR6109R | TD3 103 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6109V1*EIR6109I1 + EUR6109V2*EIR6109I2 + EUR6109V1*EIR6109I1)*EWR6109PF | [5 empty] | TD3 1601-103-34 CAT IIIA (E70)
EWR6109Q | TD3 103 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6109V1*EIR6109I1 + EUR6109V2*EIR6109I2 + EUR6109V1*EIR6109I1)*sin[arcos(EWR6109PF)] | [5 empty] | TD3 1601-103-34 CAT IIIA (E70)
EWR6109S | TD3 103 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6109V1*EIR6109I1 + EUR6109V2*EIR6109I2 + EUR6109V1*EIR6109I1) | [5 empty] | TD3 1601-103-34 CAT IIIA (E70)
EWR6110R | TD4 103 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6110V1*EIR6110I1 + EUR6110V2*EIR6110I2 + EUR6110V1*EIR6110I1)*EWR6110PF | [5 empty] | TD4 1601-103-36 CAT IIIA (E70)
EWR6110Q | TD4 103 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6110V1*EIR6110I1 + EUR6110V2*EIR6110I2 + EUR6110V1*EIR6110I1)*sin[arcos(EWR6110PF)] | [5 empty] | TD4 1601-103-36 CAT IIIA (E70)
EWR6110S | TD4 103 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6110V1*EIR6110I1 + EUR6110V2*EIR6110I2 + EUR6110V1*EIR6110I1) | [5 empty] | TD4 1601-103-36 CAT IIIA (E70)
EWR6111R | TD1 103 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6111V1*EIR6111I1 + EUR6111V2*EIR6111I2 + EUR6111V1*EIR6111I1)*EWR6111PF | [5 empty] | TD1 1601-103-31 CAT IIIB (E70)
EWR6111Q | TD1 103 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6111V1*EIR6111I1 + EUR6111V2*EIR6111I2 + EUR6111V1*EIR6111I1)*sin[arcos(EWR6111PF)] | [5 empty] | TD1 1601-103-31 CAT IIIB (E70)
EWR6111S | TD1 103 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6111V1*EIR6111I1 + EUR6111V2*EIR6111I2 + EUR6111V1*EIR6111I1) | [5 empty] | TD1 1601-103-31 CAT IIIB (E70)
EWR6112R | TD2 103 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6112V1*EIR6112I1 + EUR6112V2*EIR6112I2 + EUR6112V1*EIR6112I1)*EWR6112PF | [5 empty] | TD2 1601-103-33 CAT IIIB (E70)
EWR6112Q | TD2 103 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6112V1*EIR6112I1 + EUR6112V2*EIR6112I2 + EUR6112V1*EIR6112I1)*sin[arcos(EWR6112PF)] | [5 empty] | TD2 1601-103-33 CAT IIIB (E70)
EWR6112S | TD2 103 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6112V1*EIR6112I1 + EUR6112V2*EIR6112I2 + EUR6112V1*EIR6112I1) | [5 empty] | TD2 1601-103-33 CAT IIIB (E70)
EWR6113R | TD3 103 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6113V1*EIR6113I1 + EUR6113V2*EIR6113I2 + EUR6113V1*EIR6113I1)*EWR6113PF | [5 empty] | TD3 1601-103-35 CAT IIIB (E70)
EWR6113Q | TD3 103 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6113V1*EIR6113I1 + EUR6113V2*EIR6113I2 + EUR6113V1*EIR6113I1)*sin[arcos(EWR6113PF)] | [5 empty] | TD3 1601-103-35 CAT IIIB (E70)
EWR6113S | TD3 103 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6113V1*EIR6113I1 + EUR6113V2*EIR6113I2 + EUR6113V1*EIR6113I1) | [5 empty] | TD3 1601-103-35 CAT IIIB (E70)
EWR6114R | TD4 103 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6114V1*EIR6114I1 + EUR6114V2*EIR6114I2 + EUR6114V1*EIR6114I1)*EWR6114PF | [5 empty] | TD4 1601-103-37 CAT IIIB (E70)
EWR6114Q | TD4 103 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6114V1*EIR6114I1 + EUR6114V2*EIR6114I2 + EUR6114V1*EIR6114I1)*sin[arcos(EWR6114PF)] | [5 empty] | TD4 1601-103-37 CAT IIIB (E70)
EWR6114S | TD4 103 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6114V1*EIR6114I1 + EUR6114V2*EIR6114I2 + EUR6114V1*EIR6114I1) | [5 empty] | TD4 1601-103-37 CAT IIIB (E70)
EWR6115R | TD 126 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6115V1*EIR6115I1 + EUR6115V2*EIR6115I2 + EUR6115V1*EIR6115I1)*EWR6115PF | [5 empty] | TD AXIMA 1601-126-002 CAT IIIA (E70)
EWR6115Q | TD 126 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6115V1*EIR6115I1 + EUR6115V2*EIR6115I2 + EUR6115V1*EIR6115I1)*sin[arcos(EWR6115PF)] | [5 empty] | TD AXIMA 1601-126-002 CAT IIIA (E70)
EWR6115S | TD 126 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6115V1*EIR6115I1 + EUR6115V2*EIR6115I2 + EUR6115V1*EIR6115I1) | [5 empty] | TD AXIMA 1601-126-002 CAT IIIA (E70)
EWR6116R | TD 126 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6116V1*EIR6116I1 + EUR6116V2*EIR6116I2 + EUR6116V1*EIR6116I1)*EWR6116PF | [5 empty] | TD AXIMA 1601-126-002 CAT IIIB (E70)
EWR6116Q | TD 126 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6116V1*EIR6116I1 + EUR6116V2*EIR6116I2 + EUR6116V3*EIR6116I3)*sin[arcos(EWR6116PF)] | [5 empty] | TD AXIMA 1601-126-002 CAT IIIB (E70)
EWR6116S | TD 126 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6116V1*EIR6116I1 + EUR6116V2*EIR6116I2 + EUR6116V1*EIR6116I1) | [5 empty] | TD AXIMA 1601-126-002 CAT IIIB (E70)
EWR6117R | TD AUX CLIM LOCAL 126 SECT.1 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6117V1*EIR6117I1 + EUR6117V2*EIR6117I2 + EUR6117V1*EIR6117I1)*EWR6117PF | [5 empty] | TD AXIMA 1601-126-001 Sect I (E70)
EWR6117Q | TD AUX CLIM LOCAL 126 SECT.1 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6117V1*EIR6117I1 + EUR6117V2*EIR6117I2 + EUR6117V1*EIR6117I1)*sin[arcos(EWR6117PF)] | [5 empty] | TD AXIMA 1601-126-001 Sect I (E70)
EWR6117S | TD AUX CLIM LOCAL 126 SECT.1 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6117V1*EIR6117I1 + EUR6117V2*EIR6117I2 + EUR6117V1*EIR6117I1) | [5 empty] | TD AXIMA 1601-126-001 Sect I (E70)
EWR6118R | TD AUX CLIM LOCAL 126 SECT.3 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6118V1*EIR6118I1 + EUR6118V2*EIR6118I2 + EUR6118V1*EIR6118I1)*EWR6118PF | [5 empty] | TD AXIMA 1601-126-003 Sect 3 (E70)
EWR6118Q | TD AUX CLIM LOCAL 126 SECT.3 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6118V1*EIR6118I1 + EUR6118V2*EIR6118I2 + EUR6118V1*EIR6118I1)*sin[arcos(EWR6118PF)] | [5 empty] | TD AXIMA 1601-126-003 Sect 3 (E70)
EWR6118S | TD AUX CLIM LOCAL 126 SECT.3 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6118V1*EIR6118I1 + EUR6118V2*EIR6118I2 + EUR6118V1*EIR6118I1) | [5 empty] | TD AXIMA 1601-126-003 Sect 3 (E70)
EWR6119R | TD LOCAL 117 Total Real Power R (CAT II) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6119V1*EIR6119I1 + EUR6119V2*EIR6119I2 + EUR6119V1*EIR6119I1)*EWR6119PF | [5 empty] | TD 1601-117-20 (E70)
EWR6119Q | TD LOCAL 117 Total Reactive Power Q (CAT II) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6119V1*EIR6119I1 + EUR6119V2*EIR6119I2 + EUR6119V1*EIR6119I1)*sin[arcos(EWR6119PF)] | [5 empty] | TD 1601-117-20 (E70)
EWR6119S | TD LOCAL 117 Total Apparent Power S (CAT II) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6119V1*EIR6119I1 + EUR6119V2*EIR6119I2 + EUR6119V1*EIR6119I1) | [5 empty] | TD 1601-117-20 (E70)
EWR6120R | TD1 002 IIIA Total Real Power R (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6120V1*EIR6120I1 + EUR6120V2*EIR6120I2 + EUR6120V1*EIR6120I1)*EWR6120PF | [5 empty] | TD1 1601-002-30 CAT IIIA (E70)
EWR6120Q | TD1 002 IIIA Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6120V1*EIR6120I1 + EUR6120V2*EIR6120I2 + EUR6120V1*EIR6120I1)*sin[arcos(EWR6120PF)] | [5 empty] | TD1 1601-002-30 CAT IIIA (E70)
EWR6120S | TD1 002 IIIA Total Apparent Power S (CAT IIIA) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6120V1*EIR6120I1 + EUR6120V2*EIR6120I2 + EUR6120V1*EIR6120I1) | [5 empty] | TD1 1601-002-30 CAT IIIA (E70)
EWR6121R | TD1 002 IIIB Total Real Power R (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kW | 1000 | [19 empty] | (EUR6121V1*EIR6121I1 + EUR6121V2*EIR6121I2 + EUR6121V1*EIR6121I1)*EWR6121PF | [5 empty] | TD1 1601-002-31 CAT IIIB (E70)
EWR6121Q | TD1 002 IIIB Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVAR | 1000 | [19 empty] | (EUR6121V1*EIR6121I1 + EUR6121V2*EIR6121I2 + EUR6121V1*EIR6121I1)*sin[arcos(EWR6121PF)] | [5 empty] | TD1 1601-002-31 CAT IIIB (E70)
EWR6121S | TD1 002 IIIB Total Apparent Power S (CAT IIIB) | MA | N | CAL | 1 | E |  |  | kVA | 1000 | [19 empty] | (EUR6121V1*EIR6121I1 + EUR6121V2*EIR6121I2 + EUR6121V1*EIR6121I1) | [5 empty] | TD1 1601-002-31 CAT IIIB (E70)
VTR6001V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 001.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3252 | NA | 14051 | NA | 16416 | 3524 | 0 | EL6021_M180 |  | INT
VTR6008V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 008.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3254 | NA | 14053 | NA | 16416 | 3528 | 0 | EL6021_M180 |  | INT
VTR6009V1 | VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) 009.1 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VVV6126DC2 | HVAC07 | HVAC |  | 6 |  |  | 3256 | NA | 14055 | NA | 16416 | 3532 | 0 | EL6021_M180 |  | INT
VCN7005M1 | AC 1 SALLE 05 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1403 | NA | [7 empty] | INT
VTR6002A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (SCHNEIDER) 002.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6002DC2 | HVAC07 | HVAC |  | 6 |  |  | 3261 | NA | 14060 | NA | 16416 | 3542 | 0 | EL6021_M180 |  | INT
VVV7010M1 | VC 1 SALLE 10 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1405 | NA | [7 empty] | INT
VTR6004A2 | VEGA BUNKER PLC : TEMPERATURE AC CABINET (SCHNEIDER) 004.2 | MA |  | RES | 1 | C |  |  | °C | 0.1 | 0 | 1000 |  |  | 24 | 26 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VCN6004DC2 | HVAC07 | HVAC |  | 6 |  |  | 3262 | NA | 14061 | NA | 16416 | 3544 | 0 | EL6021_M180 |  | INT
VTR6102 | VEGA GANTRY PLC : AMBIENT TEMPERATURE FAN CTA P03 (LEVEL 20M) | MA |  | RES | 1 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z4 | HVAC14;HVAC18 | HVAC |  | 7 |  |  | 3052 | NA | 14199 | NA | 16416 | 3820 | 0 | EL6021_M181 |  | INT
VHR6102 | VEGA GANTRY PLC : AMBIENT HYGROMETRY FAN CTA P03 (LEVEL 20M) | MA |  | RES | 1 | C |  | K | %Hr | 1 | 0 | 100 |  |  | 40 | 60 |  |  | C | [13 empty] | POL | 6000 | VZC6401Z3 | HVAC14 | HVAC |  | 7 |  |  | 3053 | NA | 14200 | NA | 16416 | 3822 | 0 | EL6021_M181 |  | INT
VVV7013M1 | VC 1 SALLE 13 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1408 | NA | [7 empty] | INT
VTR6401 | VEGA GANTRY PLC : AMBIENT TEMPERATURE FAN CTA P01 ROOMS ANNEXES (LEVEL 40M) | MA |  | RES | 1 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | POL | 6000 | VZC6401Z9 | HVAC13;HVAC14;HVAC18 | HVAC |  | 7 |  |  | 3058 | NA | 14205 | NA | 16416 | 3832 | 0 | EL6021_M181 |  | INT
VHR6401 | VEGA GANTRY PLC : AMBIENT HYGROMETRY FAN CTA P01 ROOMS ANNEXES (LEVEL 40M) | MA |  | RES | 1 | C |  | K | %Hr | 1 | 0 | 100 |  |  | 40 | 60 |  |  | C | [13 empty] | POL | 6000 | VZC6401Z10 | HVAC14 | HVAC |  | 7 |  |  | 3059 | NA | 14206 | NA | 16416 | 3834 | 0 | EL6021_M181 |  | INT
ZCM6836F1 | SWITCH 1 BUNKER - ETAT FO PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
VCN7005M2 | AC 2 SALLE 05 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1411 | NA | [7 empty] | INT
ZCM6836F2 | SWITCH 1 BUNKER - ETAT FO PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P1 | SWITCH 1 BUNKER - ETAT PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
VVV7010M2 | VC 2 SALLE 10 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1413 | NA | [7 empty] | INT
ZCM6836P2 | SWITCH 1 BUNKER - ETAT PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P3 | SWITCH 1 BUNKER - ETAT PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P4 | SWITCH 1 BUNKER - ETAT PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
VVV7013M2 | VC 2 SALLE 13 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1416 | NA | [7 empty] | INT
ZCM6836P5 | SWITCH 1 BUNKER - ETAT PORT 5 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
VTR7006V1 | VC 1 SALLE 06 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1421 | NA | [7 empty] | INT
VVV7006M1 | VC 1 SALLE 06 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1422 | NA | [7 empty] | INT
VTR7008V1 | VC 1 SALLE 08 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1423 | NA | [7 empty] | INT
VVV7008M1 | VC 1 SALLE 08 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1424 | NA | [7 empty] | INT
VTR7007V1 | VC 1 SALLE 07 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1425 | NA | [7 empty] | INT
VVV7007M1 | VC 1 SALLE 07 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1426 | NA | [7 empty] | INT
VTR7007V2 | VC 2 SALLE 07 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1427 | NA | [7 empty] | INT
VVV7007M2 | VC 2 SALLE 07 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1428 | NA | [7 empty] | INT
VTR7007V3 | VC 3 SALLE 07 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1429 | NA | [7 empty] | INT
VVV7007M3 | VC 3 SALLE 07 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1430 | NA | [7 empty] | INT
VTR7007V4 | VC 4 SALLE 07 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1431 | NA | [7 empty] | INT
VVV7007M4 | VC 4 SALLE 07 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1432 | NA | [7 empty] | INT
VTR7007V5 | VC 5 SALLE 07 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1433 | NA | [7 empty] | INT
VVV7007M5 | VC 5 SALLE 07 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1434 | NA | [7 empty] | INT
VTR7007V6 | VC 6 SALLE 07 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1435 | NA | [7 empty] | INT
VVV7007M6 | VC 6 SALLE 07 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC21 | HVAC (C) | LGRNG | 9 |  |  | 1436 | NA | [7 empty] | INT
VTR7011V1 | VC 1 SALLE 11 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1437 | NA | [7 empty] | INT
VVV7011M1 | VC 1 SALLE 11 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1438 | NA | [7 empty] | INT
VTR7012V1 | VC 1 SALLE 12 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1439 | NA | [7 empty] | INT
VVV7012M1 | VC 1 SALLE 12 LAGRANGE STATUS | MA | N | RES | 2 | C | [26 empty] | MTCP | 2000 |  | HVAC20 | HVAC (C) | LGRNG | 9 |  |  | 1440 | NA | [7 empty] | INT
EIR7320I1 | TGBT Lagrange 184-13-20 Phase current I1 (CAT I et CAT II) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1525 | NA | [7 empty] | U32
EIR7320I2 | TGBT Lagrange 184-13-20 Phase current I2 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1527 | NA | [7 empty] | U32
EIR7320I3 | TGBT Lagrange 184-13-20 Phase current I3 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1529 | NA | [7 empty] | U32
EIR7320IN | TGBT Lagrange 184-13-20 Neutral Current (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1531 | NA | [7 empty] | U32
EUR732012 | TGBT Lagrange 184-13-20 line to line voltage 1 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1533 | NA | [7 empty] | U32
EUR732023 | TGBT Lagrange 184-13-20 line to line voltage 2 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1535 | NA | [7 empty] | U32
EUR732031 | TGBT Lagrange 184-13-20 line to line voltage 3 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1537 | NA | [7 empty] | U32
EUR7320V1 | TGBT Lagrange 184-13-20Phase voltage 1 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1539 | NA | [7 empty] | U32
EUR7320V2 | TGBT Lagrange 184-13-20 Phase voltage 2 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1541 | NA | [7 empty] | U32
EUR7320V3 | TGBT Lagrange 184-13-20 Phase voltage 3 (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1543 | NA | [7 empty] | U32
EWR7320PF | TGBT Lagrange 184-13-20 Power factor (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1545 | NA | [7 empty] | U32
EFR7320 | TGBT Lagrange 184-13-20 Frequency (CAT I ET CAT II) | MA | N | RES | 2 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1547 | NA | [7 empty] | U32
EIR7530I1 | TD 184-05-30 Phase current I1 (CAT IIIA) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1549 | NA | [7 empty] | U32
EIR7530I2 | TD 184-05-30 Phase current I2 (CAT IIIA) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1551 | NA | [7 empty] | U32
EIR7530I3 | TD 184-05-30 Phase current I3 (CAT IIIA) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1553 | NA | [7 empty] | U32
EIR7530IN | TD 184-05-30 Neutral Current | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1555 | NA | [7 empty] | U32
EUR753012 | TD 184-05-30 line to line voltage 1 (CAT IIIA) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1557 | NA | [7 empty] | U32
EUR753023 | TD 184-05-30 line to line voltage 2 (CAT IIIA) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1559 | NA | [7 empty] | U32
EUR753031 | TD 184-05-30 line to line voltage 3 (CAT IIIA) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1561 | NA | [7 empty] | U32
EUR7530V1 | TD 184-05-30 Phase voltage 1 (CAT IIIA) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1563 | NA | [7 empty] | U32
EUR7530V2 | TD 184-05-30 Phase voltage 2 (CAT IIIA) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1565 | NA | [7 empty] | U32
EUR7530V3 | TD 184-05-30 Phase voltage 2 (CAT IIIA) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1567 | NA | [7 empty] | U32
EWR7530PF | TD 184-05-30 Power factor (CAT IIIA) | MA | N | RES | 2 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1569 | NA | [7 empty] | U32
EFR7530 | TD 184-05-30 Frequency (CAT IIIA) | MA | N | RES | 2 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1571 | NA | [7 empty] | U32
EIR7531I1 | TD 184-05-31 Phase current I1 (CAT IIIB) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1573 | NA | [7 empty] | U32
EIR7531I2 | TD 184-05-31 Phase current I2 (CAT IIIB) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1575 | NA | [7 empty] | U32
EIR7531I3 | TD 184-05-31 Phase current I3 (CAT IIIB) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1577 | NA | [7 empty] | U32
EIR7531IN | TD 184-05-31 Neutral Current | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1579 | NA | [7 empty] | U32
EUR753112 | TD 184-05-31 line to line voltage 1 (CAT IIIB) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1581 | NA | [7 empty] | U32
EUR753123 | TD 184-05-31 line to line voltage 2 (CAT IIIB) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1583 | NA | [7 empty] | U32
EUR753131 | TD 184-05-31 line to line voltage 3 (CAT IIIB) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1585 | NA | [7 empty] | U32
EUR7531V1 | TD 184-05-31 Phase voltage 1 (CAT IIIB) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1587 | NA | [7 empty] | U32
EUR7531V2 | TD 184-05-31 Phase voltage 2 (CAT IIIB) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1589 | NA | [7 empty] | U32
EUR7531V3 | TD 184-05-31 Phase voltage 2 (CAT IIIB) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1591 | NA | [7 empty] | U32
EWR7531PF | TD 184-05-31 Power factor (CAT IIIB) | MA | N | RES | 2 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1593 | NA | [7 empty] | U32
EFR7531 | TD 184-05-31 Frequency (CAT IIIB) | MA | N | RES | 2 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1595 | NA | [7 empty] | U32
EIR7532I1 | TD Clima CAT II-III 184-13-32 Phase current I1 (CAT II-III) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1597 | NA | [7 empty] | U32
EIR7532I2 | TD Clima CAT II-III 184-13-32 Phase current I2 (CAT II-III) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1599 | NA | [7 empty] | U32
EIR7532I3 | TD Clima CAT II-III 184-13-32 Phase current I3 (CAT II-III) | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1601 | NA | [7 empty] | U32
EIR7532IN | TD Clima CAT II-III 184-13-32 Neutral Current | MA | N | RES | 2 | E |  |  | A | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1603 | NA | [7 empty] | U32
EUR753212 | TD Clima CAT II-III 184-13-32 line to line voltage 1 (CAT II-III) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1605 | NA | [7 empty] | U32
EUR753223 | TD Clima CAT II-III 184-13-32 line to line voltage 2 (CAT II-III) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1607 | NA | [7 empty] | U32
EUR753231 | TD Clima CAT II-III 184-13-32 line to line voltage 3 (CAT II-III) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1609 | NA | [7 empty] | U32
EUR7532V1 | TD Clima CAT II-III 184-13-32 Phase voltage 1 (CAT II-III) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1611 | NA | [7 empty] | U32
EUR7532V2 | TD Clima CAT II-III 184-13-32 Phase voltage 2 (CAT II-III) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1613 | NA | [7 empty] | U32
EUR7532V3 | TD Clima CAT II-III 184-13-32 Phase voltage 2 (CAT II-III) | MA | N | RES | 2 | E |  |  | V | 1 | -2150000000 | 2150000000 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1615 | NA | [7 empty] | U32
EWR7532PF | TD Clima CAT II-III 184-13-32 Power factor (CAT II-III) | MA | N | RES | 2 | E |  |  | NA | 1 | -2150000000 | 2150000000 | [20 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1617 | NA | [7 empty] | U32
EFR7532 | TD Clima CAT II-III 184-13-32 Frequency (CAT II-III) | MA | N | RES | 2 | E |  |  | Hz | 1 | -2150000000 | 2150000000 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | TD 184-13-32 CAT II-III (E73 popup) | Energy TD (E) | LGRNG | 9 |  |  | 1619 | NA | [7 empty] | U32
EIR7071I1 | Lagrange UPS A Output phase current I1 | MA | N | RES | 2 | E |  |  | A | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1669 | NA | [7 empty] | UINT
EIR7071I2 | Lagrange UPS A Output phase current I2 | MA | N | RES | 2 | E |  |  | A | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1670 | NA | [7 empty] | UINT
EIR7071I3 | Lagrange UPS A Output phase current I3 | MA | N | RES | 2 | E |  |  | A | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1671 | NA | [7 empty] | UINT
EUR7071V1 | Lagrange UPS A Output phase voltage V1 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1672 | NA | [7 empty] | UINT
EUR7071V2 | Lagrange UPS A Output phase voltage V2 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1673 | NA | [7 empty] | UINT
EUR7071V3 | Lagrange UPS A Output phase voltage V3 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1674 | NA | [7 empty] | UINT
EUR707112 | Lagrange UPS A Output line to line voltage U12 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1675 | NA | [7 empty] | UINT
EUR707123 | Lagrange UPS A Output line to line voltage U23 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1676 | NA | [7 empty] | UINT
EUR707131 | Lagrange UPS A Output line to line voltage U31 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1677 | NA | [7 empty] | UINT
EUR7071UBP | Lagrange UPS A Battery voltage UB+ | MA | N | RES | 2 | E |  |  | V | 0.1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1678 | NA | [7 empty] | UINT
EUR7071UBM | Lagrange UPS A Battery voltage UB- | MA | N | RES | 2 | E |  |  | V | 0.1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1679 | NA | [7 empty] | UINT
ZCM6836P6 | SWITCH 1 BUNKER - ETAT PORT 6 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
EDR7071 | Lagrange UPS A Battery remaining runtime | MA | N | RES | 2 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1681 | NA | [7 empty] | UINT
ETR7071 | Lagrange UPS A Battery temperature | MA | N | RES | 2 | E |  |  | °C | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1682 | NA | [7 empty] | UINT
ENR7071 | Lagrange UPS A Battery remaining capacity | MA | N | RES | 2 | E |  |  | % | 1 | 0 | 65535 | [20 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1683 | NA | [7 empty] | UINT
EWR7071S | Lagrange UPS A Nominal output apparent power UPS | MA | N | RES | 2 | E |  |  | kVA | 0.1 | 0 | 65535 | [20 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1684 | NA | [7 empty] | UINT
EIR7072I1 | Lagrange UPS B Output phase current I1 | MA | N | RES | 2 | E |  |  | A | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1685 | NA | [7 empty] | UINT
EIR7072I2 | Lagrange UPS B Output phase current I2 | MA | N | RES | 2 | E |  |  | A | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1686 | NA | [7 empty] | UINT
EIR7072I3 | Lagrange UPS B Output phase current I3 | MA | N | RES | 2 | E |  |  | A | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1687 | NA | [7 empty] | UINT
EUR7072V1 | Lagrange UPS B Output phase voltage V1 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1688 | NA | [7 empty] | UINT
EUR7072V2 | Lagrange UPS B Output phase voltage V2 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1689 | NA | [7 empty] | UINT
EUR7072V3 | Lagrange UPS B Output phase voltage V3 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1690 | NA | [7 empty] | UINT
EUR707212 | Lagrange UPS B Output line to line voltage U12 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1691 | NA | [7 empty] | UINT
EUR707223 | Lagrange UPS B Output line to line voltage U23 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1692 | NA | [7 empty] | UINT
EUR707231 | Lagrange UPS B Output line to line voltage U31 | MA | N | RES | 2 | E |  |  | V | 1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1693 | NA | [7 empty] | UINT
EUR7072UBP | Lagrange UPS B Battery voltage UB+ | MA | N | RES | 2 | E |  |  | V | 0.1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1694 | NA | [7 empty] | UINT
EUR7072UBM | Lagrange UPS B Battery voltage UB- | MA | N | RES | 2 | E |  |  | V | 0.1 | 0 | 65535 | [13 empty] | 3 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1695 | NA | [7 empty] | UINT
ZCM6836P7 | SWITCH 1 BUNKER - ETAT PORT 7 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
EDR7072 | Lagrange UPS B Battery remaining runtime | MA | N | RES | 2 | E |  |  | min | 1 | 0 | 65535 | [20 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1697 | NA | [7 empty] | UINT
ETR7072 | Lagrange UPS B Battery temperature | MA | N | RES | 2 | E |  |  | °C | 0.1 | 0 | 65535 | [13 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1698 | NA | [7 empty] | UINT
ENR7072 | Lagrange UPS B Battery remaining capacity | MA | N | RES | 2 | E |  |  | % | 1 | 0 | 65535 | [20 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1699 | NA | [7 empty] | UINT
EWR7072S | Lagrange UPS B Nominal output apparent power UPS | MA | N | RES | 2 | E |  |  | kVA | 0.1 | 0 | 65535 | [20 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1700 | NA | [7 empty] | UINT
SOR7001 | LAGRANGE DETG CENTRAL CHANNEL1 OXYGEN LEVEL | MA | N | RES | 2 | S;F;D |  |  |  | 1 | [22 empty] | MTCP | 500 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1049-1050 | NA | [7 empty] | FLOAT
SOR7002 | LAGRANGE DETG CENTRAL CHANNEL2 OXYGEN LEVEL | MA | N | RES | 2 | S;F;D |  |  |  | 1 | [22 empty] | MTCP | 500 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1053-1054 | NA | [7 empty] | FLOAT
SOR7003 | LAGRANGE DETG CENTRAL CHANNEL3 OXYGEN LEVEL | MA | N | RES | 2 | S;F;D |  |  |  | 1 | [22 empty] | MTCP | 500 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1055-1056 | NA | [7 empty] | FLOAT
SOR7004 | LAGRANGE DETG CENTRAL CHANNEL4 OXYGEN LEVEL | MA | N | RES | 2 | S;F;D |  |  |  | 1 | [22 empty] | MTCP | 500 |  | DG71 (DETG Lagrange Group) | Detection Gaz (DG) | LGRNG | 9 |  |  | 1059-1060 | NA | [7 empty] | FLOAT
EWR7320R | TGBT Lagrange 184-13-20 Total Real Power R (CAT I ET CAT II) | MA | N | CAL | 2 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR7320V1*EIR7320I1 + EUR7320V2*EIR7320I2 + EUR7320I3*EIR7320I3)*EUR7320PF |  |  | MTCP |  |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7320Q | TGBT Lagrange 184-13-20Total Reactive Power Q (CAT I ET CAT II) | MA | N | CAL | 2 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR7320V1*EIR7320I1 + EUR7320V2*EIR7320I2 + EUR7320I3*EIR7320I3)*sin[arcos(EUR7320PF)] |  |  | MTCP |  |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7320S | TGBT Lagrange 184-13-20 Total Apparent Power (CAT I ET CAT II) | MA | N | CAL | 2 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR7320V1*EIR7320I1 + EUR7320V2*EIR7320I2 + EUR7320I3*EIR7320I3) |  |  | MTCP |  |  | TGBT 184-13-20 CAT. I II (E74 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7530R | TD 184-05-30 Total Real Power R (CAT IIIA) | MA | N | CAL | 2 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR7530V1*EIR7530I1 + EUR7530V2*EIR7530I2 + EUR7530I3*EIR7530I3)*EUR7530PF |  |  | MTCP |  |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7530Q | TD 184-05-30 Total Reactive Power Q (CAT IIIA) | MA | N | CAL | 2 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR7530V1*EIR7530I1 + EUR7530V2*EIR7530I2 + EUR7530I3*EIR7530I3)*sin[arcos(EUR7530PF)] |  |  | MTCP |  |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7530S | TD 184-05-30 Total Apparent Power Q (CAT IIIA) | MA | N | CAL | 2 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR7530V1*EIR7530I1 + EUR7530V2*EIR7530I2 + EUR7530I3*EIR7530I3) |  |  | MTCP |  |  | TD 184-05-30 CAT. IIIA (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7531R | TD 184-05-31 Total Real Power R (CAT IIIB) | MA | N | CAL | 2 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR7531V1*EIR7531I1 + EUR7531V2*EIR7531I2 + EUR7531I3*EIR7531I3)*EUR7531PF |  |  | MTCP |  |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7531Q | TD 184-05-31 Total Reactive Power Q (CAT IIIB) | MA | N | CAL | 2 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR7531V1*EIR7531I1 + EUR7531V2*EIR7531I2 + EUR7531I3*EIR7531I3)*sin[arcos(EUR7531PF)] |  |  | MTCP |  |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7531S | TD 184-05-31 Total Apparent Power Q (CAT IIIB) | MA | N | CAL | 2 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR7531V1*EIR7531I1 + EUR7531V2*EIR7531I2 + EUR7531I3*EIR7531I3) |  |  | MTCP |  |  | TD 184-05-31 CAT. IIIB (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7532R | TD Clima CAT I-II 184-13-32 Total Real Power R (CAT I-II) | MA | N | CAL | 2 | E |  |  | kW | 1000 | [18 empty] | FORM | (EUR7532V1*EIR7532I1 + EUR7532V2*EIR7532I2 + EUR7532I3*EIR7532I3)*EUR7532PF |  |  | MTCP |  |  | TD 184-13-32 CAT II-III (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7532Q | TD Clima CAT I-II 184-13-32 Total Reactive Power Q (CAT I-II) | MA | N | CAL | 2 | E |  |  | kVAR | 1000 | [18 empty] | FORM | (EUR7532V1*EIR7532I1 + EUR7532V2*EIR7532I2 + EUR7532I3*EIR7532I3)*sin[arcos(EUR7532PF)] |  |  | MTCP |  |  | TD 184-13-32 CAT II-III (E73 popup) | Energy Lagrange (E) | LGRNG | 9
EWR7532S | TD Clima CAT I-II 184-13-32 Total Apparent Power Q (CAT I-II) | MA | N | CAL | 2 | E |  |  | kVA | 1000 | [18 empty] | FORM | (EUR7532V1*EIR7532I1 + EUR7532V2*EIR7532I2 + EUR7532I3*EIR7532I3) |  |  | MTCP |  |  | TD 184-13-32 CAT II-III (E73 popup) | Energy Lagrange (E) | LGRNG | 9
SPARE | SPARE SER |  | N | RES | [39 empty] | 12374 | 12 | 16416 | 171 | 4 | SPARE |  | BITVAL
SPARE | SPARE SER |  | N | RES | [39 empty] | 12426 | 6 | 16416 | 274 | 6 | SPARE |  | SPARE | SPARE
SPARE | SPARE SER |  | N | RES | [39 empty] | 12426 | 8 | 16416 | 275 | 0 | SPARE |  | SPARE | SPARE
SPARE | SPARE SER |  | N | RES | [39 empty] | 12426 | 10 | 16416 | 275 | 2 | SPARE |  | SPARE | SPARE
SPARE | SPARE SER |  | N | RES | [39 empty] | 12426 | 12 | 16416 | 275 | 4 | SPARE |  | SPARE | SPARE
SPARE | SPARE SER |  | N | RES | [39 empty] | 12426 | 14 | 16416 | 275 | 6 | SPARE |  | SPARE | SPARE
SPARE | SPARE SER |  | N | RES | [34 empty] | 3 |  |  | 92 | 11 | 12595 | 6 | 16416 | 612 | 6 | EL6021_M177 |  | BITVAL
ZCM6836P8 | SWITCH 1 BUNKER - ETAT PORT 8 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
| VALIDITY | [42 empty] | 12838 | 1 | 16416 | 1098 | 1 | EL1809_M186 |  | BITVAL
ZCM6836P9 | SWITCH 1 BUNKER - ETAT PORT 9 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
| VALIDITY | [42 empty] | 12838 | 3 | 16416 | 1098 | 3 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12838 | 4 | 16416 | 1098 | 4 | EL1809_M186 | 3 | BITVAL
| VALIDITY | [42 empty] | 12838 | 5 | 16416 | 1098 | 5 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12838 | 6 | 16416 | 1098 | 6 | EL1809_M186 | 4 | BITVAL
| VALIDITY | [42 empty] | 12838 | 7 | 16416 | 1098 | 7 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12838 | 8 | 16416 | 1099 | 0 | EL1809_M186 | 5 | BITVAL
| VALIDITY | [42 empty] | 12838 | 9 | 16416 | 1099 | 1 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12838 | 10 | 16416 | 1099 | 2 | EL1809_M186 | 6 | BITVAL
| VALIDITY | [42 empty] | 12838 | 11 | 16416 | 1099 | 3 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12838 | 12 | 16416 | 1099 | 4 | EL1809_M186 | 7 | BITVAL
| VALIDITY | [42 empty] | 12838 | 13 | 16416 | 1099 | 5 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12838 | 14 | 16416 | 1099 | 6 | EL1809_M186 | 8 | BITVAL
| VALIDITY | [42 empty] | 12838 | 15 | 16416 | 1099 | 7 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 0 | 16416 | 1100 | 0 | EL1809_M186 | 9 | BITVAL
| VALIDITY | [42 empty] | 12839 | 1 | 16416 | 1100 | 1 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 2 | 16416 | 1100 | 2 | EL1809_M186 | 10 | BITVAL
| VALIDITY | [42 empty] | 12839 | 3 | 16416 | 1100 | 3 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 4 | 16416 | 1100 | 4 | EL1809_M186 | 11 | BITVAL
| VALIDITY | [42 empty] | 12839 | 5 | 16416 | 1100 | 5 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 6 | 16416 | 1100 | 6 | EL1809_M186 | 12 | BITVAL
| VALIDITY | [42 empty] | 12839 | 7 | 16416 | 1100 | 7 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 8 | 16416 | 1101 | 0 | EL1809_M186 | 13 | BITVAL
| VALIDITY | [42 empty] | 12839 | 9 | 16416 | 1101 | 1 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 10 | 16416 | 1101 | 2 | EL1809_M186 | 14 | BITVAL
| VALIDITY | [42 empty] | 12839 | 11 | 16416 | 1101 | 3 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 12 | 16416 | 1101 | 4 | EL1809_M186 | 15 | BITVAL
| VALIDITY | [42 empty] | 12839 | 13 | 16416 | 1101 | 5 | EL1809_M186 |  | BITVAL
SPARE | [43 empty] | 12839 | 14 | 16416 | 1101 | 6 | EL1809_M186 | 16 | BITVAL
| VALIDITY | [42 empty] | 12839 | 15 | 16416 | 1101 | 7 | EL1809_M186 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 1 | 16416 | 1102 | 1 | EL1134_M2 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 3 | 16416 | 1102 | 3 | EL1134_M2 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 5 | 16416 | 1102 | 5 | EL1134_M2 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 7 | 16416 | 1102 | 7 | EL1134_M2 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 9 | 16416 | 1103 | 1 | EL1134_M3 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 11 | 16416 | 1103 | 3 | EL1134_M3 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 13 | 16416 | 1103 | 5 | EL1134_M3 |  | BITVAL
| VALIDITY | [42 empty] | 12840 | 15 | 16416 | 1103 | 7 | EL1134_M3 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 1 | 16416 | 1104 | 1 | EL1134_M4 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 3 | 16416 | 1104 | 3 | EL1134_M4 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 5 | 16416 | 1104 | 5 | EL1134_M4 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 7 | 16416 | 1104 | 7 | EL1134_M4 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 9 | 16416 | 1105 | 1 | EL1134_M5 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 11 | 16416 | 1105 | 3 | EL1134_M5 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 13 | 16416 | 1105 | 5 | EL1134_M5 |  | BITVAL
| VALIDITY | [42 empty] | 12841 | 15 | 16416 | 1105 | 7 | EL1134_M5 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 1 | 16416 | 1106 | 1 | EL1134_M6 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 3 | 16416 | 1106 | 3 | EL1134_M6 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 5 | 16416 | 1106 | 5 | EL1134_M6 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 7 | 16416 | 1106 | 7 | EL1134_M6 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 9 | 16416 | 1107 | 1 | EL1134_M7 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 11 | 16416 | 1107 | 3 | EL1134_M7 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 13 | 16416 | 1107 | 5 | EL1134_M7 |  | BITVAL
| VALIDITY | [42 empty] | 12842 | 15 | 16416 | 1107 | 7 | EL1134_M7 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 1 | 16416 | 1108 | 1 | EL1134_M8 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 3 | 16416 | 1108 | 3 | EL1134_M8 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 5 | 16416 | 1108 | 5 | EL1134_M8 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 7 | 16416 | 1108 | 7 | EL1134_6 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 9 | 16416 | 1109 | 1 | EL1134_M9 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 11 | 16416 | 1109 | 3 | EL1134_M9 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 13 | 16416 | 1109 | 5 | EL1134_M9 |  | BITVAL
| VALIDITY | [42 empty] | 12843 | 15 | 16416 | 1109 | 7 | EL1134_M9 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 1 | 16416 | 1110 | 1 | EL1134_M10 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 3 | 16416 | 1110 | 3 | EL1134_M10 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 5 | 16416 | 1110 | 5 | EL1134_M10 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 7 | 16416 | 1110 | 7 | EL1134_M10 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 9 | 16416 | 1111 | 1 | EL1134_M11 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 11 | 16416 | 1111 | 3 | EL1134_M11 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 13 | 16416 | 1111 | 5 | EL1134_M11 |  | BITVAL
| VALIDITY | [42 empty] | 12844 | 15 | 16416 | 1111 | 7 | EL1134_M11 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 1 | 16416 | 1112 | 1 | EL1134_M13 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 3 | 16416 | 1112 | 3 | EL1134_M13 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 5 | 16416 | 1112 | 5 | EL1134_M13 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 7 | 16416 | 1112 | 7 | EL1134_M13 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 9 | 16416 | 1113 | 1 | EL1134_M14 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 11 | 16416 | 1113 | 3 | EL1134_M14 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 13 | 16416 | 1113 | 5 | EL1134_M14 |  | BITVAL
| VALIDITY | [42 empty] | 12845 | 15 | 16416 | 1113 | 7 | EL1134_M14 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 1 | 16416 | 1114 | 1 | EL1134_M15 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 3 | 16416 | 1114 | 3 | EL1134_M15 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 5 | 16416 | 1114 | 5 | EL1134_M15 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 7 | 16416 | 1114 | 7 | EL1134_M15 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 9 | 16416 | 1115 | 1 | EL1134_M16 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 11 | 16416 | 1115 | 3 | EL1134_M16 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 13 | 16416 | 1115 | 5 | EL1134_M16 |  | BITVAL
| VALIDITY | [42 empty] | 12846 | 15 | 16416 | 1115 | 7 | EL1134_M16 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 1 | 16416 | 1116 | 1 | EL1134_M17 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 3 | 16416 | 1116 | 3 | EL1134_M17 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 5 | 16416 | 1116 | 5 | EL1134_M17 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 7 | 16416 | 1116 | 7 | EL1134_14 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 9 | 16416 | 1117 | 1 | EL1134_M18 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 11 | 16416 | 1117 | 3 | EL1134_M18 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 13 | 16416 | 1117 | 5 | EL1134_M18 |  | BITVAL
| VALIDITY | [42 empty] | 12847 | 15 | 16416 | 1117 | 7 | EL1134_M18 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 1 | 16416 | 1118 | 1 | EL1134_M19 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 3 | 16416 | 1118 | 3 | EL1134_M19 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 5 | 16416 | 1118 | 5 | EL1134_M19 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 7 | 16416 | 1118 | 7 | EL1134_M19 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 9 | 16416 | 1119 | 1 | EL1134_M20 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 11 | 16416 | 1119 | 3 | EL1134_M20 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 13 | 16416 | 1119 | 5 | EL1134_M20 |  | BITVAL
| VALIDITY | [42 empty] | 12848 | 15 | 16416 | 1119 | 7 | EL1134_M20 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 1 | 16416 | 1120 | 1 | EL1134_M21 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 3 | 16416 | 1120 | 3 | EL1134_M21 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 5 | 16416 | 1120 | 5 | EL1134_M21 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 7 | 16416 | 1120 | 7 | EL1134_M21 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 9 | 16416 | 1121 | 1 | EL1134_M22 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 11 | 16416 | 1121 | 3 | EL1134_M22 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 13 | 16416 | 1121 | 5 | EL1134_M22 |  | BITVAL
| VALIDITY | [42 empty] | 12849 | 15 | 16416 | 1121 | 7 | EL1134_M22 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 1 | 16416 | 1122 | 1 | EL1134_M24 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 3 | 16416 | 1122 | 3 | EL1134_M24 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 5 | 16416 | 1122 | 5 | EL1134_M24 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 7 | 16416 | 1122 | 7 | EL1134_M24 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 9 | 16416 | 1123 | 1 | EL1134_M25 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 11 | 16416 | 1123 | 3 | EL1134_M25 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 13 | 16416 | 1123 | 5 | EL1134_M25 |  | BITVAL
| VALIDITY | [42 empty] | 12850 | 15 | 16416 | 1123 | 7 | EL1134_M25 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 1 | 16416 | 1124 | 1 | EL1134_M26 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 3 | 16416 | 1124 | 3 | EL1134_M26 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 5 | 16416 | 1124 | 5 | EL1134_M26 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 7 | 16416 | 1124 | 7 | EL1134_M26 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 9 | 16416 | 1125 | 1 | EL1134_M27 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 11 | 16416 | 1125 | 3 | EL1134_M27 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 13 | 16416 | 1125 | 5 | EL1134_M27 |  | BITVAL
| VALIDITY | [42 empty] | 12851 | 15 | 16416 | 1125 | 7 | EL1134_M27 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 1 | 16416 | 1126 | 1 | EL1134_M28 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 3 | 16416 | 1126 | 3 | EL1134_M28 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 5 | 16416 | 1126 | 5 | EL1134_M28 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 7 | 16416 | 1126 | 7 | EL1134_M28 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 9 | 16416 | 1127 | 1 | EL1134_M29 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 11 | 16416 | 1127 | 3 | EL1134_M29 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 13 | 16416 | 1127 | 5 | EL1134_M29 |  | BITVAL
| VALIDITY | [42 empty] | 12852 | 15 | 16416 | 1127 | 7 | EL1134_M29 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 1 | 16416 | 1128 | 1 | EL1134_M30 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 3 | 16416 | 1128 | 3 | EL1134_M30 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 5 | 16416 | 1128 | 5 | EL1134_M30 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 7 | 16416 | 1128 | 7 | EL1134_M30 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 9 | 16416 | 1129 | 1 | EL1134_M31 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 11 | 16416 | 1129 | 3 | EL1134_M31 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 13 | 16416 | 1129 | 5 | EL1134_M31 |  | BITVAL
| VALIDITY | [42 empty] | 12853 | 15 | 16416 | 1129 | 7 | EL1134_M31 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 1 | 16416 | 1130 | 1 | EL1134_M32 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 3 | 16416 | 1130 | 3 | EL1134_M32 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 5 | 16416 | 1130 | 5 | EL1134_M32 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 7 | 16416 | 1130 | 7 | EL1134_M32 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 9 | 16416 | 1131 | 1 | EL1134_M33 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 11 | 16416 | 1131 | 3 | EL1134_M33 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 13 | 16416 | 1131 | 5 | EL1134_M33 |  | BITVAL
| VALIDITY | [42 empty] | 12854 | 15 | 16416 | 1131 | 7 | EL1134_M33 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 1 | 16416 | 1132 | 1 | EL1134_M35 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 3 | 16416 | 1132 | 3 | EL1134_M35 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 5 | 16416 | 1132 | 5 | EL1134_M35 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 7 | 16416 | 1132 | 7 | EL1134_M35 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 9 | 16416 | 1133 | 1 | EL1134_M36 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 11 | 16416 | 1133 | 3 | EL1134_M36 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 13 | 16416 | 1133 | 5 | EL1134_M36 |  | BITVAL
| VALIDITY | [42 empty] | 12855 | 15 | 16416 | 1133 | 7 | EL1134_M36 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 1 | 16416 | 1134 | 1 | EL1134_M37 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 3 | 16416 | 1134 | 3 | EL1134_M37 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 5 | 16416 | 1134 | 5 | EL1134_M37 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 7 | 16416 | 1134 | 7 | EL1134_M37 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 9 | 16416 | 1135 | 1 | EL1134_M38 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 11 | 16416 | 1135 | 3 | EL1134_M38 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 13 | 16416 | 1135 | 5 | EL1134_M38 |  | BITVAL
| VALIDITY | [42 empty] | 12856 | 15 | 16416 | 1135 | 7 | EL1134_M38 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 1 | 16416 | 1136 | 1 | EL1134_M39 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 3 | 16416 | 1136 | 3 | EL1134_M39 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 5 | 16416 | 1136 | 5 | EL1134_M39 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 7 | 16416 | 1136 | 7 | EL1134_M39 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 9 | 16416 | 1137 | 1 | EL1134_M40 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 11 | 16416 | 1137 | 3 | EL1134_M40 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 13 | 16416 | 1137 | 5 | EL1134_M40 |  | BITVAL
| VALIDITY | [42 empty] | 12857 | 15 | 16416 | 1137 | 7 | EL1134_M40 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 1 | 16416 | 1138 | 1 | EL1134_M41 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 3 | 16416 | 1138 | 3 | EL1134_M41 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 5 | 16416 | 1138 | 5 | EL1134_M41 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 7 | 16416 | 1138 | 7 | EL1134_M41 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 9 | 16416 | 1139 | 1 | EL1134_M42 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 11 | 16416 | 1139 | 3 | EL1134_M42 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 13 | 16416 | 1139 | 5 | EL1134_M42 |  | BITVAL
| VALIDITY | [42 empty] | 12858 | 15 | 16416 | 1139 | 7 | EL1134_M42 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 1 | 16416 | 1140 | 1 | EL1134_M43 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 3 | 16416 | 1140 | 3 | EL1134_M43 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 5 | 16416 | 1140 | 5 | EL1134_M43 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 7 | 16416 | 1140 | 7 | EL1134_M43 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 9 | 16416 | 1141 | 1 | EL1134_M44 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 11 | 16416 | 1141 | 3 | EL1134_M44 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 13 | 16416 | 1141 | 5 | EL1134_M44 |  | BITVAL
| VALIDITY | [42 empty] | 12859 | 15 | 16416 | 1141 | 7 | EL1134_M44 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 1 | 16416 | 1142 | 1 | EL1134_M46 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 3 | 16416 | 1142 | 3 | EL1134_M46 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 5 | 16416 | 1142 | 5 | EL1134_M46 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 7 | 16416 | 1142 | 7 | EL1134_M46 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 9 | 16416 | 1143 | 1 | EL1134_M47 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 11 | 16416 | 1143 | 3 | EL1134_M47 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 13 | 16416 | 1143 | 5 | EL1134_M47 |  | BITVAL
| VALIDITY | [42 empty] | 12860 | 15 | 16416 | 1143 | 7 | EL1134_M47 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 1 | 16416 | 1144 | 1 | EL1134_M48 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 3 | 16416 | 1144 | 3 | EL1134_M48 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 5 | 16416 | 1144 | 5 | EL1134_M48 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 7 | 16416 | 1144 | 7 | EL1134_M48 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 9 | 16416 | 1145 | 1 | EL1134_M49 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 11 | 16416 | 1145 | 3 | EL1134_M49 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 13 | 16416 | 1145 | 5 | EL1134_M49 |  | BITVAL
| VALIDITY | [42 empty] | 12861 | 15 | 16416 | 1145 | 7 | EL1134_M49 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 1 | 16416 | 1146 | 1 | EL1134_M50 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 3 | 16416 | 1146 | 3 | EL1134_M50 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 5 | 16416 | 1146 | 5 | EL1134_M50 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 7 | 16416 | 1146 | 7 | EL1134_M50 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 9 | 16416 | 1147 | 1 | EL1134_M51 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 11 | 16416 | 1147 | 3 | EL1134_M51 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 13 | 16416 | 1147 | 5 | EL1134_M51 |  | BITVAL
| VALIDITY | [42 empty] | 12862 | 15 | 16416 | 1147 | 7 | EL1134_M51 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 1 | 16416 | 1148 | 1 | EL1134_M52 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 3 | 16416 | 1148 | 3 | EL1134_M52 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 5 | 16416 | 1148 | 5 | EL1134_M52 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 7 | 16416 | 1148 | 7 | EL1134_M52 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 9 | 16416 | 1149 | 1 | EL1134_M53 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 11 | 16416 | 1149 | 3 | EL1134_M53 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 13 | 16416 | 1149 | 5 | EL1134_M53 |  | BITVAL
| VALIDITY | [42 empty] | 12863 | 15 | 16416 | 1149 | 7 | EL1134_M53 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 1 | 16416 | 1150 | 1 | EL1134_M54 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 3 | 16416 | 1150 | 3 | EL1134_M54 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 5 | 16416 | 1150 | 5 | EL1134_M54 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 7 | 16416 | 1150 | 7 | EL1134_M54 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 9 | 16416 | 1151 | 1 | EL1134_M55 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 11 | 16416 | 1151 | 3 | EL1134_M55 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 13 | 16416 | 1151 | 5 | EL1134_M55 |  | BITVAL
| VALIDITY | [42 empty] | 12864 | 15 | 16416 | 1151 | 7 | EL1134_M55 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 1 | 16416 | 1152 | 1 | EL1134_M57 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 3 | 16416 | 1152 | 3 | EL1134_M57 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 5 | 16416 | 1152 | 5 | EL1134_M57 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 7 | 16416 | 1152 | 7 | EL1134_M57 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 9 | 16416 | 1153 | 1 | EL1134_M58 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 11 | 16416 | 1153 | 3 | EL1134_M58 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 13 | 16416 | 1153 | 5 | EL1134_M58 |  | BITVAL
| VALIDITY | [42 empty] | 12865 | 15 | 16416 | 1153 | 7 | EL1134_M58 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 1 | 16416 | 1154 | 1 | EL1134_M59 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 3 | 16416 | 1154 | 3 | EL1134_M59 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 5 | 16416 | 1154 | 5 | EL1134_M59 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 7 | 16416 | 1154 | 7 | EL1134_M59 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 9 | 16416 | 1155 | 1 | EL1134_M60 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 11 | 16416 | 1155 | 3 | EL1134_M60 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 13 | 16416 | 1155 | 5 | EL1134_M60 |  | BITVAL
| VALIDITY | [42 empty] | 12866 | 15 | 16416 | 1155 | 7 | EL1134_M60 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 1 | 16416 | 1156 | 1 | EL1134_M61 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 3 | 16416 | 1156 | 3 | EL1134_M61 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 5 | 16416 | 1156 | 5 | EL1134_M61 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 7 | 16416 | 1156 | 7 | EL1134_M61 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 9 | 16416 | 1157 | 1 | EL1134_M62 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 11 | 16416 | 1157 | 3 | EL1134_M62 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 13 | 16416 | 1157 | 5 | EL1134_M62 |  | BITVAL
| VALIDITY | [42 empty] | 12867 | 15 | 16416 | 1157 | 7 | EL1134_M62 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 1 | 16416 | 1158 | 1 | EL1134_M63 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 3 | 16416 | 1158 | 3 | EL1134_M63 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 5 | 16416 | 1158 | 5 | EL1134_M63 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 7 | 16416 | 1158 | 7 | EL1134_M63 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 9 | 16416 | 1159 | 1 | EL1134_M64 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 11 | 16416 | 1159 | 3 | EL1134_M64 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 13 | 16416 | 1159 | 5 | EL1134_M64 |  | BITVAL
| VALIDITY | [42 empty] | 12868 | 15 | 16416 | 1159 | 7 | EL1134_M64 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 1 | 16416 | 1160 | 1 | EL1134_M65 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 3 | 16416 | 1160 | 3 | EL1134_M65 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 5 | 16416 | 1160 | 5 | EL1134_M65 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 7 | 16416 | 1160 | 7 | EL1134_M65 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 9 | 16416 | 1161 | 1 | EL1134_M66 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 11 | 16416 | 1161 | 3 | EL1134_M66 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 13 | 16416 | 1161 | 5 | EL1134_M66 |  | BITVAL
| VALIDITY | [42 empty] | 12869 | 15 | 16416 | 1161 | 7 | EL1134_M66 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 1 | 16416 | 1162 | 1 | EL1134_M68 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 3 | 16416 | 1162 | 3 | EL1134_M68 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 5 | 16416 | 1162 | 5 | EL1134_M68 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 7 | 16416 | 1162 | 7 | EL1134_M68 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 9 | 16416 | 1163 | 1 | EL1134_M69 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 11 | 16416 | 1163 | 3 | EL1134_M69 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 13 | 16416 | 1163 | 5 | EL1134_M69 |  | BITVAL
| VALIDITY | [42 empty] | 12870 | 15 | 16416 | 1163 | 7 | EL1134_M69 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 1 | 16416 | 1164 | 1 | EL1134_M70 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 3 | 16416 | 1164 | 3 | EL1134_M70 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 5 | 16416 | 1164 | 5 | EL1134_M70 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 7 | 16416 | 1164 | 7 | EL1134_M70 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 9 | 16416 | 1165 | 1 | EL1134_M71 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 11 | 16416 | 1165 | 3 | EL1134_M71 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 13 | 16416 | 1165 | 5 | EL1134_M71 |  | BITVAL
| VALIDITY | [42 empty] | 12871 | 15 | 16416 | 1165 | 7 | EL1134_M71 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 1 | 16416 | 1166 | 1 | EL1134_M72 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 3 | 16416 | 1166 | 3 | EL1134_M72 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 5 | 16416 | 1166 | 5 | EL1134_M72 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 7 | 16416 | 1166 | 7 | EL1134_M72 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 9 | 16416 | 1167 | 1 | EL1134_M73 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 11 | 16416 | 1167 | 3 | EL1134_M73 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 13 | 16416 | 1167 | 5 | EL1134_M73 |  | BITVAL
| VALIDITY | [42 empty] | 12872 | 15 | 16416 | 1167 | 7 | EL1134_M73 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 1 | 16416 | 1168 | 1 | EL1134_M74 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 3 | 16416 | 1168 | 3 | EL1134_M74 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 5 | 16416 | 1168 | 5 | EL1134_M74 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 7 | 16416 | 1168 | 7 | EL1134_M74 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 9 | 16416 | 1169 | 1 | EL1134_M75 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 11 | 16416 | 1169 | 3 | EL1134_M75 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 13 | 16416 | 1169 | 5 | EL1134_M75 |  | BITVAL
| VALIDITY | [42 empty] | 12873 | 15 | 16416 | 1169 | 7 | EL1134_M75 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 1 | 16416 | 1170 | 1 | EL1134_M76 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 3 | 16416 | 1170 | 3 | EL1134_M76 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 5 | 16416 | 1170 | 5 | EL1134_M76 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 7 | 16416 | 1170 | 7 | EL1134_M76 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 9 | 16416 | 1171 | 1 | EL1134_M77 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 11 | 16416 | 1171 | 3 | EL1134_M77 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 13 | 16416 | 1171 | 5 | EL1134_M77 |  | BITVAL
| VALIDITY | [42 empty] | 12874 | 15 | 16416 | 1171 | 7 | EL1134_M77 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 1 | 16416 | 1172 | 1 | EL1134_M79 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 3 | 16416 | 1172 | 3 | EL1134_M79 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 5 | 16416 | 1172 | 5 | EL1134_M79 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 7 | 16416 | 1172 | 7 | EL1134_M79 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 9 | 16416 | 1173 | 1 | EL1134_M80 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 11 | 16416 | 1173 | 3 | EL1134_M80 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 13 | 16416 | 1173 | 5 | EL1134_M80 |  | BITVAL
| VALIDITY | [42 empty] | 12875 | 15 | 16416 | 1173 | 7 | EL1134_M80 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 1 | 16416 | 1174 | 1 | EL1134_M81 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 3 | 16416 | 1174 | 3 | EL1134_M81 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 5 | 16416 | 1174 | 5 | EL1134_M81 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 7 | 16416 | 1174 | 7 | EL1134_M81 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 9 | 16416 | 1175 | 1 | EL1134_M82 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 11 | 16416 | 1175 | 3 | EL1134_M82 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 13 | 16416 | 1175 | 5 | EL1134_M82 |  | BITVAL
| VALIDITY | [42 empty] | 12876 | 15 | 16416 | 1175 | 7 | EL1134_M82 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 1 | 16416 | 1176 | 1 | EL1134_M83 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 3 | 16416 | 1176 | 3 | EL1134_M83 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 5 | 16416 | 1176 | 5 | EL1134_M83 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 7 | 16416 | 1176 | 7 | EL1134_M83 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 9 | 16416 | 1177 | 1 | EL1134_M84 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 11 | 16416 | 1177 | 3 | EL1134_M84 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 13 | 16416 | 1177 | 5 | EL1134_M84 |  | BITVAL
| VALIDITY | [42 empty] | 12877 | 15 | 16416 | 1177 | 7 | EL1134_M84 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 1 | 16416 | 1178 | 1 | EL1134_M85 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 3 | 16416 | 1178 | 3 | EL1134_M85 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 5 | 16416 | 1178 | 5 | EL1134_M85 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 7 | 16416 | 1178 | 7 | EL1134_M85 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 9 | 16416 | 1179 | 1 | EL1134_M86 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 11 | 16416 | 1179 | 3 | EL1134_M86 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 13 | 16416 | 1179 | 5 | EL1134_M86 |  | BITVAL
| VALIDITY | [42 empty] | 12878 | 15 | 16416 | 1179 | 7 | EL1134_M86 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 1 | 16416 | 1180 | 1 | EL1134_M87 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 3 | 16416 | 1180 | 3 | EL1134_M87 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 5 | 16416 | 1180 | 5 | EL1134_M87 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 7 | 16416 | 1180 | 7 | EL1134_M87 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 9 | 16416 | 1181 | 1 | EL1134_M88 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 11 | 16416 | 1181 | 3 | EL1134_M88 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 13 | 16416 | 1181 | 5 | EL1134_M88 |  | BITVAL
| VALIDITY | [42 empty] | 12879 | 15 | 16416 | 1181 | 7 | EL1134_M88 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 1 | 16416 | 1182 | 1 | EL1134_M90 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 3 | 16416 | 1182 | 3 | EL1134_M90 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 5 | 16416 | 1182 | 5 | EL1134_M90 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 7 | 16416 | 1182 | 7 | EL1134_M90 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 9 | 16416 | 1183 | 1 | EL1134_M91 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 11 | 16416 | 1183 | 3 | EL1134_M91 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 13 | 16416 | 1183 | 5 | EL1134_M91 |  | BITVAL
| VALIDITY | [42 empty] | 12880 | 15 | 16416 | 1183 | 7 | EL1134_M91 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 1 | 16416 | 1184 | 1 | EL1134_M92 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 3 | 16416 | 1184 | 3 | EL1134_M92 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 5 | 16416 | 1184 | 5 | EL1134_M92 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 7 | 16416 | 1184 | 7 | EL1134_M92 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 9 | 16416 | 1185 | 1 | EL1134_M93 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 11 | 16416 | 1185 | 3 | EL1134_M93 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 13 | 16416 | 1185 | 5 | EL1134_M93 |  | BITVAL
| VALIDITY | [42 empty] | 12881 | 15 | 16416 | 1185 | 7 | EL1134_M93 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 1 | 16416 | 1186 | 1 | EL1134_M94 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 3 | 16416 | 1186 | 3 | EL1134_M94 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 5 | 16416 | 1186 | 5 | EL1134_M94 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 7 | 16416 | 1186 | 7 | EL1134_M94 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 9 | 16416 | 1187 | 1 | EL1134_M95 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 11 | 16416 | 1187 | 3 | EL1134_M95 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 13 | 16416 | 1187 | 5 | EL1134_M95 |  | BITVAL
| VALIDITY | [42 empty] | 12882 | 15 | 16416 | 1187 | 7 | EL1134_M95 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 1 | 16416 | 1188 | 1 | EL1134_M96 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 3 | 16416 | 1188 | 3 | EL1134_M96 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 5 | 16416 | 1188 | 5 | EL1134_M96 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 7 | 16416 | 1188 | 7 | EL1134_M96 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 9 | 16416 | 1189 | 1 | EL1134_M97 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 11 | 16416 | 1189 | 3 | EL1134_M97 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 13 | 16416 | 1189 | 5 | EL1134_M97 |  | BITVAL
| VALIDITY | [42 empty] | 12883 | 15 | 16416 | 1189 | 7 | EL1134_M97 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 1 | 16416 | 1190 | 1 | EL1134_M98 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 3 | 16416 | 1190 | 3 | EL1134_M98 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 5 | 16416 | 1190 | 5 | EL1134_M98 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 7 | 16416 | 1190 | 7 | EL1134_M98 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 9 | 16416 | 1191 | 1 | EL1134_M99 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 11 | 16416 | 1191 | 3 | EL1134_M99 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 13 | 16416 | 1191 | 5 | EL1134_M99 |  | BITVAL
| VALIDITY | [42 empty] | 12884 | 15 | 16416 | 1191 | 7 | EL1134_M99 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 1 | 16416 | 1192 | 1 | EL1134_M101 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 3 | 16416 | 1192 | 3 | EL1134_M101 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 5 | 16416 | 1192 | 5 | EL1134_M101 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 7 | 16416 | 1192 | 7 | EL1134_M101 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 9 | 16416 | 1193 | 1 | EL1134_M102 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 11 | 16416 | 1193 | 3 | EL1134_M102 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 13 | 16416 | 1193 | 5 | EL1134_M102 |  | BITVAL
| VALIDITY | [42 empty] | 12885 | 15 | 16416 | 1193 | 7 | EL1134_M102 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 1 | 16416 | 1194 | 1 | EL1134_M103 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 3 | 16416 | 1194 | 3 | EL1134_M103 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 5 | 16416 | 1194 | 5 | EL1134_M103 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 7 | 16416 | 1194 | 7 | EL1134_M103 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 9 | 16416 | 1195 | 1 | EL1134_M104 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 11 | 16416 | 1195 | 3 | EL1134_M104 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 13 | 16416 | 1195 | 5 | EL1134_M104 |  | BITVAL
| VALIDITY | [42 empty] | 12886 | 15 | 16416 | 1195 | 7 | EL1134_M104 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 1 | 16416 | 1196 | 1 | EL1134_M105 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 3 | 16416 | 1196 | 3 | EL1134_M105 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 5 | 16416 | 1196 | 5 | EL1134_M105 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 7 | 16416 | 1196 | 7 | EL1134_M105 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 9 | 16416 | 1197 | 1 | EL1134_M106 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 11 | 16416 | 1197 | 3 | EL1134_M106 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 13 | 16416 | 1197 | 5 | EL1134_M106 |  | BITVAL
| VALIDITY | [42 empty] | 12887 | 15 | 16416 | 1197 | 7 | EL1134_M106 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 1 | 16416 | 1198 | 1 | EL1134_M107 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 3 | 16416 | 1198 | 3 | EL1134_M107 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 5 | 16416 | 1198 | 5 | EL1134_M107 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 7 | 16416 | 1198 | 7 | EL1134_M107 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 9 | 16416 | 1199 | 1 | EL1134_M108 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 11 | 16416 | 1199 | 3 | EL1134_M108 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 13 | 16416 | 1199 | 5 | EL1134_M108 |  | BITVAL
| VALIDITY | [42 empty] | 12888 | 15 | 16416 | 1199 | 7 | EL1134_M108 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 1 | 16416 | 1200 | 1 | EL1134_M109 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 3 | 16416 | 1200 | 3 | EL1134_M109 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 5 | 16416 | 1200 | 5 | EL1134_M109 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 7 | 16416 | 1200 | 7 | EL1134_M109 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 9 | 16416 | 1201 | 1 | EL1134_M110 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 11 | 16416 | 1201 | 3 | EL1134_M110 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 13 | 16416 | 1201 | 5 | EL1134_M110 |  | BITVAL
| VALIDITY | [42 empty] | 12889 | 15 | 16416 | 1201 | 7 | EL1134_M110 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 1 | 16416 | 1202 | 1 | EL1134_M112 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 3 | 16416 | 1202 | 3 | EL1134_M112 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 5 | 16416 | 1202 | 5 | EL1134_M112 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 7 | 16416 | 1202 | 7 | EL1134_M112 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 9 | 16416 | 1203 | 1 | EL1134_M113 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 11 | 16416 | 1203 | 3 | EL1134_M113 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 13 | 16416 | 1203 | 5 | EL1134_M113 |  | BITVAL
| VALIDITY | [42 empty] | 12890 | 15 | 16416 | 1203 | 7 | EL1134_M113 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 1 | 16416 | 1204 | 1 | EL1134_M114 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 3 | 16416 | 1204 | 3 | EL1134_M114 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 5 | 16416 | 1204 | 5 | EL1134_M114 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 7 | 16416 | 1204 | 7 | EL1134_M114 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 9 | 16416 | 1205 | 1 | EL1134_M115 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 11 | 16416 | 1205 | 3 | EL1134_M115 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 13 | 16416 | 1205 | 5 | EL1134_M115 |  | BITVAL
| VALIDITY | [42 empty] | 12891 | 15 | 16416 | 1205 | 7 | EL1134_M115 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 1 | 16416 | 1206 | 1 | EL1134_M116 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 3 | 16416 | 1206 | 3 | EL1134_M116 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 5 | 16416 | 1206 | 5 | EL1134_M116 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 7 | 16416 | 1206 | 7 | EL1134_M116 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 9 | 16416 | 1207 | 1 | EL1134_M117 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 11 | 16416 | 1207 | 3 | EL1134_M117 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 13 | 16416 | 1207 | 5 | EL1134_M117 |  | BITVAL
| VALIDITY | [42 empty] | 12892 | 15 | 16416 | 1207 | 7 | EL1134_M117 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 1 | 16416 | 1208 | 1 | EL1134_M118 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 3 | 16416 | 1208 | 3 | EL1134_M118 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 5 | 16416 | 1208 | 5 | EL1134_M118 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 7 | 16416 | 1208 | 7 | EL1134_M118 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 9 | 16416 | 1209 | 1 | EL1134_M119 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 11 | 16416 | 1209 | 3 | EL1134_M119 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 13 | 16416 | 1209 | 5 | EL1134_M119 |  | BITVAL
| VALIDITY | [42 empty] | 12893 | 15 | 16416 | 1209 | 7 | EL1134_M119 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 1 | 16416 | 1210 | 1 | EL1134_M120 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 3 | 16416 | 1210 | 3 | EL1134_M120 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 5 | 16416 | 1210 | 5 | EL1134_M120 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 7 | 16416 | 1210 | 7 | EL1134_M120 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 9 | 16416 | 1211 | 1 | EL1134_M121 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 11 | 16416 | 1211 | 3 | EL1134_M121 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 13 | 16416 | 1211 | 5 | EL1134_M121 |  | BITVAL
| VALIDITY | [42 empty] | 12894 | 15 | 16416 | 1211 | 7 | EL1134_M121 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 1 | 16416 | 1212 | 1 | EL1134_M123 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 3 | 16416 | 1212 | 3 | EL1134_M123 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 5 | 16416 | 1212 | 5 | EL1134_M123 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 7 | 16416 | 1212 | 7 | EL1134_M123 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 9 | 16416 | 1213 | 1 | EL1134_M124 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 11 | 16416 | 1213 | 3 | EL1134_M124 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 13 | 16416 | 1213 | 5 | EL1134_M124 |  | BITVAL
| VALIDITY | [42 empty] | 12895 | 15 | 16416 | 1213 | 7 | EL1134_M124 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 1 | 16416 | 1214 | 1 | EL1134_M125 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 3 | 16416 | 1214 | 3 | EL1134_M125 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 5 | 16416 | 1214 | 5 | EL1134_M125 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 7 | 16416 | 1214 | 7 | EL1134_M125 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 9 | 16416 | 1215 | 1 | EL1134_M126 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 11 | 16416 | 1215 | 3 | EL1134_M126 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 13 | 16416 | 1215 | 5 | EL1134_M126 |  | BITVAL
| VALIDITY | [42 empty] | 12896 | 15 | 16416 | 1215 | 7 | EL1134_M126 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 1 | 16416 | 1216 | 1 | EL1134_M127 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 3 | 16416 | 1216 | 3 | EL1134_M127 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 5 | 16416 | 1216 | 5 | EL1134_M127 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 7 | 16416 | 1216 | 7 | EL1134_M127 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 9 | 16416 | 1217 | 1 | EL1134_M128 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 11 | 16416 | 1217 | 3 | EL1134_M128 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 13 | 16416 | 1217 | 5 | EL1134_M128 |  | BITVAL
| VALIDITY | [42 empty] | 12897 | 15 | 16416 | 1217 | 7 | EL1134_M128 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 1 | 16416 | 1218 | 1 | EL1134_M129 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 3 | 16416 | 1218 | 3 | EL1134_M129 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 5 | 16416 | 1218 | 5 | EL1134_M129 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 7 | 16416 | 1218 | 7 | EL1134_M129 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 9 | 16416 | 1219 | 1 | EL1134_M130 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 11 | 16416 | 1219 | 3 | EL1134_M130 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 13 | 16416 | 1219 | 5 | EL1134_M130 |  | BITVAL
| VALIDITY | [42 empty] | 12898 | 15 | 16416 | 1219 | 7 | EL1134_M130 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 1 | 16416 | 1220 | 1 | EL1134_M131 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 3 | 16416 | 1220 | 3 | EL1134_M131 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 5 | 16416 | 1220 | 5 | EL1134_M131 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 7 | 16416 | 1220 | 7 | EL1134_M131 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 9 | 16416 | 1221 | 1 | EL1134_M132 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 11 | 16416 | 1221 | 3 | EL1134_M132 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 13 | 16416 | 1221 | 5 | EL1134_M132 |  | BITVAL
| VALIDITY | [42 empty] | 12899 | 15 | 16416 | 1221 | 7 | EL1134_M132 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 1 | 16416 | 1222 | 1 | EL1134_M134 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 3 | 16416 | 1222 | 3 | EL1134_M134 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 5 | 16416 | 1222 | 5 | EL1134_M134 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 7 | 16416 | 1222 | 7 | EL1134_M134 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 9 | 16416 | 1223 | 1 | EL1134_M135 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 11 | 16416 | 1223 | 3 | EL1134_M135 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 13 | 16416 | 1223 | 5 | EL1134_M135 |  | BITVAL
| VALIDITY | [42 empty] | 12900 | 15 | 16416 | 1223 | 7 | EL1134_M135 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 1 | 16416 | 1224 | 1 | EL1134_M136 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 3 | 16416 | 1224 | 3 | EL1134_M136 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 5 | 16416 | 1224 | 5 | EL1134_M136 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 7 | 16416 | 1224 | 7 | EL1134_M136 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 9 | 16416 | 1225 | 1 | EL1134_M137 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 11 | 16416 | 1225 | 3 | EL1134_M137 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 13 | 16416 | 1225 | 5 | EL1134_M137 |  | BITVAL
| VALIDITY | [42 empty] | 12901 | 15 | 16416 | 1225 | 7 | EL1134_M137 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 1 | 16416 | 1226 | 1 | EL1134_M138 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 3 | 16416 | 1226 | 3 | EL1134_M138 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 5 | 16416 | 1226 | 5 | EL1134_M138 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 7 | 16416 | 1226 | 7 | EL1134_M138 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 9 | 16416 | 1227 | 1 | EL1134_M139 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 11 | 16416 | 1227 | 3 | EL1134_M139 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 13 | 16416 | 1227 | 5 | EL1134_M139 |  | BITVAL
| VALIDITY | [42 empty] | 12902 | 15 | 16416 | 1227 | 7 | EL1134_M139 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 1 | 16416 | 1228 | 1 | EL1134_M140 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 3 | 16416 | 1228 | 3 | EL1134_M140 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 5 | 16416 | 1228 | 5 | EL1134_M140 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 7 | 16416 | 1228 | 7 | EL1134_M140 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 9 | 16416 | 1229 | 1 | EL1134_M141 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 11 | 16416 | 1229 | 3 | EL1134_M141 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 13 | 16416 | 1229 | 5 | EL1134_M141 |  | BITVAL
| VALIDITY | [42 empty] | 12903 | 15 | 16416 | 1229 | 7 | EL1134_M141 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 1 | 16416 | 1230 | 1 | EL1134_M142 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 3 | 16416 | 1230 | 3 | EL1134_M142 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 5 | 16416 | 1230 | 5 | EL1134_M142 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 7 | 16416 | 1230 | 7 | EL1134_M142 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 9 | 16416 | 1231 | 1 | EL1134_M143 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 11 | 16416 | 1231 | 3 | EL1134_M143 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 13 | 16416 | 1231 | 5 | EL1134_M143 |  | BITVAL
| VALIDITY | [42 empty] | 12904 | 15 | 16416 | 1231 | 7 | EL1134_M143 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 1 | 16416 | 1232 | 1 | EL1134_M145 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 3 | 16416 | 1232 | 3 | EL1134_M145 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 5 | 16416 | 1232 | 5 | EL1134_M145 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 7 | 16416 | 1232 | 7 | EL1134_M145 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 9 | 16416 | 1233 | 1 | EL1134_M146 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 11 | 16416 | 1233 | 3 | EL1134_M146 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 13 | 16416 | 1233 | 5 | EL1134_M146 |  | BITVAL
| VALIDITY | [42 empty] | 12905 | 15 | 16416 | 1233 | 7 | EL1134_M146 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 1 | 16416 | 1234 | 1 | EL1134_M147 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 3 | 16416 | 1234 | 3 | EL1134_M147 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 5 | 16416 | 1234 | 5 | EL1134_M147 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 7 | 16416 | 1234 | 7 | EL1134_M147 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 9 | 16416 | 1235 | 1 | EL1134_M148 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 11 | 16416 | 1235 | 3 | EL1134_M148 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 13 | 16416 | 1235 | 5 | EL1134_M148 |  | BITVAL
| VALIDITY | [42 empty] | 12906 | 15 | 16416 | 1235 | 7 | EL1134_M148 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 1 | 16416 | 1236 | 1 | EL1134_M149 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 3 | 16416 | 1236 | 3 | EL1134_M149 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 5 | 16416 | 1236 | 5 | EL1134_M149 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 7 | 16416 | 1236 | 7 | EL1134_M149 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 9 | 16416 | 1237 | 1 | EL1134_M150 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 11 | 16416 | 1237 | 3 | EL1134_M150 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 13 | 16416 | 1237 | 5 | EL1134_M150 |  | BITVAL
| VALIDITY | [42 empty] | 12907 | 15 | 16416 | 1237 | 7 | EL1134_M150 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 1 | 16416 | 1238 | 1 | EL1134_M151 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 3 | 16416 | 1238 | 3 | EL1134_M151 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 5 | 16416 | 1238 | 5 | EL1134_M151 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 7 | 16416 | 1238 | 7 | EL1134_M151 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 9 | 16416 | 1239 | 1 | EL1134_M152 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 11 | 16416 | 1239 | 3 | EL1134_M152 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 13 | 16416 | 1239 | 5 | EL1134_M152 |  | BITVAL
| VALIDITY | [42 empty] | 12908 | 15 | 16416 | 1239 | 7 | EL1134_M152 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 1 | 16416 | 1240 | 1 | EL1134_M153 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 3 | 16416 | 1240 | 3 | EL1134_M153 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 5 | 16416 | 1240 | 5 | EL1134_M153 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 7 | 16416 | 1240 | 7 | EL1134_M153 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 9 | 16416 | 1241 | 1 | EL1134_M154 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 11 | 16416 | 1241 | 3 | EL1134_M154 |  | BITVAL
| VALIDITY | [42 empty] | 12909 | 13 | 16416 | 1241 | 5 | EL1134_M154 |  | BITVAL
SPARE | VALIDITY | [42 empty] | 12909 | 15 | 16416 | 1241 | 7 | EL1134_M154 |  | BITVAL
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | NOT | [10 empty] | 12971 | 2 | 16416 | 1364 | 2 | EL2809_M187 | 3 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | NOT | [10 empty] | 12971 | 3 | 16416 | 1364 | 3 | EL2809_M187 | 4 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | NOT | [10 empty] | 12971 | 4 | 16416 | 1364 | 4 | EL2809_M187 | 5 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | NOT | [10 empty] | 12971 | 5 | 16416 | 1364 | 5 | EL2809_M187 | 6 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | NOT | [10 empty] | 12971 | 6 | 16416 | 1364 | 6 | EL2809_M187 | 7 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | NOT | [10 empty] | 12971 | 7 | 16416 | 1364 | 7 | EL2809_M187 | 8 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 8 | 16416 | 1365 | 0 | EL2809_M187 | 9 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 9 | 16416 | 1365 | 1 | EL2809_M187 | 10 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 10 | 16416 | 1365 | 2 | EL2809_M187 | 11 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 11 | 16416 | 1365 | 3 | EL2809_M187 | 12 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 12 | 16416 | 1365 | 4 | EL2809_M187 | 13 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 13 | 16416 | 1365 | 5 | EL2809_M187 | 14 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 14 | 16416 | 1365 | 6 | EL2809_M187 | 15 | BIT
SPARE | PLC INTERNAL SIGNAL | CT | N | INT | [28 empty] | POL | [10 empty] | 12971 | 15 | 16416 | 1365 | 7 | EL2809_M187 | 16 | BIT
| SPARE | [37 empty] | 4 |  |  | 3023 | NA | 16050 | 0 | 16416 | 7522 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3024 | NA | 16051 | 0 | 16416 | 7524 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3025 | NA | 16052 | 0 | 16416 | 7526 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3026 | NA | 16053 | 0 | 16416 | 7528 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3027 | NA | 16054 | 0 | 16416 | 7530 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3028 | NA | 16055 | 0 | 16416 | 7532 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3029 | NA | 16056 | 0 | 16416 | 7534 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3030 | NA | 16057 | 0 | 16416 | 7536 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3031 | NA | 16058 | 0 | 16416 | 7538 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3032 | NA | 16059 | 0 | 16416 | 7540 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3033 | NA | 16060 | 0 | 16416 | 7542 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3034 | NA | 16061 | 0 | 16416 | 7544 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3055 | NA | 16062 | 0 | 16416 | 7546 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3055 | NA | 16063 | 0 | 16416 | 7548 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3056 | NA | 16064 | 0 | 16416 | 7550 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3057 | NA | 16065 | 0 | 16416 | 7552 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3058 | NA | 16066 | 0 | 16416 | 7554 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3059 | NA | 13128 | NA | 16416 | 1678 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3060 | NA | 13129 | NA | 16416 | 1680 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3061 | NA | 13130 | NA | 16416 | 1682 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3062 | NA | 13131 | NA | 16416 | 1684 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3063 | NA | 13132 | NA | 16416 | 1686 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3064 | NA | 13133 | NA | 16416 | 1688 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3065 | NA | 13134 | NA | 16416 | 1690 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3066 | NA | 13135 | NA | 16416 | 1692 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3067 | NA | 13136 | NA | 16416 | 1694 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3068 | NA | 13137 | NA | 16416 | 1696 | 0 | EL6021_M178 |  | U16
| SPARE | [37 empty] | 4 |  |  | 3218 | NA | 13287 | NA | 16416 | 1996 | 0 | EL6021_M178 |  | I32
| SPARE | [37 empty] | 4 |  |  | 3220 | NA | 13289 | NA | 16416 | 2000 | 0 | EL6021_M178 |  | I32
| SPARE | [37 empty] | 4 |  |  | 3222 | NA | 13291 | NA | 16416 | 2004 | 0 | EL6021_M178 |  | I32
| SPARE | [37 empty] | 4 |  |  | 3224 | NA | 13293 | NA | 16416 | 2008 | 0 | EL6021_M178 |  | I32
| SPARE | [37 empty] | 4 |  |  | 3226 | NA | 13295 | NA | 16416 | 2012 | 0 | EL6021_M178 |  | I32
| SPARE | [37 empty] | 4 |  |  | 3228 | NA | 13297 | NA | 16416 | 2016 | 0 | EL6021_M178 |  | I32
| SPARE | [37 empty] | 4 |  |  | 3366 | NA | 13435 | NA | 16416 | 2292 | 0 | EL6021_M178 |  | UINT
| SPARE | [37 empty] | 4 |  |  | 3367 | NA | 13436 | NA | 16416 | 2294 | 0 | EL6021_M178 |  | UINT
| SPARE | [37 empty] | 4 |  |  | 3368 | NA | 13437 | NA | 16416 | 2296 | 0 | EL6021_M178 |  | UINT
| SPARE | [37 empty] | 4 |  |  | 3369 | NA | 13438 | NA | 16416 | 2298 | 0 | EL6021_M178 |  | UINT
| SPARE | [37 empty] | 5 |  |  | 3004 | NA | 13450 | NA | 16416 | 2322 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 3005 | NA | 13451 | NA | 16416 | 2324 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 3006 | NA | 13452 | NA | 16416 | 2326 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 3007 | NA | 13453 | NA | 16416 | 2328 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 3008 | NA | 13454 | NA | 16416 | 2330 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 3009 | NA | 13455 | NA | 16416 | 2332 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 3010 | NA | 13456 | NA | 16416 | 2334 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2001 | NA | 13459 | NA | 16416 | 2340 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2002 | NA | 13460 | NA | 16416 | 2342 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2003 | NA | 13461 | NA | 16416 | 2344 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2004 | NA | 13462 | NA | 16416 | 2346 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2005 | NA | 13463 | NA | 16416 | 2348 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2006 | NA | 13464 | NA | 16416 | 2350 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2007 | NA | 13465 | NA | 16416 | 2352 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2008 | NA | 13466 | NA | 16416 | 2354 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 2009 | NA | 13467 | NA | 16416 | 2356 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1023 | NA | 13490 | NA | 16416 | 2402 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1024 | NA | 13491 | NA | 16416 | 2404 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1025 | NA | 13492 | NA | 16416 | 2406 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1026 | NA | 13493 | NA | 16416 | 2408 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1027 | NA | 13494 | NA | 16416 | 2410 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1028 | NA | 13495 | NA | 16416 | 2412 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1030 | NA | 13497 | NA | 16416 | 2416 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1032 | NA | 13499 | NA | 16416 | 2420 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1034 | NA | 13501 | NA | 16416 | 2424 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | ti | NA | 13533 | NA | 16416 | 2488 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1074 | NA | 13534 | NA | 16416 | 2490 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1075 | NA | 13535 | NA | 16416 | 2492 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1076 | NA | 13536 | NA | 16416 | 2494 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1077 | NA | 13537 | NA | 16416 | 2496 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1078 | NA | 13538 | NA | 16416 | 2498 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1080 | NA | 13540 | NA | 16416 | 2502 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1082 | NA | 13542 | NA | 16416 | 2506 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1084 | NA | 13544 | NA | 16416 | 2510 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1123 | NA | 13574 | NA | 16416 | 2570 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1124 | NA | 13575 | NA | 16416 | 2572 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1125 | NA | 13576 | NA | 16416 | 2574 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1126 | NA | 13577 | NA | 16416 | 2576 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1127 | NA | 13578 | NA | 16416 | 2578 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1128 | NA | 13579 | NA | 16416 | 2580 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1130 | NA | 13581 | NA | 16416 | 2584 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1132 | NA | 13583 | NA | 16416 | 2588 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1134 | NA | 13585 | NA | 16416 | 2592 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1173 | NA | 13615 | NA | 16416 | 2652 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1174 | NA | 13616 | NA | 16416 | 2654 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1175 | NA | 13617 | NA | 16416 | 2656 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1176 | NA | 13618 | NA | 16416 | 2658 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1177 | NA | 13619 | NA | 16416 | 2660 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1178 | NA | 13620 | NA | 16416 | 2662 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1180 | NA | 13622 | NA | 16416 | 2666 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1182 | NA | 13624 | NA | 16416 | 2670 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1184 | NA | 13626 | NA | 16416 | 2674 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1223 | NA | 13656 | NA | 16416 | 2734 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1224 | NA | 13657 | NA | 16416 | 2736 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1225 | NA | 13658 | NA | 16416 | 2738 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1226 | NA | 13659 | NA | 16416 | 2740 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1227 | NA | 13660 | NA | 16416 | 2742 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1228 | NA | 13661 | NA | 16416 | 2744 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1230 | NA | 13663 | NA | 16416 | 2748 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1232 | NA | 13665 | NA | 16416 | 2752 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1234 | NA | 13667 | NA | 16416 | 2756 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1273 | NA | 13697 | NA | 16416 | 2816 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1274 | NA | 13698 | NA | 16416 | 2818 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1275 | NA | 13699 | NA | 16416 | 2820 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1276 | NA | 13700 | NA | 16416 | 2822 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1277 | NA | 13701 | NA | 16416 | 2824 | 0 | EL6021_M179 |  | U16
| SPARE | [37 empty] | 5 |  |  | 1278 | NA | 13702 | NA | 16416 | 2826 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1280 | NA | 13704 | NA | 16416 | 2830 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1282 | NA | 13706 | NA | 16416 | 2834 | 0 | EL6021_M179 |  | U32
| SPARE | [37 empty] | 5 |  |  | 1284 | NA | 13708 | NA | 16416 | 2838 | 0 | EL6021_M179 |  | U32
SPARE | SPARE | [31 empty] | NOT | [5 empty] | 6 |  |  | 3005 | NA | 13722 | NA | 16416 | 2866 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3010 | NA | 13727 | NA | 16416 | 2876 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3012 | NA | 13729 | NA | 16416 | 2880 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3013 | NA | 13730 | NA | 16416 | 2882 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3014 | NA | 13731 | NA | 16416 | 2884 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3015 | NA | 13732 | NA | 16416 | 2886 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3018 | NA | 13735 | NA | 16416 | 2892 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3019 | NA | 13736 | NA | 16416 | 2894 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3020 | NA | 13737 | NA | 16416 | 2896 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3021 | NA | 13738 | NA | 16416 | 2898 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3022 | NA | 13739 | NA | 16416 | 2900 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3023 | NA | 13740 | NA | 16416 | 2902 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3024 | NA | 13741 | NA | 16416 | 2904 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3025 | NA | 13742 | NA | 16416 | 2906 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3026 | NA | 13743 | NA | 16416 | 2908 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3027 | NA | 13744 | NA | 16416 | 2910 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3028 | NA | 13745 | NA | 16416 | 2912 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3029 | NA | 13746 | NA | 16416 | 2914 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3030 | NA | 13747 | NA | 16416 | 2916 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3031 | NA | 13748 | NA | 16416 | 2918 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3032 | NA | 13749 | NA | 16416 | 2920 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3033 | NA | 13750 | NA | 16416 | 2922 | 0 | EL6021_M180 |  | UINT | 1 o 2
SPARE | SPARE | [37 empty] | 6 |  |  | 3034 | NA | 13751 | NA | 16416 | 2924 | 0 | EL6021_M180 |  | UINT | 1 o 2
| SPARE | [40 empty] | 3014 | 7 | 13780 | 14 | 16416 | 2983 | 6 | EL6021_M180 |  | BITVAL
| SPARE | [37 empty] | 6 |  |  | 3162 | NA | 13961 | NA | 16416 | 3344 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3163 | NA | 13962 | NA | 16416 | 3346 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3164 | NA | 13963 | NA | 16416 | 3348 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3165 | NA | 13964 | NA | 16416 | 3350 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3166 | NA | 13965 | NA | 16416 | 3352 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3167 | NA | 13966 | NA | 16416 | 3354 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3168 | NA | 13967 | NA | 16416 | 3356 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3169 | NA | 13968 | NA | 16416 | 3358 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3170 | NA | 13969 | NA | 16416 | 3360 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3171 | NA | 13970 | NA | 16416 | 3362 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3172 | NA | 13971 | NA | 16416 | 3364 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3173 | NA | 13972 | NA | 16416 | 3366 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3174 | NA | 13973 | NA | 16416 | 3368 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3175 | NA | 13974 | NA | 16416 | 3370 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3176 | NA | 13975 | NA | 16416 | 3372 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3177 | NA | 13976 | NA | 16416 | 3374 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3178 | NA | 13977 | NA | 16416 | 3376 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3179 | NA | 13978 | NA | 16416 | 3378 | 0 | EL6021_M180 |  | INT
| SPARE | [40 empty] | 3228 | NA | 14027 | NA | 16416 | 3476 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3238 | NA | 14037 | NA | 16416 | 3496 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3239 | NA | 14038 | NA | 16416 | 3498 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3258 | NA | 14057 | NA | 16416 | 3536 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3259 | NA | 14058 | NA | 16416 | 3538 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3260 | NA | 14059 | NA | 16416 | 3540 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3263 | NA | 14062 | NA | 16416 | 3546 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3264 | NA | 14063 | NA | 16416 | 3548 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3265 | NA | 14064 | NA | 16416 | 3550 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3266 | NA | 14065 | NA | 16416 | 3552 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3267 | NA | 14066 | NA | 16416 | 3554 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3268 | NA | 14067 | NA | 16416 | 3556 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3269 | NA | 14068 | NA | 16416 | 3558 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3270 | NA | 14069 | NA | 16416 | 3560 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3271 | NA | 14070 | NA | 16416 | 3562 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3272 | NA | 14071 | NA | 16416 | 3564 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3273 | NA | 14072 | NA | 16416 | 3566 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3274 | NA | 14073 | NA | 16416 | 3568 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3275 | NA | 14074 | NA | 16416 | 3570 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3276 | NA | 14075 | NA | 16416 | 3572 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3277 | NA | 14076 | NA | 16416 | 3574 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3278 | NA | 14077 | NA | 16416 | 3576 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3279 | NA | 14078 | NA | 16416 | 3578 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3280 | NA | 14079 | NA | 16416 | 3580 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3281 | NA | 14080 | NA | 16416 | 3582 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3282 | NA | 14081 | NA | 16416 | 3584 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3283 | NA | 14082 | NA | 16416 | 3586 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3284 | NA | 14083 | NA | 16416 | 3588 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3285 | NA | 14084 | NA | 16416 | 3590 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3286 | NA | 14085 | NA | 16416 | 3592 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3287 | NA | 14086 | NA | 16416 | 3594 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3288 | NA | 14087 | NA | 16416 | 3596 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3289 | NA | 14088 | NA | 16416 | 3598 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3290 | NA | 14089 | NA | 16416 | 3600 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3291 | NA | 14090 | NA | 16416 | 3602 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3292 | NA | 14091 | NA | 16416 | 3604 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3293 | NA | 14092 | NA | 16416 | 3606 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 6 |  |  | 3294 | NA | 14093 | NA | 16416 | 3608 | 0 | EL6021_M180 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3002 | NA | 14100 | NA | 16416 | 3622 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3003 | NA | 14101 | NA | 16416 | 3624 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3009 | NA | 14107 | NA | 16416 | 3636 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3010 | NA | 14108 | NA | 16416 | 3638 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3012 | NA | 14110 | NA | 16416 | 3642 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3013 | NA | 14111 | NA | 16416 | 3644 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3014 | NA | 14112 | NA | 16416 | 3646 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3015 | NA | 14113 | NA | 16416 | 3648 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3016 | NA | 14114 | NA | 16416 | 3650 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3017 | NA | 14115 | NA | 16416 | 3652 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3018 | NA | 14116 | NA | 16416 | 3654 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3019 | NA | 14117 | NA | 16416 | 3656 | 0 | EL6021_M181 |  | UINT | 1 o 2
| SPARE | [37 empty] | 7 |  |  | 3010 | NA | 14142 | NA | 16416 | 3706 | 0 | EL6021_M181 |  | U16
| SPARE | [37 empty] | 7 |  |  | 3014 | NA | 14149 | NA | 16416 | 3720 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3015 | NA | 14150 | NA | 16416 | 3722 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3016 | NA | 14151 | NA | 16416 | 3724 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3017 | NA | 14152 | NA | 16416 | 3726 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3020 | NA | [7 empty] | UINT
| SPARE | [37 empty] | 7 |  |  | 3021 | NA | [7 empty] | UINT
| SPARE | [37 empty] | 7 |  |  | 3022 | NA | 14157 | NA | 16416 | 3736 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3023 | NA | 14158 | NA | 16416 | 3738 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3024 | NA | 14159 | NA | 16416 | 3740 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3032 | NA | 14174 | NA | 16416 | 3770 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3033 | NA | 14175 | NA | 16416 | 3772 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3034 | NA | 14176 | NA | 16416 | 3774 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3035 | NA | 14177 | NA | 16416 | 3776 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3036 | NA | 14178 | NA | 16416 | 3778 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3040 | NA | 14185 | NA | 16416 | 3792 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3041 | NA | 14186 | NA | 16416 | 3794 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3042 | NA | 14187 | NA | 16416 | 3796 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3043 | NA | 14188 | NA | 16416 | 3798 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3046 | NA | 14193 | NA | 16416 | 3808 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3047 | NA | 14194 | NA | 16416 | 3810 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3048 | NA | 14195 | NA | 16416 | 3812 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3049 | NA | 14196 | NA | 16416 | 3814 | 0 | EL6021_M181 |  | UINT
| SPARE | [37 empty] | 7 |  |  | 3092 | NA | 14239 | NA | 16416 | 3900 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3093 | NA | 14240 | NA | 16416 | 3902 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3094 | NA | 14241 | NA | 16416 | 3904 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3095 | NA | 14242 | NA | 16416 | 3906 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3096 | NA | 14243 | NA | 16416 | 3908 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3097 | NA | 14244 | NA | 16416 | 3910 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3098 | NA | 14245 | NA | 16416 | 3912 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3099 | NA | 14246 | NA | 16416 | 3914 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3100 | NA | 14247 | NA | 16416 | 3916 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3101 | NA | 14248 | NA | 16416 | 3918 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3102 | NA | 14249 | NA | 16416 | 3920 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3103 | NA | 14250 | NA | 16416 | 3922 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3104 | NA | 14251 | NA | 16416 | 3924 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3105 | NA | 14252 | NA | 16416 | 3926 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3106 | NA | 14253 | NA | 16416 | 3928 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3107 | NA | 14254 | NA | 16416 | 3930 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3108 | NA | 14255 | NA | 16416 | 3932 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3109 | NA | 14256 | NA | 16416 | 3934 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3110 | NA | 14257 | NA | 16416 | 3936 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3111 | NA | 14258 | NA | 16416 | 3938 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3112 | NA | 14259 | NA | 16416 | 3940 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3113 | NA | 14260 | NA | 16416 | 3942 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3114 | NA | 14261 | NA | 16416 | 3944 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3115 | NA | 14262 | NA | 16416 | 3946 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3116 | NA | 14263 | NA | 16416 | 3948 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3117 | NA | 14264 | NA | 16416 | 3950 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3118 | NA | 14265 | NA | 16416 | 3952 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3119 | NA | 14266 | NA | 16416 | 3954 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3120 | NA | 14267 | NA | 16416 | 3956 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3121 | NA | 14268 | NA | 16416 | 3958 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3122 | NA | 14269 | NA | 16416 | 3960 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3123 | NA | 14270 | NA | 16416 | 3962 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3124 | NA | 14271 | NA | 16416 | 3964 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3125 | NA | 14272 | NA | 16416 | 3966 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3126 | NA | 14273 | NA | 16416 | 3968 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3127 | NA | 14274 | NA | 16416 | 3970 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3128 | NA | 14275 | NA | 16416 | 3972 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3129 | NA | 14276 | NA | 16416 | 3974 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3130 | NA | 14277 | NA | 16416 | 3976 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3131 | NA | 14278 | NA | 16416 | 3978 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3132 | NA | 14279 | NA | 16416 | 3980 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3133 | NA | 14280 | NA | 16416 | 3982 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3134 | NA | 14281 | NA | 16416 | 3984 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3135 | NA | 14282 | NA | 16416 | 3986 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3136 | NA | 14283 | NA | 16416 | 3988 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3137 | NA | 14284 | NA | 16416 | 3990 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3138 | NA | 14285 | NA | 16416 | 3992 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3139 | NA | 14286 | NA | 16416 | 3994 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3140 | NA | 14287 | NA | 16416 | 3996 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3141 | NA | 14288 | NA | 16416 | 3998 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3142 | NA | 14289 | NA | 16416 | 4000 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3143 | NA | 14290 | NA | 16416 | 4002 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3144 | NA | 14291 | NA | 16416 | 4004 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3145 | NA | 14292 | NA | 16416 | 4006 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3146 | NA | 14293 | NA | 16416 | 4008 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3147 | NA | 14294 | NA | 16416 | 4010 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3148 | NA | 14295 | NA | 16416 | 4012 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3149 | NA | 14296 | NA | 16416 | 4014 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3150 | NA | 14297 | NA | 16416 | 4016 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3151 | NA | 14298 | NA | 16416 | 4018 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3152 | NA | 14299 | NA | 16416 | 4020 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3153 | NA | 14300 | NA | 16416 | 4022 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3154 | NA | 14301 | NA | 16416 | 4024 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3155 | NA | 14302 | NA | 16416 | 4026 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3156 | NA | 14303 | NA | 16416 | 4028 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3157 | NA | 14304 | NA | 16416 | 4030 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3158 | NA | 14305 | NA | 16416 | 4032 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3159 | NA | 14306 | NA | 16416 | 4034 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3160 | NA | 14307 | NA | 16416 | 4036 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3161 | NA | 14308 | NA | 16416 | 4038 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3162 | NA | 14309 | NA | 16416 | 4040 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3163 | NA | 14310 | NA | 16416 | 4042 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3164 | NA | 14311 | NA | 16416 | 4044 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3165 | NA | 14312 | NA | 16416 | 4046 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3166 | NA | 14313 | NA | 16416 | 4048 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3167 | NA | 14314 | NA | 16416 | 4050 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3168 | NA | 14315 | NA | 16416 | 4052 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3169 | NA | 14316 | NA | 16416 | 4054 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3170 | NA | 14317 | NA | 16416 | 4056 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3171 | NA | 14318 | NA | 16416 | 4058 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3172 | NA | 14319 | NA | 16416 | 4060 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3173 | NA | 14320 | NA | 16416 | 4062 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3174 | NA | 14321 | NA | 16416 | 4064 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3175 | NA | 14322 | NA | 16416 | 4066 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3176 | NA | 14323 | NA | 16416 | 4068 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3177 | NA | 14324 | NA | 16416 | 4070 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3178 | NA | 14325 | NA | 16416 | 4072 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3179 | NA | 14326 | NA | 16416 | 4074 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3180 | NA | 14327 | NA | 16416 | 4076 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3181 | NA | 14328 | NA | 16416 | 4078 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3208 | NA | 14355 | NA | 16416 | 4132 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3209 | NA | 14356 | NA | 16416 | 4134 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3210 | NA | 14357 | NA | 16416 | 4136 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3211 | NA | 14358 | NA | 16416 | 4138 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3212 | NA | 14359 | NA | 16416 | 4140 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3213 | NA | 14360 | NA | 16416 | 4142 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3214 | NA | 14361 | NA | 16416 | 4144 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3215 | NA | 14362 | NA | 16416 | 4146 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3216 | NA | 14363 | NA | 16416 | 4148 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3217 | NA | 14364 | NA | 16416 | 4150 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3218 | NA | 14365 | NA | 16416 | 4152 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3219 | NA | 14366 | NA | 16416 | 4154 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3220 | NA | 14367 | NA | 16416 | 4156 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3221 | NA | 14368 | NA | 16416 | 4158 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3222 | NA | 14369 | NA | 16416 | 4160 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3223 | NA | 14370 | NA | 16416 | 4162 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3224 | NA | 14371 | NA | 16416 | 4164 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3225 | NA | 14372 | NA | 16416 | 4166 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3226 | NA | 14373 | NA | 16416 | 4168 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3227 | NA | 14374 | NA | 16416 | 4170 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3228 | NA | 14375 | NA | 16416 | 4172 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3229 | NA | 14376 | NA | 16416 | 4174 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3230 | NA | 14377 | NA | 16416 | 4176 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3231 | NA | 14378 | NA | 16416 | 4178 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3232 | NA | 14379 | NA | 16416 | 4180 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3233 | NA | 14380 | NA | 16416 | 4182 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3234 | NA | 14381 | NA | 16416 | 4184 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3235 | NA | 14382 | NA | 16416 | 4186 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3236 | NA | 14383 | NA | 16416 | 4188 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3237 | NA | 14384 | NA | 16416 | 4190 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3238 | NA | 14385 | NA | 16416 | 4192 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3239 | NA | 14386 | NA | 16416 | 4194 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3240 | NA | 14387 | NA | 16416 | 4196 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3241 | NA | 14388 | NA | 16416 | 4198 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3242 | NA | 14389 | NA | 16416 | 4200 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3243 | NA | 14390 | NA | 16416 | 4202 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3244 | NA | 14391 | NA | 16416 | 4204 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3245 | NA | 14392 | NA | 16416 | 4206 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3246 | NA | 14393 | NA | 16416 | 4208 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3247 | NA | 14394 | NA | 16416 | 4210 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3248 | NA | 14395 | NA | 16416 | 4212 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3249 | NA | 14396 | NA | 16416 | 4214 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3250 | NA | 14397 | NA | 16416 | 4216 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3251 | NA | 14398 | NA | 16416 | 4218 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3252 | NA | 14399 | NA | 16416 | 4220 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3253 | NA | 14400 | NA | 16416 | 4222 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3254 | NA | 14401 | NA | 16416 | 4224 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3255 | NA | 14402 | NA | 16416 | 4226 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3256 | NA | 14403 | NA | 16416 | 4228 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3257 | NA | 14404 | NA | 16416 | 4230 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3258 | NA | 14405 | NA | 16416 | 4232 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3259 | NA | 14406 | NA | 16416 | 4234 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3260 | NA | 14407 | NA | 16416 | 4236 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3261 | NA | 14408 | NA | 16416 | 4238 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3262 | NA | 14409 | NA | 16416 | 4240 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3263 | NA | 14410 | NA | 16416 | 4242 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3264 | NA | 14411 | NA | 16416 | 4244 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3265 | NA | 14412 | NA | 16416 | 4246 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3266 | NA | 14413 | NA | 16416 | 4248 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3267 | NA | 14414 | NA | 16416 | 4250 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3268 | NA | 14415 | NA | 16416 | 4252 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3269 | NA | 14416 | NA | 16416 | 4254 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3270 | NA | 14417 | NA | 16416 | 4256 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3271 | NA | 14418 | NA | 16416 | 4258 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3272 | NA | 14419 | NA | 16416 | 4260 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3273 | NA | 14420 | NA | 16416 | 4262 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3274 | NA | 14421 | NA | 16416 | 4264 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3275 | NA | 14422 | NA | 16416 | 4266 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3276 | NA | 14423 | NA | 16416 | 4268 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3277 | NA | 14424 | NA | 16416 | 4270 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3278 | NA | 14425 | NA | 16416 | 4272 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3279 | NA | 14426 | NA | 16416 | 4274 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3280 | NA | 14427 | NA | 16416 | 4276 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3281 | NA | 14428 | NA | 16416 | 4278 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3282 | NA | 14429 | NA | 16416 | 4280 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3283 | NA | 14430 | NA | 16416 | 4282 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3284 | NA | 14431 | NA | 16416 | 4284 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3285 | NA | 14432 | NA | 16416 | 4286 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3286 | NA | 14433 | NA | 16416 | 4288 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3287 | NA | 14434 | NA | 16416 | 4290 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3288 | NA | 14435 | NA | 16416 | 4292 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3289 | NA | 14436 | NA | 16416 | 4294 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3290 | NA | 14437 | NA | 16416 | 4296 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3291 | NA | 14438 | NA | 16416 | 4298 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3292 | NA | 14439 | NA | 16416 | 4300 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3293 | NA | 14440 | NA | 16416 | 4302 | 0 | EL6021_M181 |  | INT
| SPARE | [37 empty] | 7 |  |  | 3294 | NA | 14441 | NA | 16416 | 4304 | 0 | EL6021_M181 |  | INT
SZC6000 | VEGA BUNKER DTG&DI PLC : WATCHDOG | MA | N | RES | 1 | A |  |  |  |  | 0 | 65535 | [20 empty] | POL | 6000 |  | DG60 Etat PLC DETG DI | Detection Gaz (DG) |  | 1 |  |  | 500 | 0 | 12550 | 0 | 16416 | 522 | 0 | EL6021_M176 |  | U16
WZC6002 | VEGA BUNKER O&W PLC : WATCHDOG | MA | N | RES | 1 | A |  |  |  |  | 0 | 65535 | [20 empty] | POL | 6000 |  | W60 Etat PLC OeV | Optique et Video VEGA (W) |  | 2 |  |  | 250 | 0 | 12390 | 0 | 16416 | 202 | 0 | EL6021_M176 |  | U16
ZCM6836P10 | SWITCH 1 BUNKER - ETAT PORT 10 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P11 | SWITCH 1 BUNKER - ETAT PORT 11 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P12 | SWITCH 1 BUNKER - ETAT PORT 12 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P13 | SWITCH 1 BUNKER - ETAT PORT 13 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P14 | SWITCH 1 BUNKER - ETAT PORT 14 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P15 | SWITCH 1 BUNKER - ETAT PORT 15 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P16 | SWITCH 1 BUNKER - ETAT PORT 16 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P17 | SWITCH 1 BUNKER - ETAT PORT 17 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P18 | SWITCH 1 BUNKER - ETAT PORT 18 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P19 | SWITCH 1 BUNKER - ETAT PORT 19 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P20 | SWITCH 1 BUNKER - ETAT PORT 20 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P21 | SWITCH 1 BUNKER - ETAT PORT 21 | MA | N | INT | 0 | Z | [9 empty] | x<>'up' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P22 | SWITCH 1 BUNKER - ETAT PORT 22 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P23 | SWITCH 1 BUNKER - ETAT PORT 23 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6836P24 | SWITCH 1 BUNKER - ETAT PORT 24 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837F1 | SWITCH 2 BUNKER - ETAT FO PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837F2 | SWITCH 2 BUNKER - ETAT FO PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P1 | SWITCH 2 BUNKER - ETAT PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P2 | SWITCH 2 BUNKER - ETAT PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P3 | SWITCH 2 BUNKER - ETAT PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P4 | SWITCH 2 BUNKER - ETAT PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P5 | SWITCH 2 BUNKER - ETAT PORT 5 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P6 | SWITCH 2 BUNKER - ETAT PORT 6 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P7 | SWITCH 2 BUNKER - ETAT PORT 7 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P8 | SWITCH 2 BUNKER - ETAT PORT 8 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P9 | SWITCH 2 BUNKER - ETAT PORT 9 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P10 | SWITCH 2 BUNKER - ETAT PORT 10 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P11 | SWITCH 2 BUNKER - ETAT PORT 11 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P12 | SWITCH 2 BUNKER - ETAT PORT 12 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P13 | SWITCH 2 BUNKER - ETAT PORT 13 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P14 | SWITCH 2 BUNKER - ETAT PORT 14 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P15 | SWITCH 2 BUNKER - ETAT PORT 15 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P16 | SWITCH 2 BUNKER - ETAT PORT 16 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P17 | SWITCH 2 BUNKER - ETAT PORT 17 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
GE01DMA | SYNTHESE DEFAUT Groupe électrogène | MA | N | CAL | 2 | E | [24 empty] | ECN7000W;EKM7000W;EKM7001W |  | MTCP |  |  |  | Energy Lagrange (E) | NEW | 10
OVM6401C1 | WIS OVM 6401 FERMEE 1 ISOLATION APPROVISIONNEMENT EAU OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 0 | 16416 | 9422 | 0 | EL1008_M190 | 1 | BITVAL
OVM6403C1 | WIS OVM 6403 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 2 | 16416 | 9422 | 2 | EL1008_M190 | 2 | BITVAL
OVM6405C1 | WIS OVM 6405 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 4 | 16416 | 9422 | 4 | EL1008_M190 | 3 | BITVAL
OVM6406C1 | WIS OVM 6406 FERMEE 1 VIDANGE RESERVOIRS FONCTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 6 | 16416 | 9422 | 6 | EL1008_M190 | 4 | BITVAL
OVM6407C1 | WIS OVM 6407 FERMEE 1 ISOLATION APPROVISIONNEMENT EAU EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 8 | 16416 | 9423 | 0 | EL1008_M190 | 5 | BITVAL
OVM6409C1 | WIS OVM 6409 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 10 | 16416 | 9423 | 2 | EL1008_M190 | 6 | BITVAL
OVM6411C1 | WIS OVM 6411 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 12 | 16416 | 9423 | 4 | EL1008_M190 | 7 | BITVAL
OVM6412C1 | WIS OVM 6412 FERMEE 1 VIDANGE RESERVOIRS FONCTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17000 | 14 | 16416 | 9423 | 6 | EL1008_M190 | 8 | BITVAL
OVM6401O1 | WIS OVM 6401 OUVERTE 1 ISOLATION APPROVISIONNEMENT EAU OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 0 | 16416 | 9424 | 0 | EL1008_M191 | 1 | BITVAL
OVM6402O1 | WIS OVM 6402 OUVERTE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 2 | 16416 | 9424 | 2 | EL1008_M191 | 2 | BITVAL
OVM6404O1 | WIS OVM 6404 OUVERTE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 4 | 16416 | 9424 | 4 | EL1008_M191 | 3 | BITVAL
OVM6407O1 | WIS OVM 6407 OUVERTE 1 ISOLATION APPROVISIONNEMENT EAU EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 6 | 16416 | 9424 | 6 | EL1008_M191 | 4 | BITVAL
OVM6408O1 | WIS OVM 6408 OUVERTE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 8 | 16416 | 9425 | 0 | EL1008_M191 | 5 | BITVAL
OVM6410O1 | WIS OVM 6410 OUVERTE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 10 | 16416 | 9425 | 2 | EL1008_M191 | 6 | BITVAL
OVP6401O1 | WIS OVP 6401 OUVERTE 1 ISOLATION REDONDANTE APPROVISIONNEMENT EAU OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 12 | 16416 | 9425 | 4 | EL1008_M191 | 7 | BITVAL
OVP6403O1 | WIS OVP 6403 OUVERTE 1 CHARGEMENT/PRESSURISATION DES RESERVOIRS OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17001 | 14 | 16416 | 9425 | 6 | EL1008_M191 | 8 | BITVAL
OVM6413C1 | WIS OVM 6413 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 0 | 16416 | 9426 | 0 | EL1008_M192 | 1 | BITVAL
OVM6414C1 | WIS OVM 6414 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 2 | 16416 | 9426 | 2 | EL1008_M192 | 2 | BITVAL
OVP6401C1 | WIS OVP 6401 FERMEE 1 ISOLATION REDONDANTE APPROVISIONNEMENT EAU OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 4 | 16416 | 9426 | 4 | EL1008_M192 | 3 | BITVAL
OVP6402C1 | WIS OVP 6402 FERMEE 1 VIDANGE/DEPRESSURISATION OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 6 | 16416 | 9426 | 6 | EL1008_M192 | 4 | BITVAL
OVP6403C1 | WIS OVP 6403 FERMEE 1 CHARGEMENT/PRESSURISATION RESERVOIRS OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 8 | 16416 | 9427 | 0 | EL1008_M192 | 5 | BITVAL
OVP6404C1 | WIS OVP 6404 FERMEE 1 CHARGEMENT RESEAU DISTRIBUTION OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 10 | 16416 | 9427 | 2 | EL1008_M192 | 6 | BITVAL
OVP6405C1 | WIS OVP 6405 FERMEE 1 DEPRESSURISATION/EVACUATION RESERVOIRS OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 12 | 16416 | 9427 | 4 | EL1008_M192 | 7 | BITVAL
OVP6406C1 | WIS OVP 6406 FERMEE 1 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17002 | 14 | 16416 | 9427 | 6 | EL1008_M192 | 8 | BITVAL
OVP6404O1 | WIS OVP 6404 OUVERTE 1 CHARGEMENT RESEAU DISTRIBUTION OUEST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 0 | 16416 | 9428 | 0 | EL1008_M193 | 1 | BITVAL
OVP6406O1 | WIS OVP 6406 OUVERTE 1 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 2 | 16416 | 9428 | 2 | EL1008_M193 | 2 | BITVAL
OVP6407O1 | WIS OVP 6407 OUVERTE 1 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 4 | 16416 | 9428 | 4 | EL1008_M193 | 3 | BITVAL
OVP6408O1 | WIS OVP 6408 OUVERTE 1 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 6 | 16416 | 9428 | 6 | EL1008_M193 | 4 | BITVAL
OVP6409O1 | WIS OVP 6409 OUVERTE 1 ISOLATION REDONDANTE APPROVISIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 8 | 16416 | 9429 | 0 | EL1008_M193 | 5 | BITVAL
OVP6411O1 | WIS OVP 6411 OUVERTE 1 CHARGEMENT/PRESSURISATION RESERVOIRS EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 10 | 16416 | 9429 | 2 | EL1008_M193 | 6 | BITVAL
OVP6412O1 | WIS OVP 6412 OUVERTE 1 CHARGEMENT RESEAU DISTRIBUTION EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 12 | 16416 | 9429 | 4 | EL1008_M193 | 7 | BITVAL
OVP6414O1 | WIS OVP 6414 OUVERTE 1 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17003 | 14 | 16416 | 9429 | 6 | EL1008_M193 | 8 | BITVAL
OVP6407C1 | WIS OVP 6407 FERMEE 1 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 0 | 16416 | 9430 | 0 | EL1008_M194 | 1 | BITVAL
OVP6408C1 | WIS OVP 6408 FERMEE 1 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 2 | 16416 | 9430 | 2 | EL1008_M194 | 2 | BITVAL
OVP6409C1 | WIS OVP 6409 FERMEE 1 ISOLATION REDONDANTE APPROVISIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 4 | 16416 | 9430 | 4 | EL1008_M194 | 5 | BITVAL
OVP6410C1 | WIS OVP 6410 FERMEE 1 VIDANGE/DEPRESSURISATION EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 6 | 16416 | 9430 | 6 | EL1008_M194 | 4 | BITVAL
OVP6411C1 | WIS OVP 6411 FERMEE 1 CHARGEMENT/PRESSURISATION RESERVOIRS EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 8 | 16416 | 9431 | 0 | EL1008_M194 | 5 | BITVAL
OVP6412C1 | WIS OVP 6412 FERMEE 1 CHARGEMENT RESEAU DISTRIBUTION EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 10 | 16416 | 9431 | 2 | EL1008_M194 | 6 | BITVAL
OVP6413C1 | WIS OVP 6413 FERMEE 1 DEPRESSURISATION/EVACUATION RESERVOIRS EST | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 12 | 16416 | 9431 | 4 | EL1008_M194 | 7 | BITVAL
OVP6414C1 | WIS OVP 6414 FERMEE 1 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17004 | 14 | 16416 | 9431 | 6 | EL1008_M194 | 8 | BITVAL
OVP6406C2 | WIS OVP 6406 FERMEE 2 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17005 | 0 | 16416 | 9432 | 0 | EL1008_M195 | 1 | BITVAL
OVP6407C2 | WIS OVP 6407 FERMEE 2 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17005 | 2 | 16416 | 9432 | 2 | EL1008_M195 | 2 | BITVAL
OVP6408C2 | WIS OVP 6408 FERMEE 2 VANNE ACTIONNEMENT OUEST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17005 | 4 | 16416 | 9432 | 4 | EL1008_M195 | 5 | BITVAL
OVP6414C2 | WIS OVP 6414 FERMEE 2 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17005 | 6 | 16416 | 9432 | 6 | EL1008_M195 | 4 | BITVAL
OVP6415C2 | WIS OVP 6415 FERMEE 2 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17005 | 8 | 16416 | 9433 | 0 | EL1008_M195 | 5 | BITVAL
OVP6416C2 | WIS OVP 6416 FERMEE 2 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17005 | 10 | 16416 | 9433 | 2 | EL1008_M195 | 6 | BITVAL
SPAREDI1 | WIS SPAREDI1 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17005 | 12 | 16416 | 9433 | 4 | EL1008_M195 |  | BITVAL
SPAREDI2 | WIS SPAREDI2 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17005 | 14 | 16416 | 9433 | 6 | EL1008_M195 |  | BITVAL
OVP6415O1 | WIS OVP 6415 OUVERTE 1 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 0 | 16416 | 9434 | 0 | EL1008_M196 | 1 | BITVAL
OVP6416O1 | WIS OVP 6416 OUVERTE 1 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 2 | 16416 | 9434 | 2 | EL1008_M196 | 2 | BITVAL
RVM6401O1 | WIS RVM 6401 OUVERTE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 4 | 16416 | 9434 | 4 | EL1008_M196 | 3 | BITVAL
RVM6402O1 | WIS RVM 6402 OUVERTE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 6 | 16416 | 9434 | 6 | EL1008_M196 | 4 | BITVAL
RVM6404O1 | WIS RVM 6404 OUVERTE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 8 | 16416 | 9435 | 0 | EL1008_M196 | 5 | BITVAL
RVM6406O1 | WIS RVM 6406 OUVERTE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 10 | 16416 | 9435 | 2 | EL1008_M196 | 6 | BITVAL
RVM6407O1 | WIS RVM 6407 OUVERTE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 12 | 16416 | 9435 | 4 | EL1008_M196 | 7 | BITVAL
RVM6409O1 | WIS RVM 6409 OUVERTE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17006 | 14 | 16416 | 9435 | 6 | EL1008_M196 | 8 | BITVAL
OVP6415C1 | WIS OVP 6415 FERMEE 1 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 0 | 16416 | 9436 | 0 | EL1008_M197 | 1 | BITVAL
OVP6416C1 | WIS OVP 6416 FERMEE 1 VANNE ACTIONNEMENT EST | CR | O | FIL | 1 | F | [26 empty] | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 2 | 16416 | 9436 | 2 | EL1008_M197 | 2 | BITVAL
RVM6401C1 | WIS RVM 6401 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 4 | 16416 | 9436 | 4 | EL1008_M197 | 3 | BITVAL
RVM6403C1 | WIS RVM 6403 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 6 | 16416 | 9436 | 6 | EL1008_M197 | 4 | BITVAL
RVM6404C1 | WIS RVM 6404 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 8 | 16416 | 9437 | 0 | EL1008_M197 | 5 | BITVAL
RVM6405C1 | WIS RVM 6405 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 10 | 16416 | 9437 | 2 | EL1008_M197 | 6 | BITVAL
RVM6406C1 | WIS RVM 6406 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 12 | 16416 | 9437 | 4 | EL1008_M197 | 7 | BITVAL
RVM6408C1 | WIS RVM 6408 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17007 | 14 | 16416 | 9437 | 6 | EL1008_M197 | 8 | BITVAL
RVP6401O1 | WIS RVP 6401 OUVERTE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17008 | 0 | 16416 | 9438 | 0 | EL1008_M198 | 1 | BITVAL
RVP6402O1 | WIS RVP 6402 OUVERTE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17008 | 2 | 16416 | 9438 | 2 | EL1008_M198 | 2 | BITVAL
SPAREDI3 | WIS SPAREDI3 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17008 | 4 | 16416 | 9438 | 4 | EL1008_M198 |  | BITVAL
SPAREDI4 | WIS SPAREDI4 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17008 | 6 | 16416 | 9438 | 6 | EL1008_M198 |  | BITVAL
SPAREDI5 | WIS SPAREDI5 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17008 | 8 | 16416 | 9439 | 0 | EL1008_M198 |  | BITVAL
SPAREDI6 | WIS SPAREDI6 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17008 | 10 | 16416 | 9439 | 2 | EL1008_M198 |  | BITVAL
SPAREDI7 | WIS SPAREDI7 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17008 | 12 | 16416 | 9439 | 4 | EL1008_M198 |  | BITVAL
SPAREDI8 | WIS SPAREDI8 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17008 | 14 | 16416 | 9439 | 6 | EL1008_M198 |  | BITVAL
RVM6409C1 | WIS RVM 6409 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17009 | 0 | 16416 | 9440 | 0 | EL1008_M199 | 1 | BITVAL
RVM6410C1 | WIS RVM 6410 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17009 | 2 | 16416 | 9440 | 2 | EL1008_M199 | 2 | BITVAL
RVP6401C1 | WIS RVP 6401 FERMEE 1 OR 800 - 1 OUEST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17009 | 4 | 16416 | 9440 | 4 | EL1008_M199 | 3 | BITVAL
RVP6402C1 | WIS RVP 6402 FERMEE 1 OR 800 - 2 EST COTE | CR | O | FIL | 1 | F | [26 empty] | POL | 1000 |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17009 | 6 | 16416 | 9440 | 6 | EL1008_M199 | 4 | BITVAL
SPAREDI9 | WIS SPAREDI9 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17009 | 8 | 16416 | 9441 | 0 | EL1008_M199 |  | BITVAL
SPAREDI10 | WIS SPAREDI10 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17009 | 10 | 16416 | 9441 | 2 | EL1008_M199 |  | BITVAL
SPAREDI11 | WIS SPAREDI11 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17009 | 12 | 16416 | 9441 | 4 | EL1008_M199 |  | BITVAL
SPAREDI12 | WIS SPAREDI12 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17009 | 14 | 16416 | 9441 | 6 | EL1008_M199 |  | BITVAL
ZJA6001 | WIS PLC Armed N | CR | N | FIL | 1 | Z | [26 empty] | NOT | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 17010 | 0 | 16416 | 9442 | 0 | EL1008_M200 | 1 | BITVAL
ZZC6001N | WIS H0Trigger Nominal | CR | N | FIL | 1 | Z | [26 empty] | NOT | 1000 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 17010 | 2 | 16416 | 9442 | 2 | EL1008_M200 | 2 | BITVAL
SPAREDI13 | WIS SPAREDI13 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17010 | 4 | 16416 | 9442 | 4 | EL1008_M200 |  | BITVAL
SPAREDI14 | WIS SPAREDI14 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17010 | 6 | 16416 | 9442 | 6 | EL1008_M200 |  | BITVAL
SPAREDI15 | WIS SPAREDI15 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17010 | 8 | 16416 | 9443 | 0 | EL1008_M200 |  | BITVAL
SPAREDI16 | WIS SPAREDI16 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17010 | 10 | 16416 | 9443 | 2 | EL1008_M200 |  | BITVAL
SPAREDI17 | WIS SPAREDI17 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17010 | 12 | 16416 | 9443 | 4 | EL1008_M200 |  | BITVAL
SPAREDI18 | WIS SPAREDI18 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17010 | 14 | 16416 | 9443 | 6 | EL1008_M200 |  | BITVAL
ZJA6002 | WIS PLC Armed C | CR | N | FIL | 1 | Z | [26 empty] | NOT | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 17011 | 0 | 16416 | 9444 | 0 | EL1008_M201 | 1 | BITVAL
ZZC6001R | WIS H0Trigger Redondant | CR | N | FIL | 1 | Z | [26 empty] | NOT | 1000 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 17011 | 2 | 16416 | 9444 | 2 | EL1008_M201 | 2 | BITVAL
SPAREDI19 | WIS SPAREDI19 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17011 | 4 | 16416 | 9444 | 4 | EL1008_M201 |  | BITVAL
SPAREDI20 | WIS SPAREDI20 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17011 | 6 | 16416 | 9444 | 6 | EL1008_M201 |  | BITVAL
SPAREDI21 | WIS SPAREDI21 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17011 | 8 | 16416 | 9445 | 0 | EL1008_M201 |  | BITVAL
SPAREDI22 | WIS SPAREDI22 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17011 | 10 | 16416 | 9445 | 2 | EL1008_M201 |  | BITVAL
SPAREDI23 | WIS SPAREDI23 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17011 | 12 | 16416 | 9445 | 4 | EL1008_M201 |  | BITVAL
SPAREDI24 | WIS SPAREDI24 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17011 | 14 | 16416 | 9445 | 6 | EL1008_M201 |  | BITVAL
SPAREDI25 | WIS SPAREDI25 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 0 | 16416 | 9446 | 0 | EL1008_M202 |  | BITVAL
SPAREDI26 | WIS SPAREDI26 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 2 | 16416 | 9446 | 2 | EL1008_M202 |  | BITVAL
SPAREDI27 | WIS SPAREDI27 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 4 | 16416 | 9446 | 4 | EL1008_M202 |  | BITVAL
SPAREDI28 | WIS SPAREDI28 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 6 | 16416 | 9446 | 6 | EL1008_M202 |  | BITVAL
SPAREDI29 | WIS SPAREDI29 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 8 | 16416 | 9447 | 0 | EL1008_M202 |  | BITVAL
SPAREDI30 | WIS SPAREDI30 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 10 | 16416 | 9447 | 2 | EL1008_M202 |  | BITVAL
SPAREDI31 | WIS SPAREDI31 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 12 | 16416 | 9447 | 4 | EL1008_M202 |  | BITVAL
SPAREDI32 | WIS SPAREDI32 | CR |  |  | 1 | [32 empty] | NEW | [5 empty] | 17012 | 14 | 16416 | 9447 | 6 | EL1008_M202 |  | BITVAL
ZCM6837P18 | SWITCH 2 BUNKER - ETAT PORT 18 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P19 | SWITCH 2 BUNKER - ETAT PORT 19 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P20 | SWITCH 2 BUNKER - ETAT PORT 20 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P21 | SWITCH 2 BUNKER - ETAT PORT 21 | MA | N | INT | 0 | Z | [9 empty] | x<>'up' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
OPR6401AI | WIS OPR 6401 MESURE PRESSION LIGNE OUEST OR 800 - 1 | MA | O | FIL | 1 | F |  |  |  |  | 0 | 16 | [16 empty] | FORM | 0,000002048x |  |  | POL | 6000 |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17108 | 0 | 16416 | 9638 | 0 | ELM3144_M205 | Ch1 Pin 1(+) - 2(-) | I32
ZCM6837P22 | SWITCH 2 BUNKER - ETAT PORT 22 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6837P23 | SWITCH 2 BUNKER - ETAT PORT 23 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
OPR6404AI | WIS OPR 6404 MESURE PRESSION LIGNE EST OR 800 - 2 | MA | O | FIL | 1 | F |  |  |  |  | 0 | 16 | [16 empty] | FORM | 0,000002048x |  |  | POL | 6000 |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17114 | 0 | 16416 | 9650 | 0 | ELM3144_M205 | Ch4 Pin 1(+) - 2(-) | I32
ZCM6837P24 | SWITCH 2 BUNKER - ETAT PORT 24 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Bunker (VMC02 popup) | VMC (Z)
ZCM6840F1 | SWITCH 1 PANDORA - ETAT FO PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840F2 | SWITCH 1 PANDORA - ETAT FO PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P1 | SWITCH 1 PANDORA - ETAT PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SPAREAI1 | WIS SPAREAI1 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17124 | 0 | 16416 | 9670 | 0 | ELM3144_M207 | Ch1 Pin 1(+) - 2(-) | I32
SPAREAI2 | WIS SPAREAI2 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17126 | 0 | 16416 | 9674 | 0 | ELM3144_M207 | Ch2 Pin 1(+) - 2(-) | I32
SPAREAI3 | WIS SPAREAI3 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17128 | 0 | 16416 | 9678 | 0 | ELM3144_M207 | Ch3 Pin 1(+) - 2(-) | I32
SPAREAI4 | WIS SPAREAI4 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17130 | 0 | 16416 | 9682 | 0 | ELM3144_M207 | Ch4 Pin 1(+) - 2(-) | I32
SPAREAI5 | WIS SPAREAI5 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17132 | 0 | 16416 | 9686 | 0 | ELM3144_M208 | Ch1 Pin 1(+) - 2(-) | I32
SPAREAI6 | WIS SPAREAI6 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17134 | 0 | 16416 | 9690 | 0 | ELM3144_M208 | Ch2 Pin 1(+) - 2(-) | I32
SPAREAI7 | WIS SPAREAI7 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17136 | 0 | 16416 | 9694 | 0 | ELM3144_M208 | Ch3 Pin 1(+) - 2(-) | I32
SPAREAI8 | WIS SPAREAI8 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17138 | 0 | 16416 | 9698 | 0 | ELM3144_M208 | Ch4 Pin 1(+) - 2(-) | I32
SPAREAI9 | WIS SPAREAI9 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17140 | 0 | 16416 | 9702 | 0 | ELM3144_M209 | Ch1 Pin 1(+) - 2(-) | I32
SPAREAI10 | WIS SPAREAI10 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17142 | 0 | 16416 | 9706 | 0 | ELM3144_M209 | Ch2 Pin 1(+) - 2(-) | I32
SPAREAI11 | WIS SPAREAI11 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17144 | 0 | 16416 | 9710 | 0 | ELM3144_M209 | Ch3 Pin 1(+) - 2(-) | I32
SPAREAI12 | WIS SPAREAI12 | MA | O | FIL | 1 | [32 empty] | NEW | [5 empty] | 17146 | 0 | 16416 | 9714 | 0 | ELM3144_M209 | Ch4 Pin 1(+) - 2(-) | I32
OVP6406CO | CMD WIS OVP 6406 OUVERTURE VANNE ACTIONNEMENT OUEST - U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 0 | 16416 | 10422 | 0 | EL2809_M210 | 6 | U8 | 1
OVP6407CO | CMD WIS OVP 6407 OUVERTURE VANNE ACTIONNEMENT OUEST - U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 2 | 16416 | 10422 | 2 | EL2809_M210 | 7 | U8 | 4
OVP6408CO | CMD WIS OVP 6408 OUVERTURE VANNE ACTIONNEMENT OUEST - U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 4 | 16416 | 10422 | 4 | EL2809_M210 | 8 | U8 | 16
OVP6414CO | CMD WIS OVP 6414 OUVERTURE VANNE ACTIONNEMENT EST - U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 6 | 16416 | 10422 | 6 | EL2809_M210 | 14 | U8 | 64
OVP6415CO | CMD WIS OVP 6415 OUVERTURE VANNE ACTIONNEMENT EST - U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 8 | 16416 | 10423 | 0 | EL2809_M210 | 15 | U8 | 1
OVP6416CO | CMD WIS OVP 6416 OUVERTURE VANNE ACTIONNEMENT EST - U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 10 | 16416 | 10423 | 2 | EL2809_M210 | 16 | U8 | 4
OVP6406CF | CMD WIS OVP 6406 FERMATURE VANNE ACTIONNEMENT OUEST - U8(2),FERMER(2) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 1 | 16416 | 10422 | 1 | EL2809_M211 | 3 | U8 | 2
OVP6407CF | CMD WIS OVP 6407 FERMATURE VANNE ACTIONNEMENT OUEST - U8(2),FERMER(8) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 3 | 16416 | 10422 | 3 | EL2809_M211 | 4 | U8 | 8
OVP6408CF | CMD WIS OVP 6408 FERMATURE VANNE ACTIONNEMENT OUEST - U8(2),FERMER(32) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 5 | 16416 | 10422 | 5 | EL2809_M211 | 5 | U8 | 32
OVP6414CF | CMD WIS OVP 6414 FERMATURE VANNE ACTIONNEMENT EST - U8(2),FERMER(128) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 7 | 16416 | 10422 | 7 | EL2809_M211 | 6 | U8 | 128
OVP6415CF | CMD WIS OVP 6415 FERMATURE VANNE ACTIONNEMENT EST - U8(2),FERMER(2) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 9 | 16416 | 10423 | 1 | EL2809_M211 | 7 | U8 | 2
OVP6416CF | CMD WIS OVP 6416 FERMATURE VANNE ACTIONNEMENT EST - U8(2),FERMER(8) | CT | O | FIL | 1 | F | [13 empty] | YES |  | 0.1 |  |  | ZJA6000 (OFF) | [7 empty] | NOT |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17500 | 11 | 16416 | 10423 | 3 | EL2809_M211 | 8 | U8 | 8
OVP6401CO | CMD WIS OVP6401 ISOLATION REDOND APPROVISION EAU OUEST - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 0 | 16416 | 10426 | 0 | EL2809_M210 | 1 | U8 | 1
OVP6401CF | CMD WIS OVP6401 ISOLATION REDOND APPROVISION EAU OUEST - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 1 | 16416 | 10426 | 1 | EL2809_M210 | 1 | U8 | 2
OVP6402CO | CMD WIS OVP6402 VIDANGE/DEPRESSURISATION OUEST - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 2 | 16416 | 10426 | 2 | EL2809_M210 | 2 | U8 | 4
OVP6402CF | CMD WIS OVP6402 VIDANGE/DEPRESSURISATION OUEST - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 3 | 16416 | 10426 | 3 | EL2809_M210 | 2 | U8 | 8
OVP6403CO | CMD WIS OVP6403 CHARGEMENT/PRESSUR DES RESERVOIRS OUEST - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 4 | 16416 | 10426 | 4 | EL2809_M210 | 3 | U8 | 16
OVP6403CF | CMD WIS OVP6403 CHARGEMENT/PRESSUR DES RESERVOIRS OUEST - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 5 | 16416 | 10426 | 5 | EL2809_M210 | 3 | U8 | 32
OVP6404CO | CMD WIS OVP6404 CHARGEMENT RESEAU DISTRIBUTION OUEST - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 6 | 16416 | 10426 | 6 | EL2809_M210 | 4 | U8 | 64
OVP6404CF | CMD WIS OVP6404 CHARGEMENT RESEAU DISTRIBUTION OUEST - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 7 | 16416 | 10426 | 7 | EL2809_M210 | 4 | U8 | 128
OVP6405CO | CMD WIS OVP 6405 DEPRESSUR/EVACUATION RESERVOIRS OUEST - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 8 | 16416 | 10427 | 0 | EL2809_M210 | 5 | U8 | 1
OVP6405CF | CMD WIS OVP 6405 DEPRESSUR/EVACUATION RESERVOIRS OUES - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 9 | 16416 | 10427 | 1 | EL2809_M210 | 5 | U8 | 2
OVP6409CO | CMD WIS OVP6409 ISOLATION REDONDANTE APPROVISIONNEMENT EST - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 10 | 16416 | 10427 | 2 | EL2809_M210 | 9 | U8 | 4
OVP6409CF | CMD WIS OVP6409 ISOLATION REDONDANTE APPROVISIONNEMENT EST- U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 11 | 16416 | 10427 | 3 | EL2809_M210 | 9 | U8 | 8
OVP6410CO | CMD WIS OVP6410 VIDANGE/DEPRESSUR EST - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 12 | 16416 | 10427 | 4 | EL2809_M210 | 10 | U8 | 16
OVP6410CF | CMD WIS OVP6410 VIDANGE/DEPRESSUR EST - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 13 | 16416 | 10427 | 5 | EL2809_M210 | 10 | U8 | 32
OVP6411CO | CMD WIS OVP6411 CHARGEMENT/ PRESSUR RESERVOIRS EST - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 14 | 16416 | 10427 | 6 | EL2809_M210 | 11 | U8 | 64
OVP6411CF | CMD WIS OVP6411 CHARGEMENT/ PRESSUR RESERVOIRS EST - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17502 | 15 | 16416 | 10427 | 7 | EL2809_M210 | 11 | U8 | 128
OVP6412CO | CMD WIS OVP 6412 OUVERTURE 1 CHARGEMENT RESEAU DISTRIBUTION EST - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 0 | 16416 | 10428 | 0 | EL2809_M210 | 12 | U8 | 1
OVP6412CF | CMD WIS OVP 6412 OUVERTURE 1 CHARGEMENT RESEAU DISTRIBUTION EST - U8(2),FERMER(2) / U8(2),OUVRIR(1) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 1 | 16416 | 10428 | 1 | EL2809_M210 | 12 | U8 | 2
OVP6413CO | CMD WIS OVP 6413 OUVERTURE 1 DEPRESSURISATION/EVACUATION RESERVOIRS EST - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 2 | 16416 | 10428 | 2 | EL2809_M210 | 13 | U8 | 4
OVP6413CF | CMD WIS OVP 6413 OUVERTURE 1 DEPRESSURISATION/EVACUATION RESERVOIRS EST - U8(2),FERMER(8) / U8(2),OUVRIR(4) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 3 | 16416 | 10428 | 3 | EL2809_M210 | 13 | U8 | 8
RVP6401CO | CMD WIS RVP 6401 OUVERTURE 1 OR 800 - 1 OUEST COTE - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 4 | 16416 | 10428 | 4 | EL2809_M211 | 1 | U8 | 16
RVP6401CF | CMD WIS RVP 6401 OUVERTURE 1 OR 800 - 1 OUEST COTE - U8(2),FERMER(32) / U8(2),OUVRIR(16) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 5 | 16416 | 10428 | 5 | EL2809_M211 | 1 | U8 | 32
RVP6402CO | CMD WIS RVP 6402 OUVERTURE 1 OR 800 - 2 EST COTE - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 6 | 16416 | 10428 | 6 | EL2809_M211 | 2 | U8 | 64
RVP6402CF | CMD WIS RVP 6402 OUVERTURE 1 OR 800 - 2 EST COTE - U8(2),FERMER(128) / U8(2),OUVRIR(64) | CT | O | FIL | 1 | F | [11 empty] | OFF |  |  | NF | [11 empty] | POL |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW | [5 empty] | 17503 | 7 | 16416 | 10428 | 7 | EL2809_M211 | 2 | U8 | 128
SPAREDO1 | WIS SPAREDO1 | CT | O | FIL | 1 | [38 empty] | 17503 | 8 | 16416 | 10429 | 0 | EL2809_M211 | 9 | U8 | 1
SPAREDO2 | WIS SPAREDO2 | CT | O | FIL | 1 | [38 empty] | 17503 | 10 | 16416 | 10429 | 2 | EL2809_M211 | 10 | U8 | 4
SPAREDO3 | WIS SPAREDO3 | CT | O | FIL | 1 | [38 empty] | 17503 | 12 | 16416 | 10429 | 4 | EL2809_M211 | 11 | U8 | 16
SPAREDO4 | WIS SPAREDO4 | CT | O | FIL | 1 | [38 empty] | 17503 | 14 | 16416 | 10429 | 6 | EL2809_M211 | 12 | U8 | 64
SPAREDO5 | WIS SPAREDO5 | CT | O | FIL | 1 | [38 empty] | 17504 | 0 | 16416 | 10430 | 0 | EL2809_M211 | 13 | U8 | 1
SPAREDO6 | WIS SPAREDO6 | CT | O | FIL | 1 | [38 empty] | 17504 | 2 | 16416 | 10430 | 2 | EL2809_M211 | 14 | U8 | 4
SPAREDO7 | WIS SPAREDO7 | CT | O | FIL | 1 | [38 empty] | 17504 | 4 | 16416 | 10430 | 4 | EL2809_M211 | 15 | U8 | 16
SPAREDO8 | WIS SPAREDO8 | CT | O | FIL | 1 | [38 empty] | 17504 | 6 | 16416 | 10430 | 6 | EL2809_M211 | 16 | U8 | 64
RESERVEDO1 | WIS RESERVEDDO1_Health_Status - U8(2),PLCNOTARMED(2) / U8(2),PLCARMED(1) | CT | O | FIL | 1 | [38 empty] | 17504 | 8 | 16416 | 10431 | 0 | EL2809_M212 | 1 | U8 | 1
RESERVEDO2 | WIS RESERVEDO2_PLC_Arm - U8(2),PLCNOTARMED(2) / U8(2),PLCARMED(1) | CT | O | FIL | 1 | [38 empty] | 17504 | 10 | 16416 | 10431 | 2 | EL2809_M212 | 2 | U8 | 4
RESERVEDO3 | WIS RESERVEDO3_PLC_H0_Triggered - U8(2),H0NOTTRIGGERED(32) / U8(2),H0TRIGGERED(16) | CT | O | FIL | 1 | [38 empty] | 17504 | 12 | 16416 | 10431 | 4 | EL2809_M212 | 3 | U8 | 16
RESERVEDO4 | WIS RESERVEDO4_CountDown_In_Progr - U8(2),PLCNOTARMED(2) / U8(2),PLCARMED(1) | CT | O | FIL | 1 | [38 empty] | 17504 | 14 | 16416 | 10431 | 6 | EL2809_M212 | 4 | U8 | 64
RESERVEDO5 | WIS RESERVEDDO5_Valves_Status - U8(2),PLCNOTARMED(2) / U8(2),PLCARMED(1) | CT | O | FIL | 1 | [38 empty] | 17505 | 0 | 16416 | 10432 | 0 | EL2809_M212 | 5 | U8 | 1
SPAREDO9 | WIS SPAREDO14 | CT | O | FIL | 1 | [38 empty] | 17505 | 2 | 16416 | 10432 | 2 | EL2809_M212 | 6 | U8 | 4
SPAREDO10 | WIS SPAREDO15 | CT | O | FIL | 1 | [38 empty] | 17505 | 4 | 16416 | 10432 | 4 | EL2809_M212 | 7 | U8 | 16
SPAREDO11 | WIS SPAREDO15 | CT | O | FIL | 1 | [38 empty] | 17505 | 6 | 16416 | 10432 | 6 | EL2809_M212 | 8 | U8 | 64
SPAREDO12 | WIS SPAREDO16 | CT | O | FIL | 1 | [38 empty] | 17505 | 8 | 16416 | 10433 | 0 | EL2809_M212 | 9 | U8 | 1
SPAREDO13 | WIS SPAREDO17 | CT | O | FIL | 1 | [38 empty] | 17505 | 10 | 16416 | 10433 | 2 | EL2809_M212 | 10 | U8 | 4
SPAREDO14 | WIS SPAREDO18 | CT | O | FIL | 1 | [38 empty] | 17505 | 12 | 16416 | 10433 | 4 | EL2809_M212 | 11 | U8 | 16
SPAREDO15 | WIS SPAREDO19 | CT | O | FIL | 1 | [38 empty] | 17505 | 14 | 16416 | 10433 | 6 | EL2809_M212 | 12 | U8 | 64
SPAREDO16 | WIS SPAREDO20 | CT | O | FIL | 1 | [38 empty] | 17506 | 0 | 16416 | 10434 | 0 | EL2809_M212 | 13 | U8 | 1
SPAREDO17 | WIS SPAREDO19 | CT | O | FIL | 1 | [38 empty] | 17506 | 2 | 16416 | 10434 | 2 | EL2809_M212 | 14 | U8 | 4
SPAREDO18 | WIS SPAREDO20 | CT | O | FIL | 1 | [38 empty] | 17506 | 4 | 16416 | 10434 | 4 | EL2809_M212 | 15 | U8 | 16
SPAREDO19 | WIS SPAREDO21 | CT | O | FIL | 1 | [38 empty] | 17506 | 6 | 16416 | 10434 | 6 | EL2809_M212 | 16 | U8 | 64
ZZZ6100EC10 | WIS VMC Front-End etat du module EK1100_EC10 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15179 | NA | 16416 | 5780 | NA | EK1100_EC10 |  | UINT
ZZZ6921M189 | WIS VMC API Front-End etat du module EL9221_M189 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15186 | NA | 16416 | 5794 | NA | EL9221_M189 |  | UINT
ZZZ6108M190 | WIS VMC API Front-End etat du module EL1008_M190 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15187 | NA | 16416 | 5796 | NA | EL1008_M190 |  | UINT
ZZZ6108M191 | WIS VMC API Front-End etat du module EL1008_M191 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15188 | NA | 16416 | 5798 | NA | EL1008_M191 |  | UINT
ZZZ6108M192 | WIS VMC API Front-End etat du module EL1008_M192 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15189 | NA | 16416 | 5800 | NA | EL1008_M192 |  | UINT
ZZZ6108M193 | WIS VMC API Front-End etat du module EL1008_M193 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15190 | NA | 16416 | 5802 | NA | EL1008_M193 |  | UINT
ZZZ6108M194 | WIS VMC API Front-End etat du module EL1008_M194 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15191 | NA | 16416 | 5804 | NA | EL1008_M194 |  | UINT
ZZZ6108M195 | WIS VMC API Front-End etat du module EL1008_M195 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15192 | NA | 16416 | 5806 | NA | EL1008_M195 |  | UINT
ZZZ6108M196 | WIS VMC API Front-End etat du module EL1008_M196 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15193 | NA | 16416 | 5808 | NA | EL1008_M196 |  | UINT
ZZZ6108M197 | WIS VMC API Front-End etat du module EL1008_M197 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15194 | NA | 16416 | 5810 | NA | EL1008_M197 |  | UINT
ZZZ6108M198 | WIS VMC API Front-End etat du module EL1008_M198 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15195 | NA | 16416 | 5812 | NA | EL1008_M198 |  | UINT
ZZZ6108M199 | WIS VMC API Front-End etat du module EL1008_M199 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15196 | NA | 16416 | 5814 | NA | EL1008_M199 |  | UINT
ZZZ6108M200 | WIS VMC API Front-End etat du module EL1008_M200 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15197 | NA | 16416 | 5816 | NA | EL1008_M200 |  | UINT
ZZZ6108M201 | WIS VMC API Front-End etat du module EL1008_M201 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15198 | NA | 16416 | 5818 | NA | EL1008_M201 |  | UINT
ZZZ6108M202 | WIS VMC API Front-End etat du module EL1008_M202 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15199 | NA | 16416 | 5820 | NA | EL1008_M202 |  | UINT
ZZZ6941M203 | WIS VMC API Front-End etat du module EL9410_M203 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 15181 | NA | 16416 | 5784 | NA | EL9410_M203 |  | UINT
ZZZ6314M204 | WIS VMC API Front-End etat du module ELM3144_M204 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16500 | NA | 16416 | 8422 | NA | ELM3144_M204 |  | UINT
ZZZ6314M205 | WIS VMC API Front-End etat du module ELM3144_M205 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16501 | NA | 16416 | 8424 | NA | ELM3144_M205 |  | UINT
ZZZ6314M206 | WIS VMC API Front-End etat du module ELM3144_M206 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16502 | NA | 16416 | 8426 | NA | ELM3144_M206 |  | UINT
ZZZ6314M207 | WIS VMC API Front-End etat du module ELM3144_M207 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16503 | NA | 16416 | 8428 | NA | ELM3144_M207 |  | UINT
ZZZ6314M208 | WIS VMC API Front-End etat du module ELM3144_M208 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16504 | NA | 16416 | 8430 | NA | ELM3144_M208 |  | UINT
ZZZ6314M209 | WIS VMC API Front-End etat du module ELM3144_M209 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16505 | NA | 16416 | 8432 | NA | ELM3144_M209 |  | UINT
ZZZ6289M210 | WIS VMC API Front-End etat du module EL2809_M210 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16506 | NA | 16416 | 8434 | NA | EL2809_M210 |  | UINT
ZZZ6289M211 | WIS VMC API Front-End etat du module EL2809_M211 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16507 | NA | 16416 | 8436 | NA | EL2809_M211 |  | UINT
ZZZ6289M212 | WIS VMC API Front-End etat du module EL2809_M212 | CR | N | INT | 1 | Z | [26 empty] | POL | 6000 |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW | [5 empty] | 16508 | NA | 16416 | 8438 | NA | EL2809_M212 |  | UINT
OVM6401DI | WIS OVM 6401 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6401C1;OVM6401O1 |  |  |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW
OVM6401AE | WIS OVM 6401 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6401C1;OVM6401O1 |  |  |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW
OVM6407DI | WIS OVM 6407 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6407C1;OVM6407O1 |  |  |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW
OVM6407AE | WIS OVM 6407 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6407C1;OVM6407O1 |  |  |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW
OVP6401DI | WIS OVP 6401 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6401;OVP6401 |  |  |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW
OVP6401AE | WIS OVP 6401 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6334F;OVM6334O |  |  |  |  | WIS03_WATER_WEST (1/2) | Water Injection System (WIS) | NEW
OVP6403DI | WIS OVP 6403 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVM6334F;OVM6334O |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6403AE | WIS OVP 6403 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVM6334F;OVM6334O |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6404DI | WIS OVP 6404 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6404C1;OVP6404O1 |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6404AE | WIS OVP 6404 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6404C1;OVP6404O1 |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6406DI | WIS OVP 6406 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6406C1 AND OVP6406C2 AND OVP6406O1) OR (!OVP6406C1 AND OVP6406C2 AND OVP6406O1) OR (OVP6406C1 AND !OVP6406C2 AND OVP6406O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6406AE | WIS OVP 6406 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6406C1;OVP6406C2;OVP6406O1 |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6406PF1 | WIS OVP 6406 Discordance - ABSENCE C1 OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6406C1 AND OVP6406C2 AND !OVP6406O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6406PF2 | WIS OVP 6406 Discordance - ABSENCE C2 OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6406C1 AND !OVP6406C2 AND !OVP6406O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6407DI | WIS OVP 6407 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6407C1 AND OVP6407C2 AND OVP6407O1) OR (!OVP6407C1 AND OVP6407C2 AND OVP6407O1) OR (OVP6407C1 AND !OVP6407C2 AND OVP6407O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6407AE | WIS OVP 6407 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6407C1;OVP6407C2;OVP6407O1 |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6407PF1 | WIS OVP 6407 Discordance - ABSENCE C1 OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6407C1 AND OVP6407C2 AND !OVP6407O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6407PF2 | WIS OVP 6407 Discordance - ABSENCE C2 OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6407C1 AND !OVP6407C2 AND !OVP6407O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6408DI | WIS OVP 6408 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6408C1 AND OVP6408C2 AND OVP6408O1) OR (!OVP6408C1 AND OVP6408C2 AND OVP6408O1) OR (OVP6408C1 AND !OVP64086C2 AND OVP6408O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6408AE | WIS OVP 6408 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6408C1;OVP6408C2;OVP6408O1 |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6408PF1 | WIS OVP 6408 Discordance - ABSENCE C1 OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6408C1 AND OVP6408C2 AND !OVP6408O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6408PF2 | WIS OVP 6408 Discordance - ABSENCE C2 OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6408C1 AND !OVP6408C2 AND !OVP6408O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6409DI | WIS OVP 6409 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6409C1;OVP6409O1 |  |  |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW
OVP6409AE | WIS OVP 6409Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6409C1;OVP6409O1 |  |  |  |  | WIS05_WATER_EST (1/2) | Water Injection System (WIS) | NEW
OVP6411DI | WIS OVP 6411 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6411C1;OVP6411O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6411AE | WIS OVP 6411 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6411C1;OVP6411O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6412DI | WIS OVP 6412 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6412C1;OVP6412O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6412AE | WIS OVP 6412 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | OVP6412C1;OVP6412O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6414DI | WIS OVP 6414 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6414C1 AND OVP6414C2 AND OVP6414O1) OR (!OVP6414C1 AND OVP6414C2 AND OVP6414O1) OR (OVP6414C1 AND !OVP6414C2 AND OVP6414O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6414AE | WIS OVP 6414 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6414C1;OVP6414C2;OVP6414O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6414PF1 | WIS OVP 6414 Discordance - ABSENCE C1 EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6414C1 AND OVP6414C2 AND !OVP6414O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6414PF2 | WIS OVP 6414 Discordance - ABSENCE C2 EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6414C1 AND !OVP6414C2 AND !OVP6414O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6415DI | WIS OVP 6415 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6415C1 AND OVP6415C2 AND OVP6415O1) OR (!OVP6415C1 AND OVP6415C2 AND OVP6415O1) OR (OVP6415C1 AND !OVP6415C2 AND OVP6415O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6415AE | WIS OVP 6415 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6415C1;OVP6415C2;OVP6415O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6415PF1 | WIS OVP 6415 Discordance - ABSENCE C1 EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6415C1 AND OVP6415C2 AND !OVP6415O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6415PF2 | WIS OVP 6415 Discordance - ABSENCE C2 EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6415C1 AND !OVP6415C2 AND !OVP6415O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6416DI | WIS OVP 6416 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6416C1 AND OVP6416C2 AND OVP6416O1) OR (!OVP6416C1 AND OVP6416C2 AND OVP6416O1) OR (OVP6416C1 AND !OVP6416C2 AND OVP6416O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6416AE | WIS OVP 6416 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | OVP6416C1;OVP6416C2;OVP6416O1 |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6416PF1 | WIS OVP 6416 Discordance - ABSENCE C1 EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6416C1 AND OVP6416C2 AND !OVP6416O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6416PF2 | WIS OVP 6416 Discordance - ABSENCE C2 EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6416C1 AND !OVP6416C2 AND !OVP6416O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
RVM6401DI | WIS RVM 6401 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | RVM6401C1;RVM6401O1 |  |  |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW
RVM6401AE | WIS RVM 6401 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | RVM6401C1;RVM6401O1 |  |  |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW
RVM6404DI | WIS RVM 6404 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | RVM6404C1;RVM6404O1 |  |  |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW
RVM6404AE | WIS RVM 6404 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | RVM6404C1;RVM6404O1 |  |  |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW
RVM6406DI | WIS RVM 6406 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | RVM6406C1;RVM6406O1 |  |  |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW
RVM6406AE | WIS RVM 6406 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | RVM6406C1;RVM6406O1 |  |  |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW
RVP6401DI | WIS RVP 6401 Discordance OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | RVP6401C1;RVP6401O1 |  |  |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW
RVP6401AE | WIS RVP 6401 Aucun Etat OUEST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | RVP6401C1;RVP6401O1 |  |  |  |  | WIS01_AIR_WEST | Water Injection System (WIS) | NEW
RVP6402DI | WIS RVP 6402 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | RVP6402C1;RVP6402O1 |  |  |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW
RVP6402AE | WIS RVP 6402 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | RVP6402C1;RVP6402O1 |  |  |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW
RVM6409DI | WIS RVM 6409 Discordance EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | RVM6409C1;RVM6409O1 |  |  |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW
RVM6409AE | WIS RVM 6409 Aucun Etat EST | CR | N | CAL | 1 | F | [22 empty] | NOR |  | RVM6409C1;RVM6409O1 |  |  |  |  | WIS02_AIR_EST | Water Injection System (WIS) | NEW
OVP6406O | WIS OVP 6406 OUVERTEOUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6406C1 AND !OVP6406C2 AND OVP6406O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6406C | WIS OVP 6406 FERMEE OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6406C1 AND OVP6406C2 AND !OVP6406O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6407O | WIS OVP 6407 OUVERTE OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6407C1 AND !OVP6407C2 AND OVP6407O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6407C | WIS OVP 6407 FERMEE OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6407C1 AND OVP6407C2 AND !OVP6407O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6408O | WIS OVP 6408 OUVERTE OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6408C1 AND !OVP6408C2 AND OVP6408O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6408C | WIS OVP 6408 FERMEE OUEST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6408C1 AND OVP6408C2 AND !OVP6408O1) |  |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
OVP6414O | WIS OVP 6414 OUVERTE EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6414C1 AND !OVP6414C2 AND OVP6414O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6414C | WIS OVP 6414 FERMEE EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6414C1 AND OVP6414C2 AND !OVP6414O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6415O | WIS OVP 6415 OUVERTE EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6415C1 AND !OVP6415C2 AND OVP6415O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6415C | WIS OVP 6415 FERMEE EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6415C1 AND OVP6415C2 AND !OVP6415O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6416O | WIS OVP 6416 OUVERTE EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (!OVP6416C1 AND !OVP6416C2 AND OVP6416O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
OVP6416C | WIS OVP 6416 FERMEE EST | CR | N | CAL | 1 | F | [22 empty] | AND |  | (OVP6416C1 AND OVP6416C2 AND !OVP6416O1) |  |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
ZCM6840P2 | SWITCH 1 PANDORA - ETAT PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P3 | SWITCH 1 PANDORA - ETAT PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P4 | SWITCH 1 PANDORA - ETAT PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
WISDMA | WIS ALARME SYNTHESE | AL | N | CAL | 1 | F | [24 empty] | WIS03DMA;WIS05DMA;ZJA6000 | Y |  |  |  |  | Water Injection System (WIS) | NEW
ZCM6840P5 | SWITCH 1 PANDORA - ETAT PORT 5 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZJA6000 | WIS API ARME | CR | N | INT | 1 | Z | [27 empty] | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12314 | 4 | 16416 | 50 | 4 | NA |  | BIT
ZZC6001M | WIS CCV2-C H0 ACQUITTE | CR | N | INT | 1 | Z | [27 empty] | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12314 | 6 | 16416 | 50 | 6 | NA |  | BIT
ZZC6002M | WIS DECOMPTE EN COURS | CR | N | INT | 1 | Z | [27 empty] | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12314 | 8 | 16416 | 51 | 0 | NA |  | BIT
ZZC6000M | WIS SEQUENCE TERMINE | CR | N | INT | 1 | Z | [27 empty] | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12314 | 10 | 16416 | 51 | 2 | NA |  | BIT
ZZC6003O | WIS ETAT DES VANNES | CR | N | INT | 1 | F;Z | [27 empty] | 1000 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12314 | 12 | 16416 | 51 | 4 | NA |  | BIT
ZZC6000CM | CMD WIS ACTIVATION MANUELLE SEQUENCE OUEST - U8(2),OUVRIR(1) | CT | N | INT | 1 | F | [13 empty] | YES |  |  |  |  | ZJA6000 (OFF) | [10 empty] | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17516 | 1 | 16416 | 10454 | 0 | NA |  | U8 | 1
ZZC6001CM | CMD WIS ACTIVATION MANUELLE SEQUENCE EST - U8(2),OUVRIR(2) | CT | N | INT | 1 | F | [13 empty] | YES |  |  |  |  | ZJA6000 (OFF) | [10 empty] | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17516 | 1 | 16416 | 10454 | 1 | NA |  | U8 | 2
ZZC6002CO | CMD WIS BON ETAT - U8(2),OK(2) | CT | N | INT | 1 | Z | [31 empty] | NEW | [5 empty] | 17515 | 1 | 16416 | 10452 | 1 | NA |  | U8 | 2
ZZC6002CN | CMD WIS BON ETAT - U8(2),NOK(1) | CT | N | INT | 1 | Z | [31 empty] | NEW | [5 empty] | 17515 | 0 | 16416 | 10452 | 0 | NA |  | U8 | 1
ZZC6006M | WIS ANALOG MEASURES IN NOMINAL STATUS | MA | N | CAL | 1 | F | [22 empty] | AND |  | ONR6401AI >780 AND ONR6401AI < 975 AND ONR6402AI >780 AND ONR6402AI < 975 AND ONR6403AI >780 AND ONR6403AI < 975 AND ONR6404AI >780 AND ONR6404AI < 975 AND OPR6402AI >5,35 AND OPR6402AI < 5,65 AND OPR6403AI >5,35 AND OPR6403AI < 5,65 AND OPR6405AI >5 AND OPR6405AI < 5,3 AND OPR6406AI >5 AND OPR6406AI < 5,3 AND OPR6407AI >0,19 AND OPR6408AI >0,19
ZZC6003M | WIS Sequence Automatic compte à rebours | MA | N | INT | 1 | Z | [26 empty] | NOT | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12320 | 0 | 16416 | 62 | 0 |  |  | STRING(12)
SZI7283D | Defaut Newton Local Circulation 00 - ZDA83 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 0 | [7 empty] | BITVAL
ZCM6840P6 | SWITCH 1 PANDORA - ETAT PORT 6 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SZI7284D | Defaut Newton Local technique Courant faibles 11 - ZDA84 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 4 | [7 empty] | BITVAL
ZCM6840P7 | SWITCH 1 PANDORA - ETAT PORT 7 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SZI7285D | Defaut Newton Local Climatisation 08 - ZDA85 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 8 | [7 empty] | BITVAL
ZCM6840P8 | SWITCH 1 PANDORA - ETAT PORT 8 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SZI7286D | Defaut Newton Bureau 09 – ZDA86 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 12 | [7 empty] | BITVAL
ZCM6840P9 | SWITCH 1 PANDORA - ETAT PORT 9 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SZI7287D | Defaut Newton Local énergie 10 – ZDA87 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1042 | 0 | [7 empty] | BITVAL
ZCM6840P10 | SWITCH 1 PANDORA - ETAT PORT 10 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SZI7288D | Defaut Newton Open space B 13 – ZDA88 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1042 | 4 | [7 empty] | BITVAL
ZCM6840P11 | SWITCH 1 PANDORA - ETAT PORT 11 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SZI7289D | Defaut Newton Open space A 14 – ZDA89 | CR | N | RES | 2 | S | [26 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1042 | 8 | [7 empty] | BITVAL
ZCM6840P12 | SWITCH 1 PANDORA - ETAT PORT 12 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P13 | SWITCH 1 PANDORA - ETAT PORT 13 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P14 | SWITCH 1 PANDORA - ETAT PORT 14 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P15 | SWITCH 1 PANDORA - ETAT PORT 15 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ESA8001 | Pandora - Synthèse Contacts OF TD TGBT CAT.2 | CR | O | FIL | 3 | E | [26 empty] | MTCP |  |  | E80 | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12339 | 4 | 16416 | 100 | 4 | EL1018_M002 | 3 | BITVAL
ZCM6840P16 | SWITCH 1 PANDORA - ETAT PORT 16 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ESA8002 | Pandora - Synthèse Contacts OF TD Cat. 2 | CR | O | FIL | 3 | E | [26 empty] | MTCP |  |  | E80 | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12339 | 8 | 16416 | 102 | 0 | EL1018_M002 | 5 | BITVAL
ZCM6840P17 | SWITCH 1 PANDORA - ETAT PORT 17 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P18 | SWITCH 1 PANDORA - ETAT PORT 18 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P19 | SWITCH 1 PANDORA - ETAT PORT 19 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P20 | SWITCH 1 PANDORA - ETAT PORT 20 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P21 | SWITCH 1 PANDORA - ETAT PORT 21 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P22 | SWITCH 1 PANDORA - ETAT PORT 22 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6840P23 | SWITCH 1 PANDORA - ETAT PORT 23 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ESA8003 | Pandora - Synthèse Contacts OF TGBT Cat. 3A | CR | O | FIL | 3 | E | [26 empty] | MTCP |  |  | E80 | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12340 | 8 | 16416 | 106 | 0 | EL1018_M003 | 5 | BITVAL
ZCM6840P24 | SWITCH 1 PANDORA - ETAT PORT 24 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ESA8004 | Pandora - Synthèse Contacts OF TD Cat. 3A | CR | O | FIL | 3 | E | [26 empty] | MTCP |  |  | E80 | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12340 | 12 | 16416 | 106 | 4 | EL1018_M003 | 7 | BITVAL
ZCM6841F1 | SWITCH 2 PANDORA - ETAT FO PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ESA8005 | Pandora - Synthèse Contacts OF TD Cat. 3B | CR | O | FIL | 3 | E | [26 empty] | MTCP |  |  | E80 | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12341 | 0 | 16416 | 108 | 0 | EL1018_M004 | 1 | BITVAL
ZCM6841F2 | SWITCH 2 PANDORA - ETAT FO PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ESA8006 | Pandora - Synthèse Contacts OF TGBT Cat. 3B | CR | O | FIL | 3 | E | [26 empty] | MTCP |  |  | E80 | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12341 | 4 | 16416 | 108 | 4 | EL1018_M004 | 3 | BITVAL
ZCM6841P1 | SWITCH 2 PANDORA - ETAT PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P2 | SWITCH 2 PANDORA - ETAT PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P3 | SWITCH 2 PANDORA - ETAT PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P4 | SWITCH 2 PANDORA - ETAT PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P5 | SWITCH 2 PANDORA - ETAT PORT 5 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P6 | SWITCH 2 PANDORA - ETAT PORT 6 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
SPARE | PAN DI SPARE01 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 2 | 16416 | 112 | 2 | EL1018_M005 | 2 | BITVAL
SPARE | PAN DI SPARE02 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 4 | 16416 | 112 | 4 | EL1018_M005 | 3 | BITVAL
SPARE | PAN DI SPARE03 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 6 | 16416 | 112 | 6 | EL1018_M005 | 4 | BITVAL
SPARE | PAN DI SPARE04 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 8 | 16416 | 114 | 0 | EL1018_M005 | 5 | BITVAL
SPARE | PAN DI SPARE05 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 10 | 16416 | 114 | 2 | EL1018_M005 | 6 | BITVAL
SPARE | PAN DI SPARE06 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 12 | 16416 | 114 | 4 | EL1018_M005 | 7 | BITVAL
SPARE | PAN DI SPARE07 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12342 | 14 | 16416 | 114 | 6 | EL1018_M005 | 8 | BITVAL
SPARE | PAN DI SPARE08 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 0 | 16416 | 116 | 0 | EL1018_M006 | 1 | BITVAL
SPARE | PAN DI SPARE09 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 2 | 16416 | 116 | 2 | EL1018_M006 | 2 | BITVAL
SPARE | PAN DI SPARE010 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 4 | 16416 | 116 | 4 | EL1018_M006 | 3 | BITVAL
SPARE | PAN DI SPARE011 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 6 | 16416 | 116 | 6 | EL1018_M006 | 4 | BITVAL
SPARE | PAN DI SPARE012 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 8 | 16416 | 118 | 0 | EL1018_M006 | 5 | BITVAL
SPARE | PAN DI SPARE013 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 10 | 16416 | 118 | 2 | EL1018_M006 | 6 | BITVAL
SPARE | PAN DI SPARE014 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 12 | 16416 | 118 | 4 | EL1018_M006 | 7 | BITVAL
SPARE | PAN DI SPARE015 | CR | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12343 | 14 | 16416 | 118 | 6 | EL1018_M006 | 8 | BITVAL
VTR8001T | Pandora - Température local Telecom/CFS/Banc controle | MA | O | FIL | 3 | C | [26 empty] | MTCP |  |  | HVAC24 | HVAC (Pandora) | PANDORA | 11 |  |  | NA | NA | 12789 | 0 | 16416 | 1000 | 0 | ELM3144_M008 | Ch1 Pin 1(+) - 2(-) | I32
VTR8002T | Pandora - Température local énergie | MA | O | FIL | 3 | C | [26 empty] | MTCP |  |  | HVAC24 | HVAC (Pandora) | PANDORA | 11 |  |  | NA | NA | 12791 | 0 | 16416 | 1004 | 0 | ELM3144_M008 | Ch2 Pin 1(+) - 2(-) | I32
VTR8003T | Pandora - Température Sale d'opérations | MA | O | FIL | 3 | C | [26 empty] | MTCP |  |  | HVAC24 | HVAC (Pandora) | PANDORA | 11 |  |  | NA | NA | 12793 | 0 | 16416 | 1008 | 0 | ELM3144_M008 | Ch3 Pin 1(+) - 2(-) | I32
SPARE | PAN AI SPARE01 | MA | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12795 | 0 | 16416 | 1012 | 0 | ELM3144_M008 | Ch4 Pin 1(+) - 2(-) | I32
SPARE | PAN AI SPARE02 | MA | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12797 | 0 | 16416 | 1016 | 0 | ELM3144_M009 | Ch1 Pin 1(+) - 2(-) | I32
SPARE | PAN AI SPARE03 | MA | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12799 | 0 | 16416 | 1020 | 0 | ELM3144_M009 | Ch2 Pin 1(+) - 2(-) | I32
SPARE | PAN AI SPARE04 | MA | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12801 | 0 | 16416 | 1024 | 0 | ELM3144_M009 | Ch3 Pin 1(+) - 2(-) | I32
SPARE | PAN AI SPARE05 | MA | O | FIL | 3 | [27 empty] | MTCP |  |  |  | Energie (Pandora) | PANDORA | 11 |  |  | NA | NA | 12803 | 0 | 16416 | 1028 | 0 | ELM3144_M009 | Ch4 Pin 1(+) - 2(-) | I32
SZC8237 | Pandora - NK8237 Watchdog | MA | N | RES | 3 | S |  |  |  |  | 0 | 65535 | [20 empty] | MTCP |  |  | PANDORA Etat Centrale DI | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1010 | 0 | 14289 | 0 | 16416 | 4000 | 0 | EL6021_M11 |  | U16
SZC8020 | Pandora - FC2020 Watchdog | MA | N | RES | 3 | S |  |  |  |  | 0 | 65535 | [20 empty] | MTCP |  |  | PANDORA Etat Centrale DI | Detection Incendie (DI-Pandora) | PANDORA | 11 |  |  | 1010 | 0 | 14290 | 0 | 16416 | 4002 | 0 | EL6021_M11 |  | U16
ZCM6841P7 | SWITCH 2 PANDORA - ETAT PORT 7 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P8 | SWITCH 2 PANDORA - ETAT PORT 8 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P9 | SWITCH 2 PANDORA - ETAT PORT 9 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P10 | SWITCH 2 PANDORA - ETAT PORT 10 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P11 | SWITCH 2 PANDORA - ETAT PORT 11 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P12 | SWITCH 2 PANDORA - ETAT PORT 12 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P13 | SWITCH 2 PANDORA - ETAT PORT 13 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P14 | SWITCH 2 PANDORA - ETAT PORT 14 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P15 | SWITCH 2 PANDORA - ETAT PORT 15 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P16 | SWITCH 2 PANDORA - ETAT PORT 16 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P17 | SWITCH 2 PANDORA - ETAT PORT 17 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P18 | SWITCH 2 PANDORA - ETAT PORT 18 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P19 | SWITCH 2 PANDORA - ETAT PORT 19 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P20 | SWITCH 2 PANDORA - ETAT PORT 20 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P21 | SWITCH 2 PANDORA - ETAT PORT 21 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P22 | SWITCH 2 PANDORA - ETAT PORT 22 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P23 | SWITCH 2 PANDORA - ETAT PORT 23 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6841P24 | SWITCH 2 PANDORA - ETAT PORT 24 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Pandora (VMC02 popup) | VMC (Z)
ZCM6734F1 | SWITCH 1 LAGRANGE - ETAT FO PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734F2 | SWITCH 1 LAGRANGE - ETAT FO PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734F3 | SWITCH 1 LAGRANGE - ETAT FO PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734F4 | SWITCH 1 LAGRANGE - ETAT FO PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P1 | SWITCH 1 LAGRANGE - ETAT PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P2 | SWITCH 1 LAGRANGE - ETAT PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P3 | SWITCH 1 LAGRANGE - ETAT PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P4 | SWITCH 1 LAGRANGE - ETAT PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P5 | SWITCH 1 LAGRANGE - ETAT PORT 5 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P6 | SWITCH 1 LAGRANGE - ETAT PORT 6 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P7 | SWITCH 1 LAGRANGE - ETAT PORT 7 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P8 | SWITCH 1 LAGRANGE - ETAT PORT 8 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P9 | SWITCH 1 LAGRANGE - ETAT PORT 9 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P10 | SWITCH 1 LAGRANGE - ETAT PORT 10 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P11 | SWITCH 1 LAGRANGE - ETAT PORT 11 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P12 | SWITCH 1 LAGRANGE - ETAT PORT 12 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P13 | SWITCH 1 LAGRANGE - ETAT PORT 13 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P14 | SWITCH 1 LAGRANGE - ETAT PORT 14 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P15 | SWITCH 1 LAGRANGE - ETAT PORT 15 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P16 | SWITCH 1 LAGRANGE - ETAT PORT 16 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P17 | SWITCH 1 LAGRANGE - ETAT PORT 17 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P18 | SWITCH 1 LAGRANGE - ETAT PORT 18 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P19 | SWITCH 1 LAGRANGE - ETAT PORT 19 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P20 | SWITCH 1 LAGRANGE - ETAT PORT 20 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P21 | SWITCH 1 LAGRANGE - ETAT PORT 21 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P22 | SWITCH 1 LAGRANGE - ETAT PORT 22 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P23 | SWITCH 1 LAGRANGE - ETAT PORT 23 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6734P24 | SWITCH 1 LAGRANGE - ETAT PORT 24 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735F1 | SWITCH 2 LAGRANGE - ETAT FO PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735F2 | SWITCH 2 LAGRANGE - ETAT FO PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735F3 | SWITCH 2 LAGRANGE - ETAT FO PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735F4 | SWITCH 2 LAGRANGE - ETAT FO PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P1 | SWITCH 2 LAGRANGE - ETAT PORT 1 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P2 | SWITCH 2 LAGRANGE - ETAT PORT 2 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P3 | SWITCH 2 LAGRANGE - ETAT PORT 3 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P4 | SWITCH 2 LAGRANGE - ETAT PORT 4 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P5 | SWITCH 2 LAGRANGE - ETAT PORT 5 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P6 | SWITCH 2 LAGRANGE - ETAT PORT 6 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P7 | SWITCH 2 LAGRANGE - ETAT PORT 7 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P8 | SWITCH 2 LAGRANGE - ETAT PORT 8 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P9 | SWITCH 2 LAGRANGE - ETAT PORT 9 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P10 | SWITCH 2 LAGRANGE - ETAT PORT 10 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P11 | SWITCH 2 LAGRANGE - ETAT PORT 11 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P12 | SWITCH 2 LAGRANGE - ETAT PORT 12 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P13 | SWITCH 2 LAGRANGE - ETAT PORT 13 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P14 | SWITCH 2 LAGRANGE - ETAT PORT 14 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P15 | SWITCH 2 LAGRANGE - ETAT PORT 15 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P16 | SWITCH 2 LAGRANGE - ETAT PORT 16 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P17 | SWITCH 2 LAGRANGE - ETAT PORT 17 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P18 | SWITCH 2 LAGRANGE - ETAT PORT 18 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P19 | SWITCH 2 LAGRANGE - ETAT PORT 19 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P20 | SWITCH 2 LAGRANGE - ETAT PORT 20 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P21 | SWITCH 2 LAGRANGE - ETAT PORT 21 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P22 | SWITCH 2 LAGRANGE - ETAT PORT 22 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P23 | SWITCH 2 LAGRANGE - ETAT PORT 23 | MA | N | INT | 0 | Z | [9 empty] | x<>'UP' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
ZCM6735P24 | SWITCH 2 LAGRANGE - ETAT PORT 24 | MA | N | INT | 0 | Z | [9 empty] | x<>'down' |  |  | Z | [16 empty] | Switch Lagrange (VMC02 popup) | VMC (Z)
VCN7005D1 | AC 1 SALLE 05 LAGRANGE GENERAL FAULT | MA | N | RES | 2 | C | [9 empty] | x<>'No Alarm' |  |  | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1401 | NA | [7 empty] | UINT
VTR7005A1 | AC 1 SALLE 05 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1402 | NA | [7 empty] | INT
VCN7005M201 | AC 1 SALLE 05 LAGRANGE MEASURE SET POINT TEMPERATURE | MA | N | RES | 2 | C |  |  | °C | 0.1 | 170 | 350 |  |  |  | (x<>25)&&(x<>27) |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1392 | NA | [7 empty] | INT
VTR7010V1 | VC 1 SALLE 10 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1404 | NA | [7 empty] | INT
VVV7010M201 | VC 1 SALLE 10 LAGRANGE MEASURE SET POINT TEMPERATURE | MA | N | RES | 2 | C |  |  | °C | 0.1 | 120 | 330 |  |  |  | (x<>25)&&(x<>27) |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1393 | NA | [7 empty] | INT
VVV7013D1 | VC 1 SALLE 13 LAGRANGE GENERAL FAULT | MA | N | RES | 2 | C | [9 empty] | x=='Alarm' |  |  | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1406 | NA | [7 empty] | INT
VTR7013V1 | VC 1 SALLE 13 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.01 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1407 | NA | [7 empty] | INT
VVV7013M201 | VC 1 SALLE 13 LAGRANGE MEASURE SET POINT TEMPERATURE | MA | N | RES | 2 | C |  |  | °C | 1 | 120 | 330 |  |  |  | (x<>25)&&(x<>27) |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1394 | NA | [7 empty] | INT
VCN7005D2 | AC 2 SALLE 05 LAGRANGE GENERAL FAULT | MA | N | RES | 2 | C | [9 empty] | x=='Alarm' |  |  | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1409 | NA | [7 empty] | INT
VTR7005A2 | AC 2 SALLE 05 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1410 | NA | [7 empty] | INT
VCN7005M202 | AC 2 SALLE 05 LAGRANGE MEASURE SET POINT TEMPERATURE | MA | N | RES | 2 | C |  |  | °C | 0.1 | [5 empty] | (x<>25)&&(x<>27) |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1396 | NA | [7 empty] | INT
VTR7010V2 | VC 2 SALLE 10 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.1 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1412 | NA | [7 empty] | INT
VVV7010M202 | VC 2 SALLE 10 LAGRANGE MEASURE SET POINT TEMPERATURE | MA | N | RES | 2 | C |  |  | °C | 0.1 | 120 | 330 |  |  |  | (x<>25)&&(x<>27) |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1397 | NA | [7 empty] | INT
VVV7013D2 | VC 2 SALLE 13 LAGRANGE GENERAL FAULT | MA | N | RES | 2 | C | [9 empty] | x=='Alarm' |  |  | C | [13 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1414 | NA | [7 empty] | INT
VTR7013V2 | VC 2 SALLE 13 LAGRANGE TEMPERATURE | MA | N | RES | 2 | C |  | K | °C | 0.01 | 0 | 1000 |  |  | 23 | 27 |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1415 | NA | [7 empty] | INT
VVV7013M202 | VC 2 SALLE 13 LAGRANGE MEASURE SET POINT TEMPERATURE | MA | N | RES | 2 | C |  |  | °C | 1 | 120 | 330 |  |  |  | (x<>25)&&(x<>27) |  |  | C | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | HVAC19 | HVAC (C) | LGRNG | 9 |  |  | 1398 | NA | [7 empty] | INT
EFR7071 | Lagrange UPS A Output Frequency | MA | N | RES | 2 | E |  |  | Hz | 0.1 | 0 | 999 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS A (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1680 | NA | [7 empty] | UINT
EFR7072 | Lagrange UPS B Output Frequency | MA | N | RES | 2 | E |  |  | Hz | 0.1 | 0 | 999 |  |  | 49 | 61 |  |  | E | [6 empty] | 1 | 0 | [5 empty] | MTCP | 2000 |  | Infos Lagrange UPS B (E73 popup) | Energy Lagrange (E) | LGRNG | 9 |  |  | 1696 | NA | [7 empty] | UINT
VMC_001_INT | INPUT_Heartbeat_Physical_Channel |  |  | INT | 0 | Z | [12 empty] | Z | [24 empty] | 12838 | 0 | 16416 | 1098 | 0 | EL1809_M186 | 1 | BITVAL
VMC_002_INT | MODE_IN_Operating_Mode_Physical_Channel |  |  | INT | 0 | Z | [12 empty] | Z | [24 empty] | 12838 | 2 | 16416 | 1098 | 2 | EL1809_M186 | 2 | BITVAL
VCF7000COGC | CMDE REARMEMENT HVAC LAGRANGE | CT | N | INT | 2 | C |  |  |  |  | 0 | [7 empty] | C |  |  |  | VCF7000CO;VRU7232CO;VRU7120CO | [12 empty] | HVAC23 | HVAC (C)
SCX7001CMGC | CMDE MARCHE EXTI UPS BATT | CT | N | INT | 2 | S |  |  |  |  | 0 | [7 empty] | S | NO |  |  | SCX7001CM;VRU7232CF;VRU7120CF | [12 empty] | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI)
SCX7002CMGC | CMDE MARCHE EXTI TECH LAU | CT | N | INT | 2 | S | [12 empty] | S | NO |  |  | SCX7002CM;VRU7232CF;VRU7120CF | [12 empty] | E77 (EXTIN Lagrange Group) | Extinction Incendie (EI)
SCE6002CMGC | CMDE MARCHE ALERTE REPLI ZLV ET SONO | CT | N | INT | 1 | S | [12 empty] | S |  |  |  | SCE6002CM;SZP6014CM | [12 empty] | DG60 | Detection Gaz (DG)
SCE6002CAGC | CMDE ARRET ALERTE REPLI ZLV ET SONO | CT | N | INT | 1 | S | [12 empty] | S |  |  |  | SCE6012CM;SZP6014CA | [12 empty] | DG60 | Detection Gaz (DG)
ZJG6104 | DETG_DI Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | DG60 | Detection Gaz (DG) | NEW | 0 |  |  |  |  | 12315 | 0 | 16416 | 52 | 0 |  |  | BITVAL
ZJG6105 | OV Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | W60 Etat PLC OeV | Optique et Video VEGA (W) | NEW | 0 |  |  |  |  | 12315 | 1 | 16416 | 52 | 2 |  |  | BITVAL
ZJG6106 | WIRE Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | VG10 | Process Fluid et Energie General (VG) | NEW | 0 |  |  |  |  | 12315 | 2 | 16416 | 52 | 4 |  |  | BITVAL
ZJG6107 | TGBT Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | E60 | Energy TGBT et USP (E) | NEW | 0 |  |  |  |  | 12315 | 3 | 16416 | 52 | 6 |  |  | BITVAL
ZJG6108 | 1D60 Watchdog TimeOut | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | E72 | Energy 1D60 (E) | NEW | 0 |  |  |  |  | 12315 | 4 | 16416 | 53 | 0 |  |  | BITVAL
ZJG6109 | Bunker Watchdog TimeOut_1 | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | CV0B X80 HVAC Bunker PLC | HVAC (C) | NEW | 0 |  |  |  |  | 12315 | 5 | 16416 | 53 | 2 |  |  | BITVAL
ZJG6110 | Bunker Watchdog TimeOut_2 | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | CV0B X80 HVAC Bunker PLC | HVAC (C) | NEW | 0 |  |  |  |  | 12315 | 6 | 16416 | 53 | 4 |  |  | BITVAL
ZJG6111 | Gantry Watchdog TimeOut_1 | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | CV0B X80 HVAC Gantry PLC | HVAC (C) | NEW | 0 |  |  |  |  | 12315 | 7 | 16416 | 53 | 6 |  |  | BITVAL
ZJG6112 | Gantry Watchdog TimeOut_2 | AL | N | INT | 0 | A |  | U | [7 empty] | x==1 |  |  | A | [13 empty] | NOT | 5000 |  | CV0B X80 HVAC Gantry PLC | HVAC (C) | NEW | 0 |  |  |  |  | 12316 | 8 | 16416 | 54 | 0 |  |  | BITVAL
ECN7000W | GE-184.GE.00.01 - General fault | AL | N | TIP | 2 | E |  | E | [8 empty] | 1 |  | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 13 | NA | [7 empty] | BOOL
EKM7000W | GE-184.GE.00.01 -ECU – Alarm Level 1 | AL | N | TIP | 2 | E | [10 empty] | 1 |  | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 17 | NA | [7 empty] | BOOL
EKM7001W | GE-184.GE.00.01 -ECU – Alarm Level 2 | AL | N | TIP | 2 | E | [10 empty] | 1 |  | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 18 | NA | [7 empty] | BOOL
EWR7184R | GE-184.GE.00.01 - Total Real Power R | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 1 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1021 | NA | [7 empty] | I16
EFR7184 | GE-184.GE.00.01 - Frequency | MA | N | TIP | 2 | E |  |  |  | 0.1 | [8 empty] | E | [6 empty] | 1 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1037 | NA | [7 empty] | U16
EUR7184V1 | GE-184.GE.00.01 - Phase voltage 1 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 3 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1038 | NA | [7 empty] | U16
EUR7184V2 | GE-184.GE.00.01 - Phase voltage 2 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 3 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1039 | NA | [7 empty] | U16
EUR7184V3 | GE-184.GE.00.01 - Phase voltage 3 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 3 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1040 | NA | [7 empty] | U16
EUR718412 | GE-184.GE.00.01 - line to line voltage 1 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 3 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1041 | NA | [7 empty] | U16
EUR718423 | GE-184.GE.00.01 - line to line voltage 2 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 3 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1042 | NA | [7 empty] | U16
EUR718413 | GE-184.GE.00.01 - line to line voltage 3 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 3 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1043 | NA | [7 empty] | U16
EIR7184I1 | GE-184.GE.00.01 - Phase currents I1 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 1 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1044 | NA | [7 empty] | U16
EIR7184I2 | GE-184.GE.00.01 - Phase currents I2 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 1 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1045 | NA | [7 empty] | U16
EIR7184I3 | GE-184.GE.00.01 - Phase currents I3 | MA | N | TIP | 2 | E | [12 empty] | E | [6 empty] | 1 | 0 | [5 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1046 | NA | [7 empty] | U16
EUR7184UB | GE-184.GE.00.01 - Battery Tension | MA | N | TIP | 2 | E |  |  |  | 0.1 | [8 empty] | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1055 | NA | [7 empty] | I16
EKM7002 | GE-184.GE.00.01 - fuel level | MA | N | TIP | 2 | E | [12 empty] | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1059 | NA | [7 empty] | I16
EKM7000 | GE-184.GE.00.01 - Engine status | MA | N | TIP | 2 | E | [12 empty] | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1307 | NA | [7 empty] | U16
EKM7003 | GE-184.GE.00.01 - Alarm status | MA | N | TIP | 2 | E | [12 empty] | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1358 | NA | [7 empty] | U16
EKM7001 | GE-184.GE.00.01 - operation mode | MA | N | TIP | 2 | E | [12 empty] | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 1395 | NA | [7 empty] | U16
EKM7000C | CMD-184.GE.00.01 - operation mode | CT | N | TIP | 2 | E | [12 empty] | E | [13 empty] | MTCP |  |  | GE01 | Energy Lagrange (E) | NEW | 10 |  |  | 3022 | NA | [7 empty] | U16
ONR6401AI | WIS ONR 6401 MESURE NIVEAU RESEVOIR OUEST OTR 101 | MA | O | FIL | 1 | F |  | 8 | mm |  | 50 | 2096 |  |  | 700 | 975 |  |  | F | [9 empty] | FORM | 0,00026189824x+100,02 |  |  | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17100 | 0 | 16416 | 9622 | 0 | ELM3144_M204 | Ch1 Pin 1(+) - 2(-) | I32
ONR6402AI | WIS ONR 6402 MESURE NIVEAU RESEVOIR OUEST OTR 102 | MA | O | FIL | 1 | F |  | 8 | mm |  | 50 | 2096 |  |  | 700 | 975 |  |  | F | [9 empty] | FORM | 0,00026189824x+100,02 |  |  | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17102 | 0 | 16416 | 9626 | 0 | ELM3144_M204 | Ch2 Pin 1(+) - 2(-) | I32
ONR6403AI | WIS ONR 6403 MESURE NIVEAU RESEVOIR EST OTR 103 | MA | O | FIL | 1 | F |  | 8 | mm |  | 50 | 2096 |  |  | 700 | 975 |  |  | F | [9 empty] | FORM | 0.00026189824x+50.02 |  |  | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17104 | 0 | 16416 | 9630 | 0 | ELM3144_M204 | Ch3 Pin 1(+) - 2(-) | I32
ONR6404AI | WIS ONR 6404 MESURE NIVEAU RESEVOIR EST OTR 104 | MA | O | FIL | 1 | F |  | 8 | mm |  | 50 | 2096 |  |  | 700 | 975 |  |  | F | [9 empty] | FORM | 0,00026189824x+100,02 |  |  | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17106 | 0 | 16416 | 9634 | 0 | ELM3144_M204 | Ch4 Pin 1(+) - 2(-) | I32
OPR6402AI | WIS OPR 6402 MESURE PRESSION RESEVOIR OUEST OTR 101 | MA | O | FIL | 1 | F |  | 8 | barg |  | 0 | 16 |  |  | 5 |  |  |  | F | [9 empty] | FORM | 0,000002048x |  |  | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17110 | 0 | 16416 | 9642 | 0 | ELM3144_M205 | Ch2 Pin 1(+) - 2(-) | I32
OPR6403AI | WIS OPR 6403 MESURE PRESSION RESEVOIR OUEST OTR 102 | MA | O | FIL | 1 | F |  | 8 | barg |  | 0 | 16 |  |  | 5 |  |  |  | F | [9 empty] | FORM | 0,000002048x |  |  | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17112 | 0 | 16416 | 9646 | 0 | ELM3144_M205 | Ch3 Pin 1(+) - 2(-) | I32
OPR6405AI | WIS OPR 6405 MESURE PRESSION RESEVOIR EST OTR 103 | MA | O | FIL | 1 | F |  | 8 | barg |  | 0 | 16 |  |  | 5 |  |  |  | F | [9 empty] | FORM | 0,000002048x |  |  | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17116 | 0 | 16416 | 9654 | 0 | ELM3144_M206 | Ch1 Pin 1(+) - 2(-) | I32
OPR6406AI | WIS OPR 6406 MESURE PRESSION RESEVOIR EST OTR 104 | MA | O | FIL | 1 | F |  | 8 | barg |  | 0 | 16 |  |  | 5 |  |  |  | F | [9 empty] | FORM | 0,000002048x |  |  | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17118 | 0 | 16416 | 9658 | 0 | ELM3144_M206 | Ch2 Pin 1(+) - 2(-) | I32
ZJR8001 | Pandora - PLC_Number | MA | N | INT | 0 | Z | [26 empty] | NOT |  |  | VMC06 Etat Pandora Front End |  | PANDORA | 11 |  |  |  |  | 12289 | 0 | 16416 | 0 | 0 |  |  | UINT
OPR6407AI | WIS OPR 6407 PRESSION CIRCUIT CARNEAU OUEST | MA | O | FIL | 1 | F |  | 8 | barg |  | 0 | 6 |  |  | 0.19 |  |  |  | F | [9 empty] | FORM | 0,000000768x |  |  | NOT | 100 |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17120 | 0 | 16416 | 9662 | 0 | ELM3144_M206 | Ch3 Pin 1(+) - 2(-) | I32
OPR6408AI | WIS OPR 6408 PRESSION CIRCUIT CARNEAU EST | MA | O | FIL | 1 | F |  | 8 | barg |  | 0 | 6 |  |  | 0.19 |  |  |  | F | [9 empty] | FORM | 0,000000768x |  |  | NOT | 100 |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW | [5 empty] | 17122 | 0 | 16416 | 9666 | 0 | ELM3144_M206 | Ch4 Pin 1(+) - 2(-) | I32
ZZZ6DMA10 | WIS SYNTHESE MODULES CHAINE 10 | AL | N | CAL | 1 | Z |  | R | [10 empty] | Z | [11 empty] | ZZZ6100EC10;ZZZ6921M189;ZZZ6108M190;ZZZ6108M191;ZZZ6108M192;ZZZ6108M193;ZZZ6108M194;ZZZ6108M195;ZZZ6108M196;ZZZ6108M197;ZZZ6108M198;ZZZ6108M199;ZZZ6108M200;ZZZ6108M201;ZZZ6108M202;ZZZ6941M203;ZZZ6314M204;ZZZ6314M205;ZZZ6314M206;ZZZ6314M207;ZZZ6314M208;ZZZ6314M209;ZZZ6289M210;ZZZ6289M211;ZZZ6289M212 | Y |  |  |  | Infos Chaine 10 (VMC01 button) | VMC (Z) | NEW
WIS04DMA | WIS SYNTHESE DEFAUT SYSTEME DE FLUIDES EAU ZLV COTE OUEST | AL | N | CAL | 1 | F | [12 empty] | F | [11 empty] | OPR6402AI;ONR6401AI;OPR6403AI;ONR6402AI;OPR6407AI | Y |  |  |  | WIS04_WATER_WEST (2/2) | Water Injection System (WIS) | NEW
WIS06DMA | WIS SYNTHESE DEFAUT SYSTEME DE FLUIDES EAU ZLV COTE EST | AL | N | CAL | 1 | F | [12 empty] | F | [11 empty] | OPR6405AI;ONR6403AI;OPR6406AI;ONR6404AI;OPR6408AI | Y |  |  |  | WIS06_WATER_EST (2/2) | Water Injection System (WIS) | NEW
ZZC6002D | WIS BON ETAT | AL | N | INT | 1 | F;Z | [12 empty] | F;Z | [14 empty] | 500 |  | WIS07_ETAT_CHRONOLOGIE | Water Injection System (WIS) | NEW | [5 empty] | 12314 | 2 | 16416 | 50 | 2 | NA |  | BIT
SZI7283W | Alarme Feu Newton Local Circulation 00 - ZDA83 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 2 | [7 empty] | BITVAL
SZI7284W | Alarme Feu Newton Local technique Courant faibles 11 - ZDA84 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 6 | [7 empty] | BITVAL
SZI7285W | Alarme Feu Newton Local Climatisation 08 - ZDA85 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 10 | [7 empty] | BITVAL
SZI7286W | Alarme Feu Newton Bureau 09 – ZDA86 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1041 | 14 | [7 empty] | BITVAL
SZI7287W | Alarme Feu Newton Local énergie 10 – ZDA87 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1042 | 2 | [7 empty] | BITVAL
SZI7288W | Alarme Feu Newton Open space B 13 – ZDA88 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1042 | 6 | [7 empty] | BITVAL
SZI7289W | Alarme Feu Newton Open space A 14 – ZDA89 | AL | N | RES | 2 | S | [12 empty] | S | [13 empty] | MTCP | 2000 |  | DI79 (DETIN Lagrange Group) | Detection Incendie (DI) | LGRNG | 9 |  |  | 1042 | 10 | [7 empty] | BITVAL
DI79DMA | SYNTHESE ALARME DETIN NEWTON | AL | N | CAL | 0 | Z | [12 empty] | Z | [11 empty] | SZI7283W;SZI7284W;SZI7285W:SZI7286W;SZI7287W;SZI7288W;SZI7289W; SCK7001D ; SZI7000D ; SZI7000DE ; SCK7000DH ; SCK7000D; | Y |  |  |  | DI79 | Detection Incendie (DI)

## LEGEND
Database Legend
Column ID | Meaning
Libellés | Reports the tag of the signal
Description | Reports the description of the signal
Type | Indicated the type of the signal, that can be: - CR = Status Signal (Compte Rendu); - AL = Alarm; - CT = Command; - MA = Analog Measurement
Cablé | Indicates weather the signal is cabled or not - N = Not cabled; - O = Cabled
Nature | Reports the Nature of the signal, that can be: - RES for serial bus field transmitted signals; - TIP for TCP/IP field transmitted signals; - FIL for wired field transmitted signals - INT for internal to VMC network generated signals (TCP/IP); - CAL for Calculated signals
Zone | Indicates the zone from which the signal s coming from. It can be: - 0 for signals generated internally to VMC network; - 1 for signals transmitted by VMC Bunker Front-End (all VEGA Launch Complex signals); - 2 for signal transmitted by VMC Lagrange Front-End; - 3 for signals transmitted by VMC Pandora Front-End; - 4 for signals transmitted by VMC BIL Front-End;
Subsystem | Reports the subsystem to which the signal belongs. It can be: - O = Optical and Video; - E = Energy; - C = HVAC; - F = Fluidic; - S = Sauvegarde; - Z = Internal; - D = DETG; - I = Infrastructure; - A = APITeam; - H = SHM;
PCP | Indicates weather a signal is to be transmitted to the Syncer or not. The cells under this column will report PCP in case of transmission with the since, otherwise they are empty.
Astreinte | Indicates the group of operators to which the signal/alarm is to be transmitted and managed. The groups can be: - E = Systeme Energy; - K = Systeme Clima; - 8 = Systeme Fluide VMC; - V = Systeme DVT; - 6 = Systeme Infrastructures; - U = Systeme API; - S = SCSI; - R = Systeme VMC;
Unit | Reports the measurement unit of the signal (in case of MA signals)
Conv | In case of MA, it reports the conversion factor. The input raw value is to be multiplied by the conversion factor in order to provide the value of the related measurement.
Min | Indicates the maximum value evaluable by the sensor
Min | Indicates the minimum value evaluable by the sensor
Low1 | Reports the first low threshold for the analog measurement to trigger the associated low alarm; empty in case of no associated alarms; normally this threshold is associated to warning status
High1 | Reports the first high threshold for the analog measurement to trigger the associated high alarm; empty in case of no associated alarms; normally this threshold is associated to warning status
Low2 | Reports the second low threshold for the analog measurement to trigger the associated low alarm; empty in case of no associated alarms; normally this threshold is associated to alarm status
High2 | Reports the second high threshold for the analog measurement to trigger the associated high alarm; empty in case of no associated alarms; normally this threshold is associated to alarm status
Equal | Reports the alarm condition in case the alarm is associated only to a specific value
Psec | Indicates the security position of the relè: - ON = Open relè - OFF = Closed relè
Aut | Authorization reports the group of operators that are allow to send the related command and to acknowledge the related alarm. The groups can be: - O = Optical and Video; - E = Energy; - C = HVAC; - F = Fluidic; - S = Sauvegarde; - Z = Internal; - D = DETG; - I = Infrastructure; - A = APITeam; - H = SHM;
Inhibited (YES/NO) | Indicates wether a command needs the Safety User authorization or not
Repos | Indicates if the relè is normally open (NO) or normally closed (NF)
Imp | Impulsion, reports, for the impulsive commands, the value of the sent impulse in seconds.
Group | Group is applicable only to group command that are represented with "GC" termination in the Libellés. This field reports the commands included in the groups and that are sent simultaneously.
AutCmd | Automatic Commands indicates if the command is automatically sent in response to a specific event; for each automatic command the tag of the signal deputed to activate the command is reported; if more than one condition are required all tags are reported and the logical condition that activate the automatic command is specified in the "Op" column
Precondition | Preconditions indicate the status of an other signal that allows the command sending
Dead Band Value | Configuration value of the dead band setting
Dead Band Perc | Configuration value in percentage of the dead band setting
Alarm Persist Value | Timing value in seconds to set on an alarm
Op | In the case in which the Nature of the signal is CAL (calculated) or AutCMD (Automatic command) it reports the logic operator through which the signal is evaluated. The following operators can be configured: - AND - OR - XOR - EQUAL - NOTEQUAL - NOT - FORM (if a specific formula is implemented as condition; the formula is reported in the associated column "FORM"
FORM | Formula column reports the Formula used to calculate the measure
Calc | The signals that appears in this column is to be considered as evaluated by the parameters of interest, according to the logical operator reported in the column "Op" or the formula reported in the column "FORM
MasterAl | Master Alarm report if the signal is a master alarm: - Y - N If the master alarm is a calculated signals activated in relation to logical conditions, these are reported in the columns "Op" and "Calc";
DRIVER | Driver specifies the driver implemented in the HLCS SW to manage the signal: - NOT, for data acquired via Notification driver; - POL, for data acquired via Polling driver; - SNMP, for data acquired via SNMP driver; - SHM, for data acquired via SHM driver; - CMD, for commands managed via Command driver; - MTCP, for data acquired via MODBUS TCP/IP driver
Syno | Synoptic column, indicates the Synoptic name where the signal is shown;
Origin | Origin column, reports the origin of the signals, if it comes from the CCS or it is new, etc. (the column is included only for support purpose)
FieldID | Field ID column, reports the identification of the slave field device: 0 - VMC Front-End PLC 1 - GAS and Fire Detection PLC (IV01) 2 - O&V PLC (OV06) 3 - Wire PLC (SV01) 4 - Energy TGBT PLC (EV03) 5 - Energy 1D60 PLC (EV0A) 6 - HVAC Bunker PLC (CV0B) 7 - HVAC MG PLC (CV0G) 8 - SHM server 9 - Lagrange PLC 10 - Groupe életgrogène 11 - Pandora PLC 12 - BIL VMC Front-End PLC 13 - BIL Clima ZVQ4001 PLC 14 - BIL Clima ZVQ4003 PLC 15 - BIL Energy TGBT 16 - BIL UPS CATIIIA 17 - BIL UPS CATIIIB
FieldReg | Field register column, reports the Modbus register in the communication exchange table of the field device where the VMC Front-End PLC reads the signal from the field
FieldBIT | Field BIT column, reports the bit in the communication exchange table of the field device where the VMC Front-End PLC reads the signal from the field
FEReg | Front End register column reports the Modbus register in the communication table of the VMC FE PLC with the VMC HLCS
FEBIT | Front End BIT column reports the Modbus register in the communication table of the VMC FE PLC with the VMC HLCS
FEIndex ADS | Front End Index ADS column reports the Index of each measure present in the PLC ADS registers
FEOffset ADS | Front End Offset ADS column reports the Offset of each measure present in the PLC ADS registers
FEBIT ADS | Front End Bit ADS column reports the Bit of each measure present in the PLC ADS registers
FE Module | Front End Module reports the extension module of the VMC FE PLC where the signal is exchanged with the field
FE PIN | Front End Module reports the PIN in the module of the VMC FE PLC where the signal is exchanged with the field
DATA TYPE | Data type column describes the type data format: - UINT if data are type - BOOL if data are Boolean type - STRING( ) if data are string type - I32 if data are type - INT if data are type - U8 , U16, U32 if data are type - BITVAL if data are type
VALUE | Value, only for commands, it indicates the value assumed by the command status

## REACTIONS
NEW | ORIGIN | SYSTEM | PLATINE | FUNCTION | DESTINATION | TRIGGER | STATUS | REACTION 1 | REACTION 2 | REACTION 3 | REACTION 4 | REACTION 5
Y | AE/AR BNKR | AE | ALL | SEND REPORT TO PLATINE | VMC FE LGRNG | SCE6001S | ON | SCE7003CM | SCE7005CM | SCE7007CM
Y | AE/AR BNKR | AE | ALL | SEND REPORT TO PLATINE | VMC FE LGRNG | SCE6001S | OFF | SCE7003CA | SCE7005CA | SCE7007CA
Y | AE/AR BNKR | AR | ALL | SEND REPORT TO PLATINE | VMC FE LGRNG | SCE6002S | ON | SCE7004CM | SCE7006CM | SCE7008CM
Y | AE/AR BNKR | AR | ALL | SEND REPORT TO PLATINE | VMC FE LGRNG | SCE6002S | OFF | SCE7004CA | SCE7006CA | SCE7008CA
Y | VMC FE LGRNG | AR | COPV | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7004D | ON | SCE6002CM | SZP6014CM
Y | VMC FE LGRNG | AR | COPV | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7004D | OFF | SCE6012CM | SZP6014CA
Y | VMC FE LGRNG | AR | PRS | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7006D | ON | SCE6002CM | SZP6014CM
Y | VMC FE LGRNG | AR | PRS | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7006D | OFF | SCE6012CM | SZP6014CA
Y | VMC FE LGRNG | AR | PNDR | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7008D | ON | SCE6002CM | SZP6014CM
Y | VMC FE LGRNG | AR | PNDR | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7008D | OFF | SCE6012CM | SZP6014CA
Y | VMC FE LGRNG | AE | COPV | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7003D | ON | SCE6001CM
Y | VMC FE LGRNG | AE | COPV | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7003D | OFF | SCE6011CM
Y | VMC FE LGRNG | AE | PRS | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7005D | ON | SCE6001CM
Y | VMC FE LGRNG | AE | PRS | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7005D | OFF | SCE6011CM
Y | VMC FE LGRNG | AE | PNDR | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7007D | ON | SCE6001CM
Y | VMC FE LGRNG | AE | PNDR | COMMAND RELATED TO PLATINE INPUT | AE/AR BNKR | SCE7007D | OFF | SCE6011CM
N |  |  |  | TRAFFIC LIGHTS | POSTE ALOUETTE | SFE6001M | ON | SFE6002CA | SFE6003CA | SFE6004CA
N |  |  |  | TRAFFIC LIGHTS | POSTE ALOUETTE | SFE6002M | ON | SFE6001CA | SFE6003CA | SFE6004CA
N |  |  |  | EXTI/HVAC |  | SCX6002GE | ON | VRU6004CF
N |  |  |  | EXTI/HVAC |  | SCX6003GE | ON | VRU6007CF
N |  |  |  | EXTI/HVAC |  | SCX6004GE | ON | VRU6008CF
N |  |  |  | EXTI/HVAC |  | SCX6005GE | ON | VRU6009CF
N |  |  |  | EXTI/HVAC |  | SCX6006GE | ON | VRU6101CF
N |  |  |  | EXTI/HVAC |  | SCX6007GE | ON | VRU6103CF
N |  |  |  | EXTI/HVAC |  | SCX6008GE | ON | VRU6111CF
N |  |  |  | EXTI/HVAC |  | SCX6009GE | ON | VRU6112CF
N |  |  |  | EXTI/HVAC |  | SCX6010GE | ON | VRU6113CF
N |  |  |  | EXTI/HVAC |  | SCX6011GE | ON | VRU6115CF
N |  |  |  | EXTI/HVAC |  | SCX6012GE | ON | VRU6116CF
N |  |  |  | EXTI/HVAC |  | SCX6001GE | ON | VRU6013CF
N |  |  |  | EXTI/HVAC |  | SCX6021GE | ON | VRU6981CF
N |  |  |  | EXTI/HVAC |  | SCX6022GE | ON | VRU6982CF
N |  |  |  | EXTI/HVAC |  | SCX6023GE | ON | VRU6983CF
N |  |  |  | TANGARA |  | SFE6101M | ON | SFE6101CM | SFE6102CA | SFE6103CA | SFE6104CA | SFE6105CA
N |  |  |  | TANGARA |  | SFE6102M | ON | SFE6102CM | SFE6101CA | SFE6103CA | SFE6104CA | SFE6105CA
N |  |  |  | TANGARA |  | SFE6103M | ON | SFE6103CM | SFE6101CA | SFE6102CA | SFE6104CA | SFE6105CA
N |  |  |  | TANGARA |  | SFE6104M | ON | SFE6104CM | SFE6101CA | SFE6102CA | SFE6103CA | SFE6105CA
N |  |  |  | TANGARA |  | SFE6105M | ON | SFE6105CM | SFE6101CA | SFE6102CA | SFE6103CA | SFE6104CA
N |  |  |  | WIS |  | ZZC6006M | OFF | ZZC6002CN
N |  |  |  | WIS |  | ZZC6006M | ON | ZZC6002CO

## GROUP COMMANDS
NEW | Libellés group | Description Group | CMD 1 | CMD 2 | CMD 3 | CMD 4 | CMD 5
Y | SCE6002CMGC | CMDE MARCHE ALERTE REPLI ZLV ET SONO | SCE6002CM | SZP6014CM
Y | SCE6002CAGC | CMDE ARRET ALERTE REPLI ZLV ET SONO | SCE6012CM | SZP6014CA
N | VVU6CM1GC | VEGA GANTRY PLC : STARTING HVAC INSTALLATION | VVU6401CM1 | VVU6126CM401
N | VVU6CA1GC | VEGA GANTRY PLC : STOPPINGING HVAC INSTALLATION | VVU6401CA1 | VVU6126CA401
N | VVU6CM3GC | VEGA GANTRY PLC : OPERATING IN ECO MODE ON | VVU6401CM3 | VVU6126CM103
N | VVU6CA3GC | VEGA GANTRY PLC : OPERATING IN ECO MODE OFF | VVU6401CA3 | VVU6126CA403
N | VPZ6CO1GC | VEGA GANTRY PLC : OPENNING HALL DOOR | VPZ6999CO | VPZ6126CO401
N | VPZ6CF1GC | VEGA GANTRY PLC : CLOSING HALL DOOR | VPZ6999CF | VPZ6126CF401
Y | VCF7000COGC | CMDE REARMEMENT HVAC LAGRANGE | VCF7000CO | VRU7232CO | VRU7120CO
Y | SCX7001CMGC | CMDE MARCHE EXTI UPS BATT | SCX7001CM | VRU7232CF | VRU7120CF
Y | SCX7002CMGC | CMDE MARCHE EXTI TECH LAU | SCX7002CM | VRU7232CF | VRU7120CF
Y | VVU90003CMGC | BIL CMDE ACQUITTEMENT DEFAULT | VVU90003CM1 | VVU90003CM2 | VVU90003CM3 | VVU90003CM4 | VVU90003CM5
Y | VVU90001CMGC1 | CMDE BIL CONFIGURATION - MODE Conf1 | VVU90001CM1 | VVU90001CM2 | VVU90001CM3 | VVU90001CM4 | VVU90001CM5
Y | VVU90001CMGC2 | CMDE BIL CONFIGURATION - MODE Conf2 | VVU90001CM6 | VVU90001CM7 | VVU90001CM8 | VVU90001CM9 | VVU90001CM10
Y | VVU94030COGC | BIL CMDE Priority selection cabinet Hiross VCT4030 | VVU94030CO | VVU94040CF
Y | VVU94040COGC | BIL CMDE Priority selection cabinet Hiross VCT4040 | VVU94030CF | VVU94040CO

## CONF_REG
CONF ITEM | ITEM TITLE | DESCRIPTION | IMPACT | ORIGIN | NATURE | SLAVE ID | SLAVE DESCRIPTION | STATUS | CONTR. REF / PM | FA REF. | IMPLEMENTED
V-1 | VMC FE PLC diagnostic signals |  |  | NEW (PLC) | INT | 0 | VMC FE PLC | VDC_4 | Rider III baseline
V-2 | Fire Detection CCS signals |  |  | CCS | RES | 1 | GAS&DI PLC | VDC_4 | Rider III baseline
V-3 | Gas detection CCS signals |  |  | CCS | RES | 1 | GAS&DI PLC | VDC_4 | Rider III baseline
V-4 | GAS&DI PLC internal diagnostic |  |  | NEW (PLC) | RES | 1 | GAS&DI PLC | VDC_4 | PLC CCN
V-5 | O&V CCS signals |  |  | CCS | RES | 2 | O&V PLC | VDC_4 | Rider III baseline
V-6 | GAS&DI PLC internal diagnostic |  |  | NEW (PLC) | RES | 2 | O&V PLC | VDC_4 | PLC CCN
V-7 | DVT CCS signals |  |  | CCS | RES | 3 | WIRE PLC | VDC_4 | Rider III baseline
V-8 | MG FLUID CCS signals |  |  | CCS | RES | 3 | WIRE PLC | VDC_4 | Rider III baseline
V-9 | MG ENE CCS signals |  |  | CCS | RES | 3 | WIRE PLC | VDC_4 | Rider III baseline
V-10 | MG HVAC MANOMETERS |  |  | CCS | RES | 3 | WIRE PLC | VDC_4 | Rider III baseline
V-11 | WIRE PLC internal diagnostic |  |  | NEW (PLC) | RES | 3 | WIRE PLC | VDC_4 | PLC CCN
V-12 | MG PM325 NETWORK ANALYZERS |  |  | NEW (ENE MC) | RES | 3 | WIRE PLC | VDC_5 | Rider III baseline
V-13 | ENE TGBT CCS signals |  |  | CCS | RES | 4 | ENE TGBT PLC | VDC_4 | Rider III baseline
V-14 | ENE TGBT PLC internal diagnostic |  |  | CCS | RES | 4 | ENE TGBT PLC | VDC_4 | PLC CCN
V-15 | VEGA CHATEAU D'EAU |  |  | CCS | RES | 4 | ENE TGBT PLC | VDC_4 | Rider III baseline
V-16 | BUNKER NETWORK ANALYZERS |  |  | NEW (ENE MC) | RES | 4 | ENE TGBT PLC | VDC_5 | Rider III baseline
V-17 | BUNKER SMOKE EXTRACTION |  |  | NEW (ENE MC) | RES | 4 | ENE TGBT PLC | VDC_5 | Rider III baseline
V-18 | ENE 1D60 PLC internal diagnostic |  |  | CCS | RES | 5 | ENE 1D60 PLC | VDC_4 | PLC CCN
V-19 | SEPAM ENERGY PARAMETERS |  |  | NEW (ENE MC) | RES | 5 | ENE 1D60 PLC | VDC_5 | Rider III baseline
V-20 | BUNKER HVAC CCS signals |  |  | CCS | RES | 6 | HVAC BUNKER PLC | VDC_5 | Rider III baseline
V-21 | BUNKER HVAC local supervisor |  |  | NEW (HVAC SPV) | RES | 6 | HVAC BUNKER PLC | VDC_5 | Rider III baseline
V-22 | HVAC Bunker PLC internal diagnostic |  |  | NEW (PLC) | RES | 6 | HVAC BUNKER PLC | VDC_5 | PLC CCN
V-23 | MG HVAC CCS signals |  |  | CCS | RES | 7 | HVAC MG PLC | VDC_5 | Rider III baseline
V-24 | HVAC MG PLC local supervisor |  |  | NEW (HVAC SPV) | RES | 7 | HVAC MG PLC | VDC_5 | Rider III baseline
V-25 | HVAC MG PLC internal diagnostic |  |  | NEW (PLC) | RES | 7 | HVAC MG PLC | VDC_5 | PLC CCN
V-26 | CCS WIRING signals (Jb_racks_list) |  |  | CCS | FIL | NA | NA | VDC_4 | Rider III baseline
V-27 | SHM |  |  | NEW (SHM) | TIP | 8 | SHM SERVER | VDC_4 | Rider III baseline
V-28 | VMC Internal Diagnostic | PLC module infodata, Switch, SAAA and Syncer connections, VBrain processes |  | NEW (VMC) | INT | NA | NA | VDC_5 | Rider III baseline
V-29 | ENE MC CALCULATED PARAMETERS | Formulas corrections |  | NEW (ENE MC) | INT | NA | NA | VDC_5 | Rider III baseline
V-30 | AUTOMATIC COMMANDS | EXTI-HVAC, AE-AR | SW; VDC | CCS |  |  |  | VDC_6 | Rider III baseline
V-31 | MA CONVERSION FACTOR | BUG 2658: MA configuration (conv factor and type, from UINT to I16) | SW; VDC | NEW | NA | NA | NA | VDC_6 | Rider III baseline | 2625
V-32 | COMMANDS PRECONDITION | HVAC precond. SPV | SW; VDC | NEW (HVAC SPV) | RES | 6.7 | HVAC PLC BUNKER AND MG | VDC_6 | Rider III baseline
V-33 | PM325 POLLING FREQUENCY MOD. | POLL. FREQ. Modified from 5000 ms to 3000 ms | SW; VDC | NEW (ENE MC) | RES | 3.4 | WIRE PLC, ENE TGBT PLC | VDC_6 | Rider III baseline
V-34 | PM325 COMM. FAULT CORRECTION | Modification of signals type (from CR to AL) and Data type (from I32 to Bitval) | VDC | NEW (ENE MC) | RES | 3 | WIRE PLC, | VDC_6 | Rider III baseline
V-35 | Master alarms | ENE, HVAC, VMC, O&V all alarms included in Master alarms; bug resolutions | SW; VDC | NA | CAL | 4,5,6,7 | NA | VDC_6 | Rider III baseline
V-36 | Impulsive command | bug correction | SW; VDC | CCS | FIL | NA | NA | VDC_6 | Rider III baseline
V-37 | ENE PLC 1D60, TGBT diagnostic syno | New synoptic for Energy PLC faults infos visualization (E60 for TGBT, E72 for 1D60) | SW; | NEW | RES | 4 | ENE TGBT PLC | VDC_6 | Rider III baseline
V-38 | HVAC bug synoptic correction | Missing signals added in synoptic, including validities | SW; | NA | NA | NA | NA | VDC_6 | Rider III baseline
V-39 | MG71 synoptic correction | Graphic animation corrections | SW; | NA | NA | NA | NA | VDC_6 | Rider III baseline
V-40 | Master Alarms | All alarms included in Master alarms for LCS, FLU | SW; VDC | NA | CAL | 1,2,3, wirings | GAS&DI, O&V, WIRE PLC, wirings | VDC_7 | Rider III baseline
V-41 | ENE TGBT Arrivee alarm condition | Signal type modifications from AL to CR | SW; VDC | CCS | RES | 4 | ENE TGBT PLC | VDC_7 | Rider III baseline
V-42 | Tag modifications | Tag modifications for some signals of GAS&DI and WIRE PLC | SW; VDC | NA | RES | 1.3 | GAS&DI, WIRE PLC | VDC_7 | Rider III baseline
V-44 | ENE TGBT MA thresholds modification | PM810 signals MA | SW; VDC | NEW (ENE MC) | RES | 4 | ENE TGBT PLC | VDC_7 | Rider III baseline
V-45 | HVAC bug synoptic corrections (post CMY FAT) | NA | SW; | NA | NA | 6.7 | HVAC PLC BUNKER AND MG | VDC_7 | Rider III baseline
V-46 | ENE TGBT bug synoptic corrections (post CMY FAT) | NA | SW; | NA | NA | 4 | TGBT PLC | VDC_7 | Rider III baseline
V-47 | ENE 1D60 bug synoptic corrections (post CMY FAT) | NA | SW; | NA | NA | 5 | 1D60 PLC | VDC_7 | Rider III baseline
V-48 | SAAA and Syncere measures elimination | Deleting of signals relevant to slave server | SW; VDC | NEW | INT | NA | NA | VDC_7 | Rider III baseline
V-49 | New synoptic addition for LCS PLCs | LCS PLC diagnostic synoptic creation | SW; | NEW | NA | 1,2,3 | GAS&DI, O&V, WIRE PLC | VDC_7 | Rider III baseline
V-50 | HVAC signals elimination | deleting of signal relevant to 1601.VC.004.02 | SW; VDC | CCS | RES | 6 | HVAC PLC BUNKER | VDC_7 | Rider III baseline
V-51 | HVAC command type modification | Modification of fire dampers commands from "single mode" to "parametric mode" | SW; VDC | NA | RES | 6 | HVAC PLC BUNKER | VDC_7 | Rider III baseline
V-52 | VALIDITY UPDATE | Removal of wirings modules validities | SW; VDC | NA | RES | 1,3,4,5,6,7 | GAS&DI, WIRE PLC, ENE TGBT AND 1D60, HVAC BUNKER AND MG | VDC_8 | Rider III baseline
V-53 | CL8 SIGNAL MODIFICATIONS | Modification of DVT signals due to CL8 introduction; PM AE | SW; VDC | PM AE | RES | 1.3 | DETG/DI PLC, WIRE PLC | VDC_8 | CCN CL8
V-53 | Signals elimination | Elimination of signals not more aquired from the VMC system | SW; VDC | CCS; NEW | RES | 3,6,7,0 | Wire PLC, HVAC BUNKER PLC, HVAC GANTRY PLC, VMC INTERNAL SIGNALS | VDC_8 | Rider III baseline
V-54 | Data type modification | Modification of SOR*** of DVT and DETIN from I16 to U16 | SW; VDC | CCS | RES | 1.3 | WIRE PLC; DETG/DI PLC | VDC_8 | Rider III baseline
V-55 | Signal description modification | Reduction of GPP6045DT1 signal description length for bug 2620 resolution | SW; VDC | CCS | RES | 6 | HVAC BUNKER PLC | VDC_8 | Rider III baseline | Bug 2620
V-56 | Master alarms | Bug 2654 resolution in Master Configuration | SW; VDC | NA | CAL | 4.5 | ENE TGBT PLC; ENE1D60 PLC | VDC_8 | Rider III baseline | Bug 2654
V-57 | NTP TSS MODE | Modification of string visualized for NO "IRIG B" information in the NTP Server | SW; VDC | NEW | INT | NA | NA | VDC_8 | Rider III baseline
V-58 | Bunker switch alarms conditions modification | Modification of Bunker switches alarm condition in ports 21st and 23st for redundancy link addition | SW; VDC | NEW | INT | NA | NA | VDC_8 | Rider III baseline
V-59 | New VEGA-C signals | Addition of new signals for VEGA-C DVT | SW; VDC | NEW | RES | 3 | Wire PLC | VDC_8
V-60 | Wire PLC Fault and Watchdog | Addition of Wire PLC Watchdog information and new fault signal | SW; VDC | NEW | RES | 3 | Wire PLC | VDC_8 | Rider III baseline
V-61 | Modification of SHM analogic measures | Modification of data-type from U16 to I16 of SHM analogic measurements | SW; VDC | NEW | RES | 8 | SHM SERVER | VDC_8 | Rider III baseline
V-62 | Energy PM3250 Gantry data type modification | Modification of data type for Energy PM3250 Gantry multimeters from I32 to FLOAT | SW;VDC | NEW | RES | 3 | Wire PLC | VDC_8 | Rider III baseline
V-63 | Dedicated astreinte for VMC | Addition of new Astreinte (Z) for VMC internal signals | SW; VDC | NEW | INT | NA | NA | VDC_8 | Rider III baseline
V-64 | Addition of precondition for O&V commands | Precondition of API ARMEE OFF for O&V commands sending from VMC | SW; VDC | CCS | RES | 2 | O&V PLC | VDC_8 | Rider III baseline
V-65 | Correction of Optical and Videosignal description | Modification of WZC6000M description for O&V automatic sequence | SW; VDC | CCS | RES | 2 | O&V PLC | VDC_8 | Rider III baseline
V-66 | Conversion factor of Mesures de Concentration | Modification of convertion factor for analogic measurement of CM4 and CL8 from 10000 to 1 | SW; VDC | CCS | RES | 1.3 | DETG/DI PLC, WIRE PLC | VDC_9 | Rider III baseline
V-67 | All commands description modification | Modification of description for all parametric commands for Output state visualization of Vbrain Reporting | SW; VDC | CCS; NEW | RES; FIL; INT | 2,3,4,6,7,8 | O&V PLC; Wire PLC; ENE TGBT PLC; HVAC BUNKER PLC; HVAC GANTRY PLC; SHM Server | VDC_9 | Rider III baseline
V-68 | Lagrange Front-End Signals | Addition of signals and commands acquired from Lagrange Front-End | SW; VDC | NEW | RES |  | Lagrange FE | VDC_9 | Rider III baseline
V-69 | Elimination of CDL3 switch | Deletion of all measures and master alarms related to CDL3 switch | SW; VDC | NEW | RES | NA | NA | VDC_9 | Rider III baseline
V-70 | Elimination of Modbus TCP/IP Spare driver | Deletion of spare driver Modbus TCP/IP and related spare measures | SW; VDC | New | RES | NA | NA | VDC_9 | NA
V-71 | Master Alarms configuration | Addition of new master alarms and modification of preexitent ones for Lagrange S/s addition | SW;VDC | New | CAL | NA | NA | VDC_9 | Rider III baseline
V-72 | Addition of precondition on CCS pumps | New precondition on OPP6301 and OPP6302 pumps | SW; VDC | CCS | RES | 3 | Wire PLC | VDC_9 | Rider III baseline
V-73 | Modification of Analogic Measures conversione factor | Application of linear calibration on raw value of hardwired analogic measures | SW; VDC | CCS | FIL | NA | NA | VDC_9 | Rider III baseline
V-74 | Deletion of alarm on Bunker switch ports | Deletion of alarm on Bunker switches ports number 23 for elimination of redundancy link | SW; VDC | NEW | RES | NA | NA | VDC_9 | Rider III baseline
V-75 | AUTOMATIC COMMANDS and GROUP AUTOMATIC COMMANDS | Configuration of automatic commands and group commands for Alert Repli/Alert Evacuation and Fire Extinction | SW; VDC | CCS/NEW | FIL/RES | NA | NA | VDC_9 | Rider III baseline
V-76 | PM3250 validity update | Validity update for Energy PM3250 | SW; VDC | NEW | RES | 4 | ENE TGBT PLC | VDC_9 | Rider III baseline
V-77 | Negated Logic signals | Implementation of Negated Logic over CCS and new Lagrange signals | SW; VDC | CCS/NEW | FIL/RES | NA | NA | VDC_9 | Rider III baseline
V-78 | Lagrange SONO commands deletion | Deletion of Lagrange SONO commands from VMC/Lagrange exchange interface | SW; VDC | NEW | FIL | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-79 | Acquisition cycle of Lagrange Hardwired signals | Reduction of Lagrange Hardwired signals' acquisition cycle to 500ms | SW; VDC | NEW | FIL | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-80 | Modification of Lagrange IP address | Correction of Lagrange iP address inside VMC acquisition drivers' configuration to 192.168.20.61 | SW; | NEW | NA | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-81 | Modification of MG72 synoptic | Modification of MG72 synoptic for Lagrange SONO Commands deletion | SW; | NEW | NA | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-82 | Banner informing on PLC swapping | Addition of a Banner informing of PLC swapping | SW; | NEW | NA | NA | NA | VDC_10 | Rider III baseline
V-83 | ASCII code plug-in addition and thresholds | Addition of plug-in to manage DAIKIN temperature fault signals in ASCII code format | SW; | NEW; | RES | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-84 | Lagrange signals address modification | Addition of one unit to all Lagrange signals addresses to provide correct communication with Lagrange PLC | SW; VDC | NEW | RES | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-85 | Addition of new information from Lagrange PLC | Addition of two signals informing which Lagrange PLC is working as Primary or Secundary | SW; VDC | NEW | RES | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-86 | Remotion of negated logic over Lagrange signals | Remotion of negated logic over Lagrange SONO signals (ZZP7001D and ZZP7002D) since it is already managed by Lagrange PLC | SW; VDC | NEW | RES | 9 | Lagrange FE | VDC_10 | Rider III baseline
V-87 | Remotion of negated logic over Wire PLC signals | Remotion of negated logic over Wire PLC signals since it is already manged by field Wire PLC | SW; VDC | CCS | RES | 3 | Lagrange FE | VDC_11 | Rider III baseline
V-88 | Vbrain Notifier_Commands monitoring | Addition of new signals informing about the status of Vbrain Notifier Commands for both HLCS Server | SW; VDC | NEW | INT | NA | NA | VDC_11 | Rider III baseline
V-89 | Minor correction of signals description | Correction on signals description monitoring HLCS 1 WebSocket status and IIS sttus | SW; VDC | NEW | NA | NA | NA | VDC_11 | Rider III baseline | Bug 2925
V-90 | Minor corrections over Lagrange signals descriptions | Correction of descriptions for Lagrange signals monitoring the status of each Lagrange Front-End Module. | SW; VDC | NEW; | RES | 9 | Lagrange FE | VDC_11 | Rider III baseline
V-91 | Addition of threshold over ZJP6103 alarm | The measure indicating the presence of a fault on the Master FE PLC shall include an alarm | SW; VDC | NEW; | INT | NA | NA | VDC_11 | Rider III baseline
V-92 | Signals elimination | Deletion of the alarms informing of a fault in the Vbrain Supervisor application | SW; VDC | NEW; | INT | NA | NA | VDC_11 | Rider III baseline
V-93 | Hardwired EXTI Commands corrections | Registers and bit of hardwired EXTI commands has been corrected after OSAT test procedures on MCCs | SW; VDC | CCS | FIL | NA | NA | VDC_11 | Rider III baseline
V-94 | VMC hardwired commands | FE ADS BIT of all hardwired VMC commands has been set equal to 0 | SW; VDC | NA | FIL | NA | NA\ | VDC_11 | Rider III baseline
V-95 | PLC EAP Interfaces and slave PLC reset command | New signals to manage status of PLCs EAP Interfaces and a new command to manage reset of Slave PLC has been added on VMC DB | SW; VDC | NEW | INT | NA | NA | VDC_11 | Rider III baseline
V-96 | State of automatic reset command of slave PLC | Addition of a new measure informing about the state of the automatic reset command | SW; VDC | NEW | INT | NA | NA | VDC_11 | Rider III baseline
V-97 | Alarm configuration | Configuration of alarm on the status of commnd reset ON/OFF | SW; VDC | NEW | INT | NA | NA | VDC_11 | Rider III baseline
V-98 | Signals elimination | Deletion of the signals of TEST. The deleted signals began with "XXX" | SW; VDC | NA | INT | NA | NA | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-99 | Addition of new information from Lagrange PLC | Addition of two signals related to the zone HA:Salle de repos 0014 - ZDA52 | SW; VDC | NEW | RES | 9 | Lagrange FE | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-100 | Negated Logic signals | Implementation of Negated Logic over Lagrange signals | SW; VDC | NA | FIL | 9 | Lagrange FE | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-101 | Minor correction of signals description | The description of the negated logic signals has been modified, only on the configuration server, introducing the following field "**" in the description | SW; VDC | NA | RES | 9 | Lagrange FE | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-102 | Master alarms | SZI7156W alarm included in DI76DMA Master alarm | SW; VDC | NA | CAL | NA | NA | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-103 | Elimination of signals to LagVMCFe | Elimination of the following signals:SZI7152D SZI7152W SZI7153D SZI7153W SZI7154D SZI7154W SCK7000DP | SW; VDC | NA | RES | 9 | Lagrange FE | VDC_12 | Rider III baseline |  | Y
V-104 | Master alarms | The signals indicated in point V-103 have been removed from the master alarms. The master alarms involved are: DI73DMA DI74DMA DI75DMA DI76DMA DI77DMA DI78DMA | SW; VDC | NA | CAL | NA | NA | VDC_12 | Rider III baseline |  | Y
V-105 | Signals modification | Elimination of signals to Syncer (PCP column) | SW; VDC | NA | FIL | NA | NA | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-106 | Elimination of signals to LagVMCFe | Elimination of the following signals: LZR7007D2 LZL7000DW LZL7000A | SW; VDC | NA | RES | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3075 | VBRAIN_CONFIG_2021-11-27
V-107 | Master alarms | The signals indicated in point V-106 have been removed from the master alarms. The master alarms involved are: ZLG6DMA | SW; VDC | NA | CAL |  | NA | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2021-11-27
V-108 | Modification of scale factor | Modification of scale factor for the following MA: VTR7006V1 VTR7008V1 VTR7007V1 VTR7007V3 VTR7007V5 VTR7007V6 VTR7011V1 VTR7012V1 | SW; VDC | NA | MA | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3040 | VBRAIN_CONFIG_2021-11-27
V-109 | Elimination of signals to TD TGBT Lagrange CAT II 184-13-20 | Delete of all signals related to TD TGBT Lagrange CAT II 184-13-20 | SW; VDC | NA | MA | 9 | Lagrange FE | VDC_12 | Rider III baseline | BUG 3040 | VBRAIN_CONFIG_2021-11-27
V-110 | Modification of the Conversion unit measurement | Modification of the Conversion unit measurement for these following MA (from 10 to 1000): QPM6243 QPM6244 QPM6245 QPM6246 QPM6247 QPM6248 QPM6249 | SW; VDC | NA | MA | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3080 | VBRAIN_CONFIG_2022-01-18
V-111 | Addition of signals Bunker (subsystem:DETG&DI) | The signal of Bunker related to WATCHDOG have been inserted. SZC6000 | SW; VDC | NA | RES | 1 | GAS and Fire Detection PLC | VDC_12 | Rider III baseline | 3047 | VBRAIN_CONFIG_2022-01-18
V-112 | Addition of signals Bunker (subsystem:O&V) | The signal of Bunker related to WATCHDOG have been inserted. WZC6002 | SW; VDC | NA | RES | 2 | O&V PLC (OV06) | VDC_12 | Rider III baseline | 3048 | VBRAIN_CONFIG_2022-01-18
V-113 | Addition of Tangara's signals and commands | Addition of Tangara's signals and commands | SW; VDC | CCS |  |  |  | VDC_12 | Rider III baseline | VG-FA-CCS-09 | VBRAIN_CONFIG_2022-01-18
V-114 | Update of Master Alarm | it has been uptated the MG71DMA master alarm after the addition of Tangara's signals | SW; VDC | NA | CAL | NA | NA | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2022-01-18
V-115 | Modification of the TYPE of the signals | The type of the following signals have been changed. The correct type is CR and not AL SZI6093D SZI6094D SZI6095D Modification DI65DMA master alarm: the signals have been removed | SW; VDC | CCS | RES | 1 | GAS and Fire Detection PLC | VDC_12 | Rider III baseline | 3059 | VBRAIN_CONFIG_2022-01-18
V-116 | Modification of the TYPE of the signals | The type of the following signals have been changed only in the VDC. The correct type is CR and not AL. WCO6001M WCO6002M WCO6003M WCO6004M WCO6005M Modification W61DMA master alarm: the signals have been removed | SW;VDC | CCS | RES | 2 | O&V PLC (OV06) | VDC_12 | Rider III baseline | 3062 | VBRAIN_CONFIG_2022-01-18
V-117 | Modification of the TYPE of the signals | The type of the following signals have been changed. The correct type is CR and not AL EQF7320N EQF7320R EQF7320C Modification EZC7325DMA master alarm: the signals have been removed EQF7530 EQF7531 EQF7232 Modification EUL7000DMA master alarm: the signals have been removed | SW; VDC | NEW | CR | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3077 | VBRAIN_CONFIG_2022-01-18
V-118 | Modification of signals | The following signals have been reversed: EQF7320N EQF7320R EQF7320C EQF7530 EQF7531 EQF7232 | SW;VDC | NEW | FIL | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3044 | VBRAIN_CONFIG_2022-01-18
V-119 | Mofdification of signal | SCG7000DA Description changed | SW;VDC | NA | FIL | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3043 | VBRAIN_CONFIG_2022-01-18
V-120 | Update of MA signals | Update MA measurements description and name to associate them with the correct tag. The MA measurements involved are: SOR6102 SOR6202 SOR6104 SOR6204 SOR6106 SOR6206 SOR6107 SOR6207 SOR6108 SOR6208 SOR6109 | SW;VDC | CCS | RES | 1 | GAS and Fire Detection PLC | VDC_12 | Rider III baseline | 3064 | VBRAIN_CONFIG_2022-01-18
V-121 | DeleteHVAC signal+B123 | Delete of the following signal VCD7014S1 VFN7013D1 VFN7010D1 VFN7005D1 Modification VFN7000DMA master alarm: the signals have been removed | SW;VDC | NEW | FIL | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3083 | VBRAIN_CONFIG_2022-01-18
V-122 | DeleteHVAC command | Delete of the following command VRU7020CF VRU7020CO Modification of VCF7000COGC, SCX7001CMGC,SCX7002CMGC commands group | SW;VDC | NEW | FIL | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3083 | VBRAIN_CONFIG_2022-01-18
V-123 | Delete HVAC signals | Delete of the following signals VVV7006DA1 VVV7006DH1 VVV7006DD1 VVV7006DF1 VVV7008DA1 VVV7008DH1 VVV7008DD1 VVV7008DF1 VVV7007DA1 VVV7007DH1 VVV7007DD1 VVV7007DF1 VVV7007DA2 VVV7007DI2 VVV7007DH2 VVV7007DD2 VVV7007DF2 VVV7007DA3 VVV7007DH3 VVV7007DD3 VVV7007DF3 VVV7007DA4 VVV7007DI4 VVV7007DH4 VVV7007DD4 VVV7007DF4 VVV7007DA5 VVV7007DH5 VVV7007DD5 VVV7007DF5 VVV7007DA6 VVV7007DH6 VVV7007DD6 VVV7007DF6 VVV7011DA6 VVV7011DH6 VVV7011DD6 VVV7011DF6 VVV7012DA6 VVV7012DH6 VVV7012DD6 VVV7012DF6 VVV7010DA1 VVV7010DH1 VVV7010DD1 VVV7010DF1 VVV7010DA2 VVV7010DI2 VVV7010DH2 VVV7010DD2 VVV7010DF2 | SW;VDC | NEW | AL | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3083 | VBRAIN_CONFIG_2022-01-18
V-124 |  | Modification of following master alarms HVAC19DMA;HVAC20DMA;HVAC21DMA | SW;VDC | NA | NA | 9 | Lagrange FE | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2022-01-18
V-125 | Modification Watchdog signal | Has been changed the driver of the ZZW6000 MA, from NOT to POL | SW;VDC | NEW | RES | 3 | Wire PLC (SV01) | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2022-01-18
V-126 | Modification watchdog signal | Delete threshold EZC6115 EZC6160 | SW;VDC | NEW | RES | 5 & 4 | Energy 1D60 PLC (EV0A) & Energy TGBT PLC (EV03) | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2022-01-18 | VBRAIN_CONFIG_2022-01-18
V-127 | Modification master alarm | Delete from VZC6000DMA master alarm the following MA signals: VZC6126W1 VZC6126W2 VZC6401W1 VZC6401W2 | SW;VDC | NA | CAL | NA | NA | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2022-01-18
V-128 | Modification description command | Modification of the description of the following command: EQF6002CM | SW;VDC | CCS | INT | 4 | Energy TGBT PLC (EV03) | VDC_12 | Rider III baseline |  | VBRAIN_CONFIG_2022-01-18
V-129 | Modification of the threshold of MA measurements | The threshold values of the following MA mesuements have been changed. It has been modified <= and => with < and > HPR6310 RPR6305 SOR6003 SOR6004 SOR6005 SOR6006 SOR6007 SOR6008 SOR6009 SOR6010 SOR6011 SOR6012 SOR6013 SOR6014 SOR6015 SOR6016 SOR6017 SOR6018 SOR6019 SOR6020 SOR6021 VPR6601 VPR6701 VPR6001 SOR6022 SOR6023 SOR6024 SOR6102 SOR6202 SOR6104 SOR6204 SOR6106 SOR6206 SOR6107 SOR6207 SOR6108 SOR6208 SOR6109 | SW;VDC | CCS | RES | 1 & 3 | GAS and Fire Detection PLC (IV01) & Wire PLC (SV01) | VDC_12 | Rider III baseline | 3072 | VBRAIN_CONFIG_2022-01-18
V-130 | Modification of signals | The following signals have been reversed: VFN7013S3 VFN7010S3 VFN7005S3 | SW;VDC | NEW | FIL | 9 | Lagrange FE | VDC_12 | Rider III baseline | 3044 | VBRAIN_CONFIG_2022-01-18
V-131 | Frequency Measures Threshold | Update the threshold of all frequency mesures inside the configurator. It has been modified <= and => with < and > The measuements involved are: EFR6081 EFR6082 EFR6083 EFR6084 EFR6091 EFR6092 EFR6071 EFR6072 EFR6073 EFR6074 EFR6075 EFR6076 EFR6077 EFR6001 EFR6002 EFR6003 EFR6004 EFR6142 EFR6242 EFR7071 EFR7072 | SW;VDC | NA | RES | 4 | Energy TGBT PLC (EV03) | VDC_12 | Rider III baseline | 3052 | VBRAIN_CONFIG_2022-01-18
V-132 | Modification Name Astrainte | The name of the Astraintes has been changed as follows and the measurements have been updated: - E = Energy VMC; - K = Air Conditioning VMC; - 8 = Fluidic VMC; - V = DVT / Gas Detection; - 6 = Infrastructures VMC; - S = SYNCER; - R = System VMC; | SW/VDC | NA | NA | NA | NA | VDC_12 | Rider III baseline | 3081 | VBRAIN_CONFIG_2022-01-18
V-133 | Deleted only from VDC the threshold | Only from VDC has been delete the threshold (LL: 0 ;HH=65535) and (LL= 0; HH=32767) for MA measures | VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-134 | Delete signals | Delete of the following signals VVV7010DI1 VVV7006DI1 VVV7008DI1 VVV7007DI1 VVV7007DI3 VVV7007DI5 VVV7007DI6 VVV7011DI1 VVV7012DI1 Modification of the following master alarm: HVAC19DMA HVAC20DMA HVAC21DMA | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3088 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-135 | Modification master alarm only from VDC | HVAC21DMA: DELETE FROM VDC VVV7007DI7 AND VVV7007DI8. THEY DON'T EXIST | VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-136 | Modification description signals | The description of the following signals have been replaced from“VC X SALLE XX LAGRANGE SONDE TEMPERATURE FAULT" to “VC X SALLE X USER INTERFACE AND SONDE TEMPERATURE FAULT” | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3088 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-137 | Modification scale factor | The scale factor of the following signal have been changed EWR7320R EWR7530R EWR7531R EWR7532R | SW;VDC | NEW | CAL | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3087 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-138 | Delete signals | Delete the following signals: ESA6161D ESA6162D ESA6121D ESA6122D ESA6041D ESA6115D ESA6161 ESA6162 ESA6121 ESA6122 ESA6041 ESA6115 The ESY6100DMA master alarm has been changed | SW;VDC | NA | RES | 4 | Energy TGBT PLC (EV03) | VDC_13 | Rider III baseline | 3093 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-139 | Modification description of the signals | Modification of the description of the signals as described in the following document: VG-SI-2212039-D-2104-CMY-1.6 PLC TGBT and UPS Interface with VMC | SW;VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3093 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-140 | Modification only from Configurator of the threshold | Regarding bug 3072, a query was made on SQL Management to replicate the threshold value "<=" with "<" | SW;VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3091 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-141 | Modification master alarm | The ESY6100DMA Master Alarm includes the following CR: ESA6520 ESA6720 ESA6535 EA6550 ESA6735 ESA6750 ESA6565 ESA6580 ESA6595 ESA6610 ESA6665 ESA6780 ESA6795 ESA6160 ESA6625 ESA6810 ESA6920 ESA6900 ESA6915 ESA6003 ESA6007 EQF6220F EQF6230F EQF6232F ESA6630 ESA6830 ESA6640 ESA6840 ESA6655 ESA6670 ESA6855 ESA6870 | SW;VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3095 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-142 | Modification of the description | The description of the following signals have been changed from 184-05-32 to 184-13-32 EQF7232 ESA7232 EIR7532I1 EIR7532I2 EIR7532I3 EIR7532IN EUR753212 EUR753223 EUR753231 EUR7532V1 EUR7532V2 EUR7532V3 EWR7532PF EFR7532 EWR7532R EWR7532Q EWR7532S | SW;VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3113 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-143 | Modification scale factor | Change the scale fator for the following measures: EWR7530Q EWR7530S EWR7531Q EWR7531S EWR7532Q EWR7532S EWR7320Q EWR7320S EWR6702AR EWR6702AQ EWR6702AS EWR6702BR EWR6702BQ EWR6702BS EWR6701R EWR6701Q EWR6701S EWR6703R EWR6703Q EWR6703S EWR6020R EWR6020Q EWR6020S EWR6021R EWR6021Q EWR6021S EWR6832R EWR6832Q EWR6832S EWR6833R EWR6833Q EWR6833S EWR6230R EWR6230Q EWR6230S EWR6231R EWR6231Q EWR6231S EWR6430R EWR6430Q EWR6430S EWR6431R EWR6431Q EWR6431S EWR6530R EWR6530Q EWR6530S EWR6531R EWR6531Q EWR6531S EWR6630R EWR6630Q EWR6630S EWR6631R EWR6631Q EWR6631S | SW;VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3150 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-144 | Modification scale factor | Change the scale factor of the following measures EWR6101R EWR6101Q EWR6101S EWR6102R EWR6102Q EWR6102S EWR6103R EWR6103Q EWR6103S EWR6104R EWR6104Q EWR6104S EWR6105R EWR6105Q EWR6105S EWR6106R EWR6106Q EWR6106S EWR6107R EWR6107Q EWR6107S EWR6108R EWR6108Q EWR6108S EWR6109R EWR6109Q EWR6109S EWR6110R EWR6110Q EWR6110S EWR6110R EWR6110Q EWR6110S EWR6111R EWR6111Q EWR6111S EWR6112R EWR6112Q EWR6112S EWR6113R EWR6113Q EWR6113S EWR6114R EWR6114Q EWR6114S EWR6115R EWR6115Q EWR6115S EWR6116R EWR6116Q EWR6116S EWR6117R EWR6117Q EWR6117S EWR6118R EWR6118Q EWR6118S EWR6119R EWR6119Q EWR6119S EWR6120R EWR6120Q EWR6120S EWR6121R EWR6121Q EWR6121S | SW;VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3150 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-145 | Modification scale factor | The scale factor of the following measures have been changed: VTR7007V2 VTR7007V4 EIR7071I1 EIR7071I2 EIR7071I3 EUR7071UBP EUR7071UBM EIR7072I1 EIR7072I2 EIR7072I3 EUR7072UBP EUR7072UBM | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3098 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-146 | Modification signals | The alarms threshold from the following analogic measures are to be deleted: VTR7006V1 VTR7008V1 VTR7007V1 VTR7007V2 VTR7007V3 VTR7007V4 VTR7007V5 VTR7007V6 VTR7011V1 VTR7012V1 The alarms thresholds for the following signals are to be modified with the following values: LOW<23; HIGH>27: VTR7005A1 VTR7010V1 VTR7013V1 VTR7005A2 VTR7010V2 VTR7013V2 | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3097 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-147 | Modification signals | The configuration of the following signals is reversed on VMC. The following signals have been reversed. VSY7020W1 VSY7020W2 VCD7014D1 EQF7530 (delete the reverse logic) ESA7530 EQF7531 (delete the reverse logic) ESA7531 EQF7232 (delete the reverse logic) ESA7232 EQF7320C (delete the reverse logic) ESA7320C VCD7014S5 | SW;VDC | NEW | NA | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3096 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-148 | Modification signals | Change the Type of the following measures from U16 to I16: HPR6310 RPR6305 | SW;VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_13 | Rider III baseline | 3070 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-149 | Modification command | Change the value of the Arret of the following command VCN7005CM101 VCN7005CA101 | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-150 | Modification signals | Data Type has been changed LZP7000D1 LZP7000D2 LZP7001D1 LZP7001D2 LZP7002D1 LZP7002D2 LZP7003D1 LZP7003D2 | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-151 | Deleted signals | The following signals are to be delated since not acquired from field: VCN7005DT1 VCN7005DT2 VVV7013DT1 VVV7013DT2 The HVAC19DMA master alarm has been changed | SW;VDC | NEW | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3109 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-152 | Modification signals | The following commands have been removed from clients publishing but not deleted because there is the possibility of using them for future implementations VVV7006CM101 VVV7006CA101 VVV7008CM101 VVV7008CA101 VVV7007CM101 VVV7007CA101 VVV7007CM103 VVV7007CA103 VVV7007CM105 VVV7007CA105 VVV7007CM106 VVV7007CA106 VVV7011CM101 VVV7011CA101 VVV7012CM101 VVV7012CA101 | SW;VDC | NA | RES | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3109 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-153 | Modification signals | The scale factor of the following measures has been changed EFR6242 EFR6142 EFR6002 EFR6004 EFR6001 EFR6003 | SW | NA | RES | 5 | Energy 1D60 PLC | VDC_13 | Rider III baseline | 3106 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-154 |  | The description of the following command has been changed: EQF6951 | SW/VDC | CCS | INT;RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3105 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-155 | Modification command | Has been set a delay for the group command VCF7000COGC | SW | NA | INT | NA | NA | VDC_13 | Rider III baseline | 3099 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-156 | Modification signals | Change the description and label of the following signals. VTR6601V1---VTR6801V1 VVV6601DT1---VVV6801DT1 VVV6601M1---VVV6801M1 The signal VVV6801DT1 has been inserted inside HVAC18DMA master alarm VTR6002V1---VTR6002V3 VVV6002M1--VVV6002M3 VVV6002DT1---VVV6002DT3 The signal VTR6002V3 and VVV6002DT3 have been inserted inside HVAC07DMA master alarm VTR6122V2---VTR6121V2 VVV6122M2--VVV6121M2 VVV6122DT2---VVV6121DT2 The signalS VTR6121V2 and VVV6121DT2 haVE been inserted inside HVAC09DMA master alarm | SW/VDC | NA | RES | 7 | HVAC MG PLC | VDC_13 | Rider III baseline | 3115 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-157 | Modification signals | For the following signals has been changed the description on the VMC Configurator EQF6667D, ESA6665, EQF6782D, ESA6780, EQF6797D, ESA6795, EQF6812D, ESA6810 | SW/VDC | NA | RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3107 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-158 | Modification signals | The configuration of the following signals is reversed on VMC synoptic with respect to field process: EQF7232 EQF7531 EQF7530 EQF7320C | SW/VDC | NA | FIL | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3096 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-159 | Modification signals | Wrong descrption of the following signals has been detected: VFN7013S3 VFN7010S3 VFN7005S3 VDC7014S5 VFN7013S2 VCN7014S2 VFN7010S2 VFN7005S2 VFN6002S1 VFN6004S1 VFN6007S1 VFN6008S1 VFN6009S1 VFN6010S1 VFN6012S1 VFN6013S1 VFN6014S1 VFN6002S2 VFN6004S2 VFN6007S2 VFN6008S2 VFN6009S2 VFN6010S2 VFN6012S2 VFN6013S2 VFN6014S2 VFN6002S3 VFN6004S3 VFN6007S3 VFN6008S3 VFN6009S3 VFN6010S3 VFN6012S3 VFN6013S3 VFN6014S3 VFN6002S4 VFN6004S4 VFN6007S4 VFN6008S4 VFN6009S4 VFN6010S4 VFN6012S4 VFN6013S4 VFN6014S4 VFN6101S1 VFN6109S1 VFN6111S1 VFN6112S1 VFN6113S1 VFN6117S1 VFN6101S2 VFN6109S2 VFN6113S2 VFN6117S2 VFN6101S3 VFN6109S3 VFN6113S3 VFN6117S3 VFN6101S4 VFN6109S4 VFN6111S4 VFN6112S4 VFN6113S4 VFN6117S4 | SW/VDC | NA | NA | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3110 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-160 | Modification signals | The addresses of the following measures have been reversed VRP6999F2 VRP6999F1 | SW/VDC | NA | RES | 7 | HVAC MG PLC | VDC_13 | Rider III baseline |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-161 | Modification signals | The following measurements have been removed from the client publication and the power formulas have been changed accordingly: EIR6702AI2 EIR6702AI3 EIR6702A EIR6702BI2 EIR6702BI3 EIR6702B EUR6702A12 EUR6702A23 EUR6702A31 EUR6702AV2 EUR6702AV3 EUR6702B12 EUR6702B23 EUR6702B31 EUR6702BV2 EUR6702BV3 | SW/VDC | NA | RES | 3 | Wire PLC | VDC_13 | Rider III baseline | 3063 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-162 | Elimination signal | Delete the following signals: VCT7020D | SW/VDC | NEW | FIL | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3109 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-163 | Modification of the master alarms | inside the DI63DMA master alarm the SZI6116W signal has been removed and it has been inserted inside the DI65DMA master alarm | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3120 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-164 | Modification of the master alarms | The following maesures have been delete from the DG64DMA master alarm SAV6102D ; SAV6104D ; SAV6106D ; SAV6107D ; SAV6108D | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3120 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-165 | DVT configurtion discrepancy | Change the scale factor of these signals: SORS014 SOR6015 SOR6017 SOR6018 SOR6019 SOR6022 | SW/VDC | CCS | RES | 3 | Wire PLC | VDC_13 | Rider III baseline | 3066 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-166 | incorrect description of the network analyzers. Lagrange signals | The description of the following signals have been modified, from TD TGBT 184-13-20 TO TGBT 184-13-20: EQF7320N ESA7320N EQF7320R ESA7320R EQF7320C ESA7320C EIR7320I1 EIR7320I2 EIR7320I3 EIR7320IN EUR732012 EUR732023 EUR732031 EUR7320V1 EUR7320V2 EUR7320V3 EWR7320PF EFR7320 EWR7320R EWR7320Q EWR7320S | SW/VDC | NEW | NA | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3113 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-167 | Signals not to be sent to the Syncer | Delete from PCP SCX7001GE SCX7002GE SWE7001F SWE7001O SWE7002F1 SWE7002O1 SWE7002F2 SWE7002O2 SDO7001W2 SDO7001N SDO7001D SDO7002W2 SDO7002N SDO7002D SDO7003W2 SDO7003N SDO7003D SDO7004W2 SDO7004N SDO7004D | SW/VDC | NEW | NA | 9 | Lagrange FE | VDC_13 | CCN CDL3 Disp. | 3130 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-168 | HVAC Depollution signal configuration discrepancies | The following measurements has been changed from bar to mbar. Consequently, the alarm threshold values ​​have been adjusted VPR6001 VPR6701 VPR6601 | SW/VDC | CCS | RES | 3 | Wire PLC | VDC_13 | Rider III baseline | 3121 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-169 | HVAC Depollution signal configuration discrepancies | The write value when the command is sent was inverted between the command CM and CF. VRU6004C VRU6009C VRU6007C VRU6013C VRU6008C VRU6101C VRU6112C VRU6103C VRU6113C VRU6111C VRU6115C VRU6116C | SW/VDC | CCS | FIL | NA | NA | VDC_13 | Rider III baseline | 3121 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-170 | HVAC Depollution signal configuration discrepancies | The default value that the command has when it's to execute in automaticly mode has been changed. VRU6004C VRU6009C VRU6007C VRU6013C VRU6008C VRU6101C VRU6112C VRU6103C VRU6113C VRU6111C VRU6115C VRU6116C | SW/VDC | CCS | FIL | NA | NA | VDC_13 | Rider III baseline | 3121 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-171 | Incorrect management of the master alarms associated with the nodes | The following master alarms have been removed: SCG7000DMA (has been modified the SCG6DMA Master alarm) SCX7000DMA (has been modified the SCX6DMA Master alarm) EQF6001DMA (has been modified the ETH6100DMA Master alarm) EZC6325DMA121 EZC6325DMA120 EZC6325DMA130 EZC6325DMA131 EZC6325DMA230 EZC6325DMA231 EZC6325DMA530 EZC6325DMA531 EZC6325DMA630 EZC6325DMA631 EZC6325DMA41 EZC6325DMA43 EZC6325DMA132 EZC6325DMA133 EZC6325ADMA42 EZC6325BDMA42 (for all "EZC6325DMAXXX) has been modified the EZC6325DMA master alarm) ESY6101DMA ESY6102DMA ESY6103DMA ESY6104DMA ESY6105DMA ESY6106DMA ESY6107DMA ESY6108DMA ESY6109DMA ESY6110DMA ESY6111DMA ESY6112DMA ESY6113DMA ESY6114DMA ESY6115DMA ESY6116DMA ESY6117DMA ESY6118DMA ESY6119DMA ESY6120DMA ESY6121DMA (for all "EZSY61XXDMA) has been modified the ESY6100DMA master alarm) MG64DMA ZZZ6030DMA | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3132 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-172 | Incorrect management of the master alarms associated with the nodes | The DG71DMA master alarm has been insered in the SCG6DMA master alarm. The EI77DMA master alarm has been inserted in the SCX6DMA master alarm. The following alarms have been inserted in the EZC6325DMA master alarm: EZC6325D121;EZC6325D120;EZC6325D130;EZC6325D131;EZC6325D230;EZC6325D231;EZC6325D530;EZC6325D531;EZC6325D630;EZC6325D631;EZC6325D41;EZC6325D43;EZC6325D132;EZC6325D133;EZC6325AD42;EZC6325BD42 The following alarms have been inserted in the ESY6100DMA master alarm: ESY6101D;ESY6102D;ESY6103D;ESY6104D;ESY6105D;ESY6106D;ESY6107D;ESY6108D;ESY6109D;ESY6110D;ESY6111D;ESY6112D;ESY6113D;ESY6114D;ESY6115D;ESY6116D;ESY6117D;ESY6118D;ESY6119D;ESY6120D;ESY6121D | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3132 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-173 |  | The ESY6100DMA master alarm has been updated in the VDC congruently with what is configured | VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-174 | Modification Bunker and Gantry Cmds Depollution, Extin and Balayage | The master alarms of the two nodes(HVAC11DMA and HVAC15DMA) have been updated by inserting following measures: HVAC11DMA: VRU6004D;VRU6007D;VRU6008D;VRU6009D;VRU6213D;VRU6101D1;VRU6103D;VRU6111D;VRU6112D;VRU6113D;VRU6115D;VRU6116D HVAC16DMA: VRU6502D;VRU6201D;VRU6101D2;VZU6601D;VZN6701D; | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3139 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-175 | Wrong description of Desenfumage ZLV signals | Change the description of ALL the Following measures. The new desciprion is: Etat selecteur du moteur ON VFN6002S1 VFN6004S1 VFN6007S1 VFN6008S1 VFN6009S1 VFN6010S1 VFN6012S1 VFN6013S1 VFN6014S1 VFN6101S1 VFN6109S1 VFN6111S1 VFN6112S1 VFN6113S1 VFN6117S1 | SW/VDC | NA | RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3138 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-176 | Wrong description of Desenfumage ZLV signals | Change the description of ALL the following measures. The new desciprion is: Alimentation Ordninys FAULT (400 V). The type of the following measures has been changed (From CR to AL) and the VFN6000DMA master alarm has been updated: VFN6002S2 VFN6004S2 VFN6007S2 VFN6008S2 VFN6009S2 VFN6010S2 VFN6012S2 VFN6013S2 VFN6014S2 VFN6101S2 VFN6109S2 VFN6113S2 VFN6117S2 | SW/VDC | NA | RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3138 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-177 | Wrong description of Desenfumage ZLV signals | Change the description of ALL the following measures. The new desciprion is: Desenfumage 002 Alimentation auxiliaires ON (48 V) VFN6002D1 VFN6004D1 VFN6007D1 VFN6008D1 VFN6009D1 VFN6010D1 VFN6012D1 VFN6013D1 VFN6014D1 VFN6101D1 VFN6109D1 VFN6113D1 VFN6117D1 | SW/VDC | NA | RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3138 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-178 | Wrong description of Desenfumage ZLV signals | The description of the following signals have also been renamed as Desenfumage XXX Désenfumage en marche: VFN6002S4 VFN6004S4 VFN6007S4 VFN6008S4 VFN6009S4 VFN6010S4 VFN6012S4 VFN6013S4 VFN6014S4 VFN6101S4 VFN6109S4 VFN6111S4 VFN6112S4 VFN6113S4 VFN6117S4 | SW/VDC | NA | RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3138 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-179 | Wrong description of Desenfumage ZLV signals | The description of the following signals have also been renamed as Desenfumage XXX Volet Ouvert: VFN6002S3 VFN6004S3 VFN6007S3 VFN6008S3 VFN6009S3 VFN6010S3 VFN6012S3 VFN6013S3 VFN6014S3 VFN6101S3 VFN6109S3 VFN6113S3 VFN6117S3 | SW/VDC | NA | RES | 4 | Energy TGBT PLC | VDC_13 | Rider III baseline | 3138 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-180 | Redundant synoptics | Has been deleted the VG06DMA alarm and VG08DMA master alarm. The remaining master alarms have been renamed. The master alarm VG6DMA has been update | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3137 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-181 | VALIDITY UPDATE | Validity of measures relevant to Bunker AC Cabinet Communication Default: VCN6007DC1 VCN6013DC1 VCN6101DC1 VCN6103DC1 VCN6113DC1 VCN6116DC1 VCN6002DC1 VCN6004DC1 VCN6007DC2 VCN6101DC2 VCN6103DC2 VCN6113DC2 VCN6116DC2 VCN6002DC2 VCN6004DC2 has to be modify respectively as follows: VZC6126K32 VZC6126K08 VZC6126K08 VZC6126K08 VZC6126K08 VZC6126K08 VZC6126K08 VZC6126K08 VZC6126K08 VZC6126K32 VZC6126K32 VZC6126K32 VZC6126K32 VZC6126K32 VZC6126K32 | VDC | NA | RES | 6 | HVAC Bunker PLC | VDC_13 | Rider III baseline | 3051 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-182 |  | The description of the following signals have also been renamed as:Desenfumage XXX Interrupteur alimentation ON VFN6111S1,VFN6112S1 The description of the following signals have also been renamed as:Desenfumage XXX Interrupteur alimentation FAULT VFN6111D1,VFN6112D1, | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3138 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-183 | Modification the Low2 and High2 values | Have been changed the values of the Low2 and High2 of the following measures. The new values are Low2:24/High2:26 VEGA BUNKER PLC : RETURN TEMPERATURE FAN COIL (AERMEC) VEGA BUNKER PLC : TEMPERATURE FAN COIL (AERMEC) VEGA BUNKER PLC : TEMPERATURE AC CABINET (STULZ) VEGA BUNKER PLC : TEMPERATURE AC CABINET (SCHNEIDER) | SW/VDC | NA | RES | 6 | HVAC Bunker PLC (CV0B) | VDC_13 | Rider III baseline | 3148 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-184 | Modification scale factor | The scale factor of the following measures have been changed: the value was divided by 10 SOR6016 SOR6020 SOR6021 | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_13 | Rider III baseline | 3066 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-185 | Vbrain Configurator modification only | Master alarms have been removed from VBrain_CLient _Logger | SW | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3144 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-186 | Delete Inhibition of the commands | All commands have been uninhibited | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3149 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-187 | Modification Name Astrainte | The name of the astrainte has been inserted as follow and the measurements have been updated: - U = API VMC; | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3093 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-188 | New allarms | The following allarms have been configured under astrainte U: ZJG6104;ZJG6105;ZJG6106;ZJG6107;ZJG6108;ZJG6109;ZJG6110;ZJG6111;ZJG6112 | SW/VDC | NEW | INT | 0 | VMC Front-End PLC | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-189 | Modification type measure | The ZJM6103 has been configured as Alarm and has been assigned to R astrainte. The ZJP6103DMA master alarm has been updated | SW/VDC | NEW | INT | 0 | VMC Front-End PLC | VDC_13 | Rider III baseline | 3143 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-190 | Modification master alarms-astrainte | The following master alarms have been sended to astrainte The astrainte "R": ZZZ6DMA0;ZZZ6DMA1;ZZZ6DMA2;ZZZ6DMA3;ZZZ6DMA4;ZZZ6DMA5;ZZZ6DMA6;ZZZ6DMA7;ZZZ6DMA8;ZZZ6DMA | SW/VDC | NEW | CAL | 0 | VMC Front-End PLC | VDC_13 | Rider III baseline | 3145 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-191 | Modification master alarms | The DG60DMA master alarm has been modified. Has been inserted the ZJG6104 alarm | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-192 | Modification master alarms | The W60DMA master alarm has been modified. Has been inserted the ZJG6105 | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-193 | Modification master alarms | The VG10DMA master alarm has been modified. Has been inserted the ZJG6106 | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-194 | Modification master alarms | The EZC6115DMA1 master alarm has been modified. Has been inserted the ZJG6107 | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-195 | Modification master alarms | The EZC6160DMA master alarm has been modified. Has been inserted the ZJG6108 | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-196 | Modification master alarms | The VZC6126DMA master alarm has been modified. Has been inserted the ZJG6109 and ZJG6110 | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-197 | Modification master alarms | The VZC6401DMA master alarm has been modified. Has been inserted the ZJG6110 and ZJG6112 | SW/VDC | NA | CAL | NA | NA | VDC_13 | Rider III baseline | 3142 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-198 | Modification of the description | The description of the following measures have been modified: SCK7001D: Defaut Lagrange Detection Alarm / Fault SZI7000D: Defaut Lagrange Detection OFF/TEST SZI7000DE:Defaut Lagrange Emergency Power SCK7000DH: Defaut Lagrange Detection Hardware Fault SCK7000D: Defaut Lagrange Detection Fault | SW/VDC | NA | RES | NA | NA | VDC_13 | Rider III baseline | 3146 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-199 | Synoptics renamed | VG13 has been renamed as VG 12 ETAT WIRE API VG12 has been renamed as E66 Eclairage Ambiance Lanceur E66 has been renamed as MG74 Niveau Chateau eau VEGA. Has been modified the name of the nodes in the configuration. The measures in the vdc have been associated with the updated synoptic | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3135 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-200 | Synoptics renamed | VG06 AND VG08 synoptics have been deleted. The number of nodes has been updated and also the associated master alarms. For this reasons the following synoptics have been reneamed: VG07 has been renamed as VG06; VG08 has been renamed as VG07; VG09 has been renamed as VG08; VG11 has been renamed as VG09; VG12 has been renamed as VG10; The measures in the vdc have been associated with the updated synoptic | SW/VDC | NA | NA | NA | NA | VDC_13 | Rider III baseline | 3137 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-201 | Updating of validity measures | The measures of validity were associated with the following measures: SOR6006: SAV6102D SOR6007: SAV6102D SOR6011: SAV6104D SOR6012: SAV6104D SOR6013: SAV6104D VPR6601: ZZN6014 VPR6701: ZZN6014 VPR6001: ZZN6014 | SW/VDC | CCS | RES | 3 | Wire PLC | VDC_13 | Rider III baseline | 3071 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-202 | Modification measures | The following measures have been sended to astrainte K: VTR6002A1 VTR6001V1 | SW/VDC | NA | RES | 6 | HVAC Bunker PLC (CV0B) | VDC_13 | Rider III baseline | 3147 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-203 | Delete measures | Delete the following measures: LZL7000P LZL7000S Update the ZLG6DMA master alarm. | SW/VDC | NEW | RES | 9 | Lagrange FE | VDC_13 |  | 3141 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-204 | Modificaton measures | The following measures have been removed from K astrainte: VTR6100V1;VTR6002V3;VTR6106V2;VTR6004V1;VTR6105V2;VTR6106V1;VTR6006V2;VTR6108V1;VTR6122V1;VTR6115V2;VTR6117V1;VTR6115V1;VTR6120V1;VTR6121V1;VTR6012V1;VTR6126V1;VTR6118V5;VTR6118V4;VTR6118V3;VTR6121V2;VTR6007A1;VTR6101A1;VTR6013A1;VTR6103A1;VTR6113A1;VTR6116A1;VTR6002A1;VTR6004A1;VTR6118V1;VTR6118V2;VTR6115V3;VTR6115V4;VTR6117V2;VTR6112V1;VTR6111V1;VTR6108V2;VTR6108V3;VTR6107V1;VTR6106V3;VTR6106V4;VTR6105V1;VTR6121V3;VTR6104V1;VTR6100V2;VTR6012V2;VTR6006V1;VTR6006V3;VTR6004V3;VTR6002V2;VTR6007A2;VTR6101A2;VTR6103A2;VTR6113A2;VTR6116A2;VTR6001V1;VTR6008V1;VTR6009V1;VTR6002A2;VTR6004A2 | SW/VDC | NA | RES | 6 | HVAC Bunker PLC (CV0B) | VDC_13 | Rider III baseline | 3147 | VBRAIN_CONFIG_2022-03-10_20-45-35
V-205 | Description changed | The description of the following command has been changed SCE6012CM | SW/VDC | CCS | FIL | NA | NA | VDC_13 | Rider III baseline |  | VBRAIN_CONFIG_2022-03-10_20-45-35
V-206 | Modification Signals | The following measures have been configured with logic negated NCL6001A;UCL6001A | SW/VDC | CCS | FIL | NA | NA | VDC_14 | Rider III baseline | 3166
V-207 | Modification Master alarm | From EZC6325DMA master alarm has been removed the ZZE6005 alarm. | SW/VDC | NA | CAL | NA | NA | VDC_14 | Rider III baseline | 3167
V-208 | Modification Signal | The ZZE6009 measure has been renamed as ZZE6010. The master alarms associated to ZZE6010 measurement that have been modified are: MG61DMA;MG62DMA;MG63DMA;MG68DMA;VG01DMA;VG10DMA | SW/VDC | NA | NA | NA | NA | VDC_14 | Rider III baseline | 3168
V-210 | Modification Signals | The following measures have been removed from K astrainte and have been modified as CR: VZU6601D VZN6701D | SW/VDC | NA | NA | NA | HVAC MG PLC (CV0G) | VDC_14 | Rider III baseline | 3169
V-211 | Modification Signals | SOR7001;SOR7002;SOR7003;SOR7004: description changed | SW/VDC | NEW | RES | 9 | Lagrange FE | VDC_14 | CCN CDL3 Disp. | 3170
V-212 | Modification Signals | The following signals have been removed from "Infrastructures VMC" astraint: EQF6001MO;EQF6004MO | SW/VDC | NA | RES | 4 | Energy TGBT PLC (EV03) | VDC_14 | Rider III baseline | 3169
V-213 | Modification Signals | Only inside the Vbrain Configuration, for the following signals,the Safety and Energy users have been inserted as Authorized users to ACK: EQF6001D,EQF6001DE,EQF6001MO,EQF6001F,EQF6001O; EQF6002D,EQF6002DE,EQF6002MO,EQF6002F,EQF6002O; EQF6950D,EQF6950DE,EQF6950F,EQF6950O; EQF6951D,EQF6951DE,EQF6951F,EQF6951O;EQF6951M EQF6003D,EQF6003DE,EQF6003F,EQF6003O; EQF6952D,EQF6952DE,EQF6952F,EQF6952O; | SW | NA | RES | 4 | Energy TGBT PLC (EV03) | VDC_14 | Rider III baseline | 3171
V-214 | Modification Signals | The following measures have been removed from "R" astrainted and have been inserted inside "U" astrainte: LZS7100D;LZS7200D;LZS7300D;LZS7400D | SW/VDC | NEW | RES | 9 | Lagrange FE | VDC_14 | CCN CDL3 Disp. | 3169
V-215 | Modification Signal | The following signal has been removed from "R" astraint: ZJM6103 | SW/VDC | NEW | INT | 9 | Lagrange FE | VDC_14 | CCN CDL3 Disp. | 3169
V-216 | Modification Signal | From EQMT6002AE and EQMT6001AE measures have been removed from the formula the following measures: EQT6002F and EQT6001F | VDC | NA | CALC | NA | NA | VDC_14 | Rider III baseline | 3172
V-217 | Deleting Signal | Deleting the following signals: EQT6001F;EQT6002F | SW/VDC | NA | RES | 5 | Energy 1D60 PLC | VDC_14 | Rider III baseline | 3172
V-218 | Deleting Signal | Deleting the following master alarm: VZC6100DMA;VZC6200DMA | SW/VDC | NA | CALC | NA | NA | VDC_14 | Rider III baseline | 3174
V-219 | Modification master alarm | From HVAC02DMA master alarm has been removed the VZC6401D alarm and have been inserted the following alarms: VSY6900W1; VSY6900W2 | SW/VDC | NA | CALC | NA | NA | VDC_14 | Rider III baseline | 3173
V-219 | Modification master alarm | From the following master alarms, have been removed the VSY6600W1, VSY6600W2,VSY6900W1 and VSY6900W2 alarms: HVAC03DMA;GGF6DMA;HVAC04DMA;HVAC05DMA;HVAC06DMA;HVAC07DMA;HVAC08DMA;HVAC09DMA;HVAC10DMA;HVAC11DMA;HVAC12DMA;HVAC13DMA;HVAC14DMA;HVAC15DMA;HVAC16DMA;HVAC17DMA;HVAC18DMA;VG09DMA | SW/VDC | NA | CALC | NA | NA | VDC_14 | Rider III baseline | 3175
V-220 | Modification signal | For ZCM6734P2 alarm, has been changed the condition of alarm (HH) | SW/VDC | NA | INT | NA | NA | VDC_14 | CCN CDL3 Disp. | 3176
V-221 | Addition new users | New users have been created to which the appropriate measures / commands have been associated: - S = Sauvegarde; - D = DETG; - I = Infrastructure; - A = APITeam; | SW/VDC | NA | NA | NA | NA | VDC_14 | Rider III baseline | 3177
V-222 | Modification description signals | The description of the following signals has been changed. "Syncer" has been replaced with "SCSI": ZNC6633NH1;ZNC6628NH1;ZNC6629NH1 | SW/VDC | NEW | INT | NA | NA | VDC_14 | Rider III baseline | 3179
V-223 | Modification measures | Query to set deadbeand value to current, voltage, power factor, Power (R,S,Q) measuements analogic. | SW | NA | NA | NA | NA | VDC_15.0 | CCN CDL3 Disp. | 3166
V-224 | Addition new signals and command | Addition new signals and command for the G.E. system | SW/VDC | NEW | TIP | 10 | Groupe életgrogène | VDC_15.0 | CCN CDL3 Disp. | 3167
V-225 | Modification master alarm | The EZC7000DMA master alarm has been modified, has been inserted the new master alarm of groupe electrogene: GE01DMA | SW/VDC | NEW | CAL | NA | NA | VDC_15.0 | CCN CDL3 Disp. | 3167
V-226 | Modification measures | The scale factor of the following signals have been modified: EWR7071S EWR7072S | SW/VDC | NEW | RES | 9 | Lagrange FE | VDC_15.0 | Rider III baseline | 3165
V-227 | Modification description | The description of the following command has been changed: WCO6005CM | SW | CCS | INT | 2 | O&V PLC | VDC_15.0 | Rider III baseline | 3168
V-228 | Alarm to astainte | The EKM7003 alarm is sent to astrainte Energy "E" | SW/VDC | NEW | TIP | 10 | Groupe életgrogène | VDC_15.0 | CCN CDL3 Disp. | 3167
V-229 | Modification GE driver acquisition parameters | Inside the VMC Configurator has been changed the value of the following parameters related to GE driver acquisition: Hopes: 5 Max Reg For Req:5 | SW | NEW | TIP | 10 | Groupe életgrogène | VDC_15.0 | CCN CDL3 Disp. | 3167
V-230 | Modification of scale factor | The scale factor of the SOR6016,SOR6020 AND SOR6021 measures have been updated (x/10) only inside software. | SW | CCS | RES | 3 | Wire PLC (SV01) | VDC_15.0 | Rider III baseline | SV21/236
V-231 | Modification GE measures | The addresses of the electrogene group have been changed. The alarm condition for EKM7003 signal has been eliminated and it will not be sent to astrainte E. Two alarms: EKM7004W and EKM7003W have been eliminated and the GE01DMA master alarm has been modified. For all the measures, the Safety and Energy Users have been inserted in the configuration server in the “Authorized users to ack” setting. | SW/VDC | NEW | TIP | 10 | Groupe életgrogène | VDC_15.1 | CCN CDL3 Disp. | 3167
V-232 | New parameter: Alarm Persistence Value configured | Has been inserted a value inside the Alarm Persistence Value setting for the following measures: SAV6100D SAV6106D SAV6107D SAV6108D | SW/VDC | NA | NA | NA | NA
V-232 | Deleting wrong dead band value for two power factor measurements | For the following measures has been deleted the wrong value related to dead band settings, according to all power factor measurements EWR6077PF;EWR6101PF | SW/VDC | NA | RES | NA | NA | VDC_15.1 | Rider III baseline | 3166
V-233 | Modification measurement | For the EWR6101PF measurement, the Safety user has been entered in the configuration server in the "Authorized users to ack" setting. | SW | NA | NA | NA | NA | VDC_15.1 | Rider III baseline | NA
V-234 | Timing value DVT measurements cm4 | In the "Alarm Persistent value" satting a timing parameter equal to 5 sec has been inserted for the alarms and defaut signals relating to the CM4 | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_15.1 | CCN CDL3 Disp. | SV21/234 236-237-218
V-235 | Modification of the calibration formula for CLIM measurements | For the measure: VPR6701,VPR6001 and VPR6601 has been chenged the calibration formula: y = 0,001x - 10,008 | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_15.1 | Rider III baseline | SV21/275
V-236 | Change of DVT measurement type | Change of measurement type from U16 to I16 SOR6003;SOR6004;SOR6005;SOR6006;SOR6007;SOR6008;SOR6009;SOR6010;SOR6011;SOR6012;SOR6013;SOR6014;SOR6015;SOR6016;SOR6017;SOR6018;SOR6019;SOR6020;SOR6021;SOR6022;SOR6023;SOR6024 | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_16 | Rider III baseline | SV21/324
V-237 | Cancellation of the low alarm threshold | Cancellation of the low alarm threshold for the following measures SOR6003;SOR6004;SOR6005;SOR6006;SOR6007;SOR6008;SOR6009;SOR6010;SOR6011;SOR6012;SOR6013;SOR6014;SOR6015;SOR6016;SOR6017;SOR6018;SOR6019;SOR6020;SOR6021;SOR6022;SOR6023;SOR6024 | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_16 | Rider III baseline | SV21/324
V-238 | Deleting measures | Deleting the following measures: ESY6930W;ESY6931W;ESY6940W;ESY6941W;ESY6950W;ESY6951W;ESY6960W;ESY6961W | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_16 | Rider III baseline | 3174
V-239 | Denied logic of the measures | The following measures must be set to logic negated: ESY6930D;ESY6931D;ESY6940D;ESY6941D;ESY6950D;ESY6951D;ESY6960D;ESY6961D | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_16 | Rider III baseline | 3174
V-240 | Deleting measures | Deleting of the following signals: ESY6970D;ESY6980D | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_16 | Rider III baseline | 3174
V-241 | Modification description DVT measures | Change the description of the DVT portique measures related to concentration and alarms | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_16 | Rider III baseline | 3176
V-242 | Query to align the database | Query execution to set the user (according to the subsystem to which they belong) to those measures that did not have it before | SW | NA | NA | NA | NA | VDC_16
V-243 | Delated alarm and measure DVT\DETG | The following measures related to CM4-7 have been delated: SAV6107D, SAV6107M,SDU6042D,SDU6042W ,SDU6043D,SDU6043W,SOR6107 SOR6207 | SW/VDC | CCS | RES | 3.1 | Wire PLC (SV01) GAS and Fire Detection PLC (IV01) | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-244 | Modification description DVT\DETG measures | The description of measures related to CM4-6/7/8 have been changed and replace with CL8-3/4 | SW/VDC | CCS | RES | 3.1 | Wire PLC (SV01) GAS and Fire Detection PLC (IV01) | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-245 | Modification validity DVT measures | The new validity of the following measures is SAV6106D: SAV6017W,SOR6017,SAV6018W,SOR6018,SAV6022W,SOR6022 | VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-246 | Modification Master alarm DETG | The DG65DMA master alarm has been modified: The description has been changed and has been delated the following alarms: SAV6107D,SDU6042D,SDU6042W,SDU6043D,SDU6043W,SOR6107 SOR6207 | SW/VDC | CCS | RES | 3.1 | Wire PLC (SV01) GAS and Fire Detection PLC (IV01) | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-247 | Timing threshold removing measures DVT | The workaround proposed to mitigate the anomaly “FA SV21/218” consisting in configuration of a timing threshold of “5 sec.” for following alarms, acquired via the “WIRE” PLC, is removed: SAV6100D;SAV6106D;SAV6108D;SAV6014W;SAV6015W;SAV6016W;SAV6017W;SAV6018W;SAV6019W;SAV6020W;SAV6021W;SAV6022W | SW/VDC | CCS | RES | 3 | Wire PLC (SV01) | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-248 | Deleting alarms to SCSI and SAAA | SAV6107D,SDU6042W and SDU6043W alarms will be not sent to SCSI and SAAA | SW/VDC | CCS | RES | 3.1 | Wire PLC (SV01) GAS and Fire Detection PLC (IV01) | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-249 | Modification NODE name DG65 | Change "DG65 Concentration Lie CM4" to "DG65 Concentration Lie CL8" inside HMI Client Configuration | SW | NA | NA | NA | NA | VDC_17.1 | VG-CP-SYS-1274-R0 - F044-00504-R1
V-250 | Modification description DVT\DETG measures | The description of the following measures and commands have been changed: SSP6001QC;SSP6001QM;SSP6001CCQ;SSP6001CMQ | SW/VDC | CCS | FIL | NA | NA | VDC_17.1 |  | As per AVIO Sauvegarde Remarks
V-251 | Modification FEOffset ADS register of VMC measures | The FEOffset ADS registers of the following measurements have been modified: ZZZ6941M174;ZZZ6324M172;ZZZ6324M173;ZZZ6324M175 | SW/VDC | NA | INT | NA | NA | VDC_18 V1.0
V-252 | Configuration WIS signals | Configuration WIS signals | SW/VDC | NA | NA | NA | NA | VDC_18 V1.0
V-253 | Modification Master alarm VMC01 | ZZZ6DMA10 MASTER ALARM has been inserted in the ZJP6103DMA Master Alarm | SW/VDC | NA | NA | NA | NA | VDC_18 V1.0
V-254 | Inhibition Commands | Have been configured the following commands with inhibition conditions: OVP6406CO;OVP6407CO;OVP6408CO;OVP6414CO;OVP6415CO;OVP6416CO;OVP6406CF;OVP6407CF;OVP6408CF;OVP6414CF;OVP6415CF;OVP6416CF;ZZC6000CM;ZZC6001CM | SW/VDC | NA | NA | NA | NA | VDC_18 V1.0
V-255 | Configuration Commands WIS | Have been configured the following commands to use in automatic reaction: ZZC6002CO;ZZC6002CN | SW/VDC | NA | INT | NA | NA | VDC_18 V1.0
V-256 | Configuration aggregate measure | Has been configured the ZZC6006M meausure to send with an automatic reaction the ZZC6002CO command when it's a true | SW/VDC | NA | INT | NA | NA | VDC_18 V1.0
V-257 | Configuration automatic reaction | The following analog measures are involved in automatic reaction: ONR6401;ONR6402;ONR6403;ONR6404:OPR6402;OPR6403;OPR6405;OPR6406;OPR6407:OPR6408 | SW/VDC | NA | INT | NA | NA | VDC_18 V1.0
V-258 | VMC Master Alarm modified | ZJP6103DMA master alarm has been modified: ZZZ6DMA10 master alarm has been added | SW/VDC | NA | CALC | NA | NA | VDC_18 V1.0
V-259 | Modification calibration form for Analog Measures WIS | For all WIS analog measures, the calibration form has been modified. ZZC6006M aggregate meausure has been updated and has been modified the description | SW/VDC | NA | NA | NA | NA | VDC_18 V1.0.1 |  | BUG WIS-009
V-260 | Updating WIS command address | The FEOffset ADS address and FEBIT ADS of the following commands have been updated: ZZC6000CM;ZZC6001CM; The FEOffset ADS address of the following commands have been updated ZZC6002CO;ZZC6002CN | SW/VDC | NA | INT | NA | NA | VDC_18 V1.0.1
V-261 | Updating WIS measures address | The FE Reg address of the following measures have been updated: ZZZ6941M174;ZZZ6324M172;ZZZ6324M173;ZZZ6324M175 | SW | NA | NA | NA | NA | VDC_18 V1.0.1
V-262 | Updating WIS command address | The FEOffset ADS address and FEBIT ADS of the following commands have been updated: ZZC6000CM;ZZC6001CM; | SW/VDC | NA | INT | NA | NA | VDC_18 V1.1 |  | WIS 007
V-263 | Adding WIS measure | WIS sequence automatic countdown measure has been added: ZZC6003M | SW/VDC | NA | INT | NA | NA | VDC_18 V1.1 |  | TASK 12
V-264 | Modification WIS measures | The description of the WIS FRONT-END modules has been modified, adding "WIS" text | SW/VDC | NA | INT | NA | NA | VDC_18 V1.1
V-265 | Modification of the calibration law and the threshold values ​​of Analog measurements WIS | The calibration form and the value of the analog measurement thresholds have been changed. Furthermore, the aggregate measurement ZZC6006M has been updated | SW/VDC | NA | NA | NA | NA | VDC_18 V.1.2 |  | WIS-014
V-266 | Modification register of GE | The Field Register has been changed for the EKM7002 measure (from 1057 to 1059) | SW/VDC | NA | TIP | 10 | NA | VDC_18 V.1.2 |  | FA n° SV22-190
V-267 | Modify authorized user - WIS signals | Change the user authorized from Fluidic operator to VMC operator: ZJA6001;ZZC6001N;ZJA6002;ZZC6001R;ZZC6002D;ZJA6000;ZZC6001M;ZZC6002M;ZZC6000M;ZZC6003O;ZZC6002CO;ZZC6002CN;ZZC6003M | SW/VDC | NA | NA | NA | NA | VDC_19 V1.0
V-268 | Modification FERegister of WIS signals | Wrong FERegister of the ZZC6002CO\ZZC6002CN command: from17511 to 17515 | VDC | NA | NA | NA | NA | VDC_19 V1.0
V-269 | Modification descriptions - WIS signals | Modified the description of the following signals: ZJA6001;ZJA6002;OPR6407AI;OPR6408AI;ZZC6002D;ZZC6002M;ZZC6002CO;ZZC6002CN | SW/VDC | NA | NA | NA | NA | VDC_19 V1.0
V-270 | Adding GE signal to astrainte | ECN7000W insert in the VBrain Notifier under “Energy” astrainte | SW | NA | TIP | 10 | Groupe életgrogène | VDC_19 V1.0 |  | WIS-06
V-271 | Automatic Reaction Modified | The automatic reaction of the ZZC6002CN command has been modified. The new condition is ZZC6006M = 0 | SW/VDC | NA | NA | NA | NA | VDC_19 V1.0 |  | WIS-07
V-272 | Modified WIS level sensor calibration law | Calibration law of ONR6401, ONR6402 and ONR6404 modified. Has been updated also ZZC6006M aggregate measure | SW/VDC | NA | NA | NA | NA | VDC_19 V1.1
V-273 | Modified WIS alarm thresholds | The alarm thresholds of the following analog measurements have been updated: ONR6401AI;ONR6402AI;ONR6403AI;ONR6404AI;OPR6401AI;OPR6402AI;OPR6403AI;OPR6404AI;OPR6405AI;OPR6406AI;OPR6407AI;OPR6408AI. Has been updated also ZZC6006M aggregate measure | SW/VDC | NA | NA | NA | NA | VDC_19 V1.1
V-274 | Changing the acquisition times of WIS analog measurements | The cycle time of the analog measurements acquired in ADS Normal and Notification Thread has been changed to 100 ms. The ADS driver and the Notification thread cycle time have also been updated to 100 ms | SW/VDC | NA | NA | NA | NA | VDC_19 V1.1
V-275 | Signals to send to the astrainte DETG | The following signals are sent to the DETG astrainte: SDO6001D;SDO6002D;SDO6003D;SDO6004D;SDO6005D; SDO6006D;SDO6007D;SDO6008D;SDO6009D;SDO6010D; SDO6011D;SDO6012D;SDO6013D;SDO6014D;SDO6015D; SDO6016D;SDO6017D;SDO6018D;SDO6019D;SDO6020D; SDO6021D;SDO6022D;SDO6023D;SDO6024D;SDO6025D; SDO6026D;SDO6027D;SDO6028D;SDO6029D | SW/VDC | CCS | RES | 1 | GAS and Fire Detection PLC (IV01) | VDC_20 V1.0 |  | SV23-181
V-276 | Thresholds modification | The thresholds of the following measures has been modified: RPR6301 (LL:0 bar; HH 6.6 bar); RPD6301 (HH:0,2 bar) | SW/VDC | CCS | FIL | NA | NA | VDC_20 V1.0 |  | SV23-087
V-277 | VDC-Modification on calibration form | Only on VDC file the form of the RPR6301 has been modified ((((1/2048)*x+4)-4)/1.6) coherently with VMC database | VDC | NA | NA | NA | NA | VDC_20 V1.0
V-278 | Typo in descriptions | Typo in the description of measures relating to the Detection Incendie (DI) Lagrange node. | SW | NA | NA | NA | NA | VDC_21 V1.0
V-279 | Addition of CR-AL NEWTON | Addition of CR-AL for Newton | SW/VDC | NEW | RES | 9 | Lagrange FE | VDC_21 V1.0
V-280 | Addition of MASTER ALARM | DI79DMA has been created as master alarm realtive to the fire detection alarms of the Newton builing | SW/VDC | NEW | RES | 10 | Lagrange FE | VDC_21 V1.0
V-281 | Modification of MASTER ALARM | SCK7000DMA ha been modified the master alarm has been modified for the insertion of the master alarm DI79 | SW/VDC | NA | NA | NA | NA | VDC_21 V1.0
V-282 | Typo in FE MODULE | Typo in the FE Module section for the OVP6305CO measure only in VDC | VDC | CCS | FIL | NA | NA | VDC_21 V1.0
V-283 | SAAA Measure modification | ZSA6629SH1 has been removed from ZIF6DMA Master Alarm and Clients; ZSA6628SH1, ZSA6633SH1 description modified; ZSA6633SH1 has been added to astrainte ( R ) VMC | SW/VDC | NEW | INT | NA | NA | VDC_21 V1.2 | VG-CP-SYS-1583-R0 - F004-00516-D-R0
V-284 | Lagrange - Pandora switch Ports | The alarms condition of the following alarms is chenaged as "UP": ZCM6840P8; ZCM6841P8,ZCM6734P4,ZCM6734P8,ZCM6734P12,ZCM6735P4,ZCM6735P8,ZCM6735P12 | SW/VDC | NEW | INT | NA | NA | VDC_21 V1.2 | VG-CP-SYS-1583-R0 - F004-00516-D-R0
V-285 | Vbrain Notifier | The description of the astrain in Vbrain Notifier has been chenged as follow: - Systeme VMC; - Systeme API; - Systeme Infrastructures; - Systeme DVT; - Systeme Fluide VMC; - Systeme Clima; - Systeme Energie; | SW | NA | NA | NA | NA | VDC_21 V1.2 | VG-CP-SYS-1583-R0 - F004-00516-D-R0
V-286 | Pandora DI | New Signals relative to DI Pandora have been added | SW\VDC | NEW | RES | 11 | Pandora | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R0
V-287 | Pandora DI Master Alarms modify | SCK6DMA has been modify to be integrate the SCK8000DMA Pandora Master Alarm | SW\VDC | NA | NA | NA | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R1
V-288 | Pandora Energy | New Signals relative to Energy Pandora have been added | SW\VDC | NEW | FIL | 11 | Pandora | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R2
V-289 | Pandora new Energy node added | ESY8000DMA master alarm for Pandora Energy | SW\VDC | NEW | NA | NA | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R3
V-290 | Pandora HVAC | New Signals relative to HVAC Pandora have been added | SW\VDC | NEW | RES | 11 | Pandora | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R4
V-291 | Pandora HVAC Master Alarms modify | VZC6DMA has been modify to be integrate the VZC8001DMA Pandora Master Alarm | SW\VDC | NA | NA | NA | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R5
V-292 | Pandora VMC Master Alarms modify | VMC6DMA has been modify to be integrate the ZJP8001DMA Pandora Master Alarm | SW\VDC | NA | NA | NA | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R6
V-293 | Pandora Etat FE | New Signals relative to Pandora Etat FE have been added | SW\VDC | NEW | INT | 11 | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R7
V-294 | Switches Pandora | Changed the field High2 in ZCM6840P11 and ZCM6841P11 | SW\VDC | NA | NA | NA | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R7
V-295 | Switches Pandora | ZCM684041DMA TYPO IN SW. The description has been changed. | SW | NA | NA | NA | NA | VDC_21 V1.3 | VG-CP-0318-IPT-R0- F002-00518-D-R7
V-296 | Moyer Generaux (MG) | MG6DMA has been modify to be integrate the MG91DMA BIL Master Alarm | SW\VDC
| Master Alarms Modification | Typo in MG6DMA; MG61DMA has been added in VDC and ZZL6007 alarm has been added in DB | SW\VDC | NA | NA | NA | NA | VDC_22_v1.1
| Alarm on Lagrange and Pandora switch ports | For the following measures have been modified the alarm's condition: ZCM6734P1;ZCM6734P10;ZCM6735P1;ZCM6735P8;ZCM6735P10 | SW\VDC | NA | NA | NA | NA | VDC_22_v1.1

## SYNO
Synoptic | Subsystem | Description | FA REF. | VDC Version | VBrain Config Version | Checksum
E60 | ENE TGBT | Addition of a new synoptic in Energy TGBT S/s for PLC faults info visualization |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E72 | ENE 1D60 | Addition of new synoptic in Energy 1D60 S/s for PLC Faults info visualization |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
MG71 | Moyens Generaux (MG) | Animation correction for graphic elements. Modification of commands buttons. General synoptic layout modification |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC01 | HVAC | Addition of validity signals. Addition of Gantry/Bunker faults signals. Addition of Gantry/Bunker alarms of 1st and 2nd level (Serial Signals) General synoptic layout modification |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC04 | HVAC | Addition of Sanitation Fan Extractor |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC07 | HVAC | Addition of validity signals for "Communication Defaut" with AC equipments |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC08 | HVAC | Addition of validity signals for "Communication Defaut" with AC equipments |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC09 | HVAC | Addition of validity signals for "Communication Defaut" with AC equipments |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC12 | HVAC | Modification of commands buttons for Group Commands. General synoptic layout corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC15 | HVAC | Addition of "Pression Differentielle" analogic measurements (Hall d'Integration, Local 701 and Local 601) |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC17 | HVAC | Modification of commands buttons for Group Commands. General synoptic layout corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
HVAC18 | HVAC | Addition of validity signals for "Communication Defaut" with AC equipments |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E61 | ENE TGBT | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E62 | ENE TGBT | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E63 | ENE TGBT | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E64 | ENE TGBT | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E65 | ENE TGBT | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E68 | ENE 1D60 | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
E69 | ENE 1D60 | Bugs corrections |  | VDC 6.0 | VBRAIN_CONFIG_2020-09-25_14-21-43 | d7b7fa1054f0a89687eda3d68350495e
DG60 | DETG/DI | Addition of a new synoptic in DETG/DI subsystem for DETG/DI PLC fault info visualization |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
VG13 | WIRE | Addition of a new synoptic in "Process Fluide et Energie Gerneral (VG)" subsystem for Wire PLC fault info visualization |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
W60 | O&V | Addition of a new synoptic in"Optique et Video (W)" subsystem for O&V PLC fault info visualization |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
VMC03 | VMC | Modification of Syncere and SAAA interface with HLCS Server Master NTP Server information correction |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DG61 | DETG | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DG62 | DETG | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DG63 | DETG | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DG64 | DVT | Modification for DG60 and VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DG65 | DVT | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI61 | DETIN | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI61 | DETIN | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI63 | DETIN | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI64 | DETIN | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI65 | DETIN | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI70 | DETIN | Modification for DG60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
DI72 | DETIN | Modification for DG60 synoptic access Bugs corrections |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
EI66 | EXTIN | Modification for DG60 and CV0B HVAC synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
EI67 | EXTIN | Modification for DG60 and CV0B HVAC synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
EI68 | EXTIN | Modification for DG60 and CV0B HVAC synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
EI69 | EXTIN | Modification for DG60, VG13 and CV0G HVAC synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
EI71 | EXTIN | Modification for DG60 and CV0B HVAC synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
MG61 | MG | Modification for VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
MG62 | MG | Modification for VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
MG63 | MG | Modification for VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
MG64 | MG | Modification for VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
MG68 | MG | Modification for VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
VG01 | VG | Modification for VG13 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E66 | MG | Modification for E60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
Départ supplementaires | ENE TGBT | Modification for E60 synoptic access |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E72 | ENE 1D60 | French language corrections General synoptic layout correction |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E68 | ENE 1D60 | French language corrections Bug resolution over ETV6005D measure update |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E60 | ENE TGBT | French language corrections |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E61 | ENE TGBT | Corrections over Arrivée 7001, 7002, 7003 (open position is not an alarm anymore - CMY modification during FAT in Rome) French Language corrections Addition of browser button for E68 access General synoptic layout modifications after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E62 | ENE TGBT | Corrections over Arrivée 7950, 7951, 7952 (open position is not an alarm anymore - CMY modification during FAT in Rome) French Language corrections Addition of browser button for E69 access General synoptic layout modifications after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E63 | ENE TGBT | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E64 | ENE TGBT | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E65 | ENE TGBT | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
E70 | ENE TD (Bunker) | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC01 | HVAC | Addition of fault signals not included in HVAC SI French language corrections General synoptic layout modifications after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC02 | HVAC | General synoptic layout modification after CMY FAT in Rome Correction for bug resolution over VSY6900W2 update error |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC03 | HVAC | Addition of signals not included in HVAC SI Bug corrections General synoptic layout modifications after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC04 | HVAC | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC05 | HVAC | Corrections of errors in the equipments repère and Rooms numeration/names (CMY FAT in Rome) |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC06 | HVAC | Corrections of errors in the equipments repère and Rooms numeration/names (CMY FAT in Rome) |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC07 | HVAC | Remotion of signals related to VC n° 2 of Local 004 General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC08 | HVAC | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC09 | HVAC | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC10 | HVAC | Corrections of errors in the equipments repère and Rooms numeration/names (CMY FAT in Rome) |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC11 | HVAC | Corrections of errors in Rooms numeration/names (CMY FAT in Rome) Correction of bug related to commands |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC12 | HVAC | French languagescorrections General synoptic layout corrections after CMY FAT in Rome Addition of VVU6126M2 CR for Clim Interne Modification of Déclenchement and Rearmement commands (from single to parametric commands) |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC13 | HVAC | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC14 | HVAC | General synoptic layout modification after CMY FAT in Rome |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC15 | HVAC | Corrections of errors in the equipments repère and Rooms numeration/names (CMY FAT in Rome) |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC16 | HVAC | Corrections of errors in Rooms numeration/names (CMY FAT in Rome) Correction of bug related to commands |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC17 | HVAC | French languagescorrections General synoptic layout corrections after CMY FAT in Rome Addition of VVU6126M2 CR for Clim Interne Modification of Déclenchement and Rearmement commands (from single to parametric commands) |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC18 | HVAC | Bug 2618 corrections |  | VDC 7.0 | VBRAIN_CONFIG_2020-10-14_09-19-45 | 1d77bb54566791770ad2fae56aab1020
HVAC15 | HVAC | General layout modification to include ZZN6014 Wire PLC fault signal (validity of Pression Differentielle signals) |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E60 | ENE TGBT | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E61 | ENE TGBT | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E62 | ENE TGBT | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E63 | ENE TGBT | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E64 | ENE TGBT | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E65 | ENE TGBT | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E68 | ENE 1D60 | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E69 | ENE 1D60 | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
E72 | ENE 1D60 | General layout modification |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
MG71 | Moyens Generaux (MG) | Elimination of TANGARA signal (not acquired in VMC system) Graphic problems resolution |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
DG64 | Detection Vapeurs Toxiques (DVT) | Addition of new VEGA-C signals and modifications for CL8 detectors |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
DG65 | Detection Vapeurs Toxiques (DVT) | Modifications for CL8 detectors |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
Etat switch Bunker | VMC | Modification of bunker switch popup for addition of redundancy link in ports 21 and 23; |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
VG13 | Process Fluide et Energie VEGA (VG) | Addition of Watchdog and new fault signal of Wire PLC |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
SHM61MA | Structural Health Monitoring (SHM) | Design modification for anomalies correction (iFAT in Rome) |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
SHM61TC | Structural Health Monitoring (SHM) | Design modification for anomalies correction (iFAT in Rome) |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
W61 | Optical and Video (W) | General layout modification in projecteurs elements animation |  | VDC 8.0 | VBRAIN_CONFIG_2020-11-09_17-40-00 | 018250c446e63d96e05aee5108826cdf
NA | Lagrange S/S | Creation and addition of all new Lagrange Synoptic for the following S/s: - Gas Detection; - Fire Extinction and Detection; - Alert Replì/Alert Evacuation; - Energy; - Internal Diagnostic; - Smoke Extraction; - HVAC |  | VDC 9.0 | VBRAIN_CONFIG_2021-02-16_16-49-41 | 13690132fbaa7bd53bb937e3d66e2af7
NA | VMC Synoptic layout modification | Improvemement of all VMC synoptic visualization perfomances on Web Client |  | VDC 9.0 | VBRAIN_CONFIG_2021-02-16_16-49-41 | 13690132fbaa7bd53bb937e3d66e2af7
MG71 | Addition of group commands and layout modification | Addition of group commands dedicated to AE/AR ZLV and general layout modification |  | VDC 9.0 | VBRAIN_CONFIG_2021-02-16_16-49-41 | 13690132fbaa7bd53bb937e3d66e2af7
MG73 | New synoptic | Creation of a new synoptic containing signals reguarding Feux de signalisation Portique, previously contained in MG712 synoptic |  | VDC 9.0 | VBRAIN_CONFIG_2021-02-16_16-49-41 | 13690132fbaa7bd53bb937e3d66e2af7
CDL3 switch | Deletion | Elimination of CDL3 switch synoptic for CDL3 switch remotion |  | VDC 9.0 | VBRAIN_CONFIG_2021-02-16_16-49-41 | 13690132fbaa7bd53bb937e3d66e2af7
VMC02 | Modification for CDL3 impacts | Graphic modification of VMC02 synoptic for remotion of CDL3 switch |  | VDC 9.0 | VBRAIN_CONFIG_2021-02-16_16-49-41 | 13690132fbaa7bd53bb937e3d66e2af7
HVAC19 | Modification of Temperature Fault signals | Ggraphic modification of Temperature Fault signals for Lagrange VC of Room 013 in order to visualize ASCII code format signals |  | VDC 10 | VBRAIN_CONFIG_2021-03-30_10-13-42 | e977fb8b0adec1126f49555dd3d20428
MG72 | Deletion of SONO Commands | Elimination of SONO commands button from MG72 synoptic |  | VDC 10 | VBRAIN_CONFIG_2021-03-30_10-13-42 | e977fb8b0adec1126f49555dd3d20428
VMC05 | General layout modification | Graphic modification of Lagrange Internal Diagnostic synoptic in order to visualize information about Lagrange primary PLC |  | VDC 10 | VBRAIN_CONFIG_2021-03-30_10-13-42 | e977fb8b0adec1126f49555dd3d20428
VMC05 | General layout modification | Graphic modification of Lagrange Internal Diagnostic synoptic in order to visualize information about Lagrange primary and secundary PLC |  | VDC 11 | VBRAIN_CONFIG_2021-09-23_16-48-16 | 306f4b65a0c7c4f38eff4eafc299eb4b
VMC04 | Signals addition and deletion | Addition of new signals monitoring the stats of Vbrain Notifer_Commands for both HLCS server and deletion of the signals monitoring the Vbrain Supervisor applications |  | VDC 11 | VBRAIN_CONFIG_2021-09-23_16-48-16 | 306f4b65a0c7c4f38eff4eafc299eb4b
VMC01 | Signals addition | New signal to have knowledge of PLCs EAP Interfaces and a new command to manage Slave PLC reset has been added on the VMC01 synoptic |  | VDC 11 | VBRAIN_CONFIG_2021-09-23_16-48-16 | 306f4b65a0c7c4f38eff4eafc299eb4b
DI76 | Signals addition | Addition of new signals monitoring the Salle de repos 0014 - ZDA52 |  | VDC 12.0 | VBRAIN_CONFIG_2021-11-02_16-29-22 | 078e735a023a36ece882f3d7f242bf724f96a646
DI73 DI74 DI75 DI76 DI77 DI78 | Deletion of Lagrange signal | The alarm SCK7000DP has been removed from the synoptic. |  | VDC 12.1 | VBRAIN_CONFIG_2021-11-17_20-39-49 | be5ab34395827bfd5389fc40862abe3d0b98d712
DI76 | Deletion of Lagrange signals | The following alarm: SZI7152D SZI7152W SZI7153D SZI7153W SZI7154D SZI7154W has been removed from the synoptic. |  | VDC 12.1 | VBRAIN_CONFIG_2021-11-17_20-39-49 | be5ab34395827bfd5389fc40862abe3d0b98d712
VMC05 Lagrange FE Status | Deletion of Lagrange signals | LZR7007D2 LZL7000DW LZL7000A Changed of description of serial modules |  | VDC 12.2 | VBRAIN_CONFIG_2021-11-27
VMC02 Network VMC | Update syno | Update of syno |  | VDC 12.2 | VBRAIN_CONFIG_2021-11-27
02 Lagrange TD TGBT 184-13-20 CAT II | Delete syno | 02 Lagrange TD TGBT 184-13-20 CAT II |  | VDC 12.2 | VBRAIN_CONFIG_2021-11-27
01 Lagrange TD TGBT 184-13-20 CAT I II | Update syno | The 01 Lagrange TD TGBT 184-13-20 CAT I syno has been renamed as 01 Lagrange TD TGBT 184-13-20 CAT I II |  | VDC 12.2 | VBRAIN_CONFIG_2021-11-27
E74 Categories I II Lagrange | Update syno | E74 Categories I II Lagrange: Delete of 02 Lagrange TD TGBT 184-13-20 CAT II button |  | VDC 12.2 | VBRAIN_CONFIG_2021-11-27
E74 TD Lagrange | Update syno | Delete of 02 Lagrange TD TGBT 184-13-20 CAT II button |  | VDC 12.2 | VBRAIN_CONFIG_2021-11-27
DG71 | Update syno | Change the description inside synoptics | 3042;3043 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
DI73 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
DI74 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
DI75 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
DI76 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
DI77 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
DI78 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
E75 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
EI77 | Update syno | Change the description inside synoptics | 3042 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
SHM62MA | Update syno | Updated of the elemens grafics | 3045 | VDC 12.2 | VBRAIN_CONFIG_2022-01-18
MG71 | Update syno | Update of syno MG71 to insert the new signals and commands related to Tangara |  | VDC12.2 | VBRAIN_CONFIG_2022-01-18
DG60 Etat PLC DETG DI | Update syno | Update of syno DG60 Etat PLC DETG DI to insert the watchdog signal | 3048 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
W60 Etat PLC OeV | Update syno | Update of syno W60 Etat PLC OeV to insert the watchdog signal | 3048 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
DI65 | Update syno | Modification of the DI65 syno to modify the type of the following signals: SZI6093D SZI6094D SZI6095D | 3059 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
E74 Categories I II Lagrange | Update syno | Modification of the E74 Categories I II Lagrange syno to modify the type of the following signals: EQF7320N EQF7320R EQF7320C | 3077 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
E73 | Update syno | Modification of the E73 syno to modify the type of the following signals: EQF7530 EQF7531 EQF7232 | 3077 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
DI70 | Update syno | Change the description inside synoptic | 3065 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC12 | Update syno | The VVU6106M has been inserted inside HVAC12 syno | 3069 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
SHM synoptics | Update syno | Updated of the SHM synoptics to indicate that the max value of the inclinometer axis are transmitted to us as an absolute value. | 3079 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
06 TD2 1601-004-34 CAT IIIB | Update syno | title in 06 TD2 1601-004-34 CAT IIIB synoptic chenged | 3068 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
TDGA 1602 201 31 CAT IIIB | Update syno | title in TDGA 1602 201 31 CAT IIIB synoptic chenged | 3068 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
E75 | Modification syno | Delete Smoke extraction signals | 3083 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC23 Lagrange Commandes | Modification syno | Delete FERMETURE INCENDIE CTA FAN LAGRANGE SALLE 20 command | 3083 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC20 | Modification syno | Delete the following signals for VC 1 SALLE 6,8,11 and 12: ANTI-FREEZE MODE FAULT ELECTRIC HEATER FAULT CONDENSATE DISCHARGE FAULT FUSE FAULT | 3083 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC21 | Modification syno | Delete signals related to VC1, VC2, VC3, VC4 and VC5 SALLE 07 | 3083 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC19 | Modification syno | Delete signals related to VC1, VC2 SALLE 10 | 3083 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC03 | Modification syno | change direction of symbos |  | VDC12.2 | VBRAIN_CONFIG_2022-01-18
VG12 | Modification syno | CHANGE IN THE SIZE OF THE SYNOPTIC |  | VDC12.2 | VBRAIN_CONFIG_2022-01-18
E75 Smoke Extraction Lagrange | Modification syno | The E75 Smoke Extraction Lagrange synoptic has been changed. - closed status correspond to value true and within the synoptic only the text "damper closed" will be visualized - opened status correspond to false and on synoptic only the text "damper opened" will be visualized. | 3044 | VDC12.2 | VBRAIN_CONFIG_2022-01-18
HVAC20 | Modification syno | Delete “VC X SALLE XX USER INTERFACE FAULT” signal | 3088 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC21 | Modification syno | Delete “VC X SALLE XX USER INTERFACE FAULT” signal | 3088 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC19 | Modification syno | Delete “VC X SALLE XX USER INTERFACE FAULT” signal | 3088 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC12/HVAC17 | Modification syno | The following alarms have been added to the synoptics: HVAC 12: VSY6600W1 VSY6600W2 HVAC17: VSY6900W1 VSY6900W2 | 3089 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E70 TD Bunker | Modification name of the nodes | All nodes within E70 TD Bunker have been renamed from HMI configuration | 3091 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E67 TD Mobile Gantry | Modification Syno | Modification of the synoptics consequently the task 3092 | 3092 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E70 TD Bunker | Modification Syno | Modification of the synoptics consequently the task 3092 | 3092 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC19/20/21 | Modification Syno | Modification of description from Default Temp. to User Interface/Sonde Temperature Fault | 3088 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E71/E75 | Modification Syno | Description of smoke estraction signals to be modified: Fan Motor Circuit Status ON/OFF -->ON Fan Motor Circuit Breaker ON/OFF -->ON Low Pressure detector --> Désenfumage en marche Low pressure detector ON/OFF --> cambiare in "Extracteur in Marche" | 3114 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
MG73 | Modification syno | On Synoptic MG73 currently the status of all traffic lights is visualized by the square colored in agreement with the light status. | 3101 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E62 | Modification syno | Syno E62: Graphic layout of command EQF6951C has been changed. The "local" and "remote" texts are dinamic | 3105 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E61 | Modification syno | Graphic layout of command EQF6002CM has been changed. The "local" and "remote" texts are dinamic |  | VDC12.2 | VBRAIN_CONFIG_2022-01-18
E63/E70 | Modification syno | E63: Synoptic layout changed in agreement with technical specification and from E70 the signs indicated in the "symptom" column have been removed. | 3105 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E68/E69/E70 | Modification syno | E69 and E68: - the following signals have been removed: EQT6001f; EQT6002F - ETV6005D is duplicated, has been removed the signal represented with a a dot E70 and E68: circuit breaker description to be removed from OF/SD signals box | 3105 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | For all analizators of Bunker, Gantry and Lagrange the unit of meaures of Apparent Power has been changed to kVA | 3150 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC 07 | Modification syno | Remove the following signals from LOCAL 002 and insert the new signals: from VTR6002V1 to VTR6002V3 from VVV6002M1 to VVV6002M3 from VVV6002DT1 to VVV6002DT3 | 3115 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC 09 | Modification syno | Remove the following signals from LOCAL 1222 and insert the new signals in the local 121: from VTR6122V2 to VTR6121V2 from VVV6122M2 to VVV6121M2 from VVV6122DT2 to VVV6121DT2 | 3115 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC 18 | Modification syno | Change the description of the Local 601 to Local 801 and change the following signals: from VTR6601V1 to VTR6801V1 from VVV6601DT1 to VVV6801DT1 from VVV6601M1 to VVV6801M1 | 3115 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
TD AXIMA 1602-401-002 cat IIIA TD AXIMA 1602-401-002 cat IIIB | Modification syno | The following signs have been removed from the synoptic: EIR6702AI2 EIR6702AI3 EIR6702A EIR6702BI2 EIR6702BI3 EIR6702B EUR6702A12 EUR6702A23 EUR6702A31 EUR6702AV2 EUR6702AV3 EUR6702B12 EUR6702B23 EUR6702B31 EUR6702BV2 EUR6702BV3 | 3063 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC12 Bunker Commandes et Configuration | Modification syno | the graphic element related to the vvu6106d signal has been changed |  | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC 23 | Modification syno | Has been changed the following objects: description "Etat CTA" signal:VCT7020D | 3109 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
DG65 | Modification syno | The color property of the sdu6041w signal has been changed |  | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
VMC03 | Modification syno | Modification of the "Syncer" text |  | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
MG72/MG71 | Modification syno | MG72:has been modified the synoptic label in agreement to signal descrptions for the following signals: sce7005d, sce7006 (Alert Evac PRS) MG71: "Feux presence lanceur" has been modified in "Access controle" | 3108 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | The "PANEL" folder and "SVG" folder have been update and have been removed the panel and .svg that didn't use. |  | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | The name of the node TD 184 05 32 CAT II III has been replaced with TD 184 13 32 CAT II III. The name of the node TD TGBT 184-13-20 CAT II III has been replaced with TGBT 184 13 32 CAT II III. | 3113 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC16/HVAC11/HVAC 15/HVAC05/HVAC06 | Modification syno | For the depollution commands on MG (601, 701, hall integration) the "OVERTURE VOLET"command label has been modified with the text "MARCHE" For room 701 and 601 "FUITE N2O4/UDMH" to be modified in "DEPOLLUTION" The description of all commands related to "Depollution et extintion N2" has been been modified with the text "Ouverture/Fermeture". Insertion of a "browser" button to open panels "CTA bunker" (synoptics:HVAC05, HVAC06) and "CTA Annex" and "CTA Hall d'ntegration" (syno:HVAC15). Put in descending order the commands shown in the HVAC 16 synoptic consistently with the signals shown in the HVAC 15 synoptic. Wrong descriprion inside HVAC 11: REZ-DE-CHAUSSE | 3121 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | the nodes of the following synoptics have been associated with the following master alarms: DETG Lagrange (group) EXTIN Lagranger (Group) Infos MX Disjoncteurs (E61 popup) DG71DMA EI77DMA EZC6115K3 | 3132 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
MG71/MG75 | Modification syno | The graphic symbol relating to the "Normal" state of the traffic lights was not linked to the correct variable. The signals are: SFE6050D, SFE6040D,SFE6030D,SFE6020D, SFE6010D Modify the synoptic making it congruent with the levels of the mobile gantry, from the highest to the lowest. The default state of the zlv barriers, if active, causes the graphic symbol to turn red | 3129 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | Has been update as follows: VG13 has been renamed as VG 10 ETAT WIRE API VG12 has been renamed as E66 Eclairage Ambiance Lanceur E66 has been renamed as MG74 Niveau Chateau eau VEGA. To be modify the name of the nodes, the name of the .svg files and the title inside the synoptics. All panels that were not used were removed from RTS\PROJECT\VMC_VBRAIN\DATA_DESIGN\CONFIG\WEB\SVG and RTS\PROJECT\VMC_VBRAIN\DATA_DESIGN\CONFIG\WEB\PANEL | 3135 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | SHM nodes of the synoptics have been renamed as follows: SHM 60 SHM Activation SHM61TC Travelling Crane 1 SHM62TC Travelling Crane 2 SHM61TMS Translation Monitoring System SHM61MA Mast Capteurs 1 SHM62MA Mast Capteurs 2 SHM61BU Massif Capteurs 1 SHM62BU Massif Capteurs 2 SHM63BU Massif Capteurs 3 SHM61MG Portique 14.400 – 18.400 SHM62MG Portique 21.200 – 26.600 SHM63MG Portique 24.000 – 29.200 – 37.000 SHM64MG Portique 31.800 – 39.600 SHM65MG Portique 42.200 – 47.400 SHM66MG Portique 50.000 – 54.000 SHM67MG Portique 54.000 SHM68MG Portique Pression Cossway Smoke extraction nodes of the synoptics have been renamed as follows: E71 Désenfumage ZLV E75 Désenfumage Lagrange | 3136 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
HVAC11/HVAC16 | Modification syno | To be insert inside the HVAC 11 and HVAC 16 the relative signals of "InertageN2" ,"Depollution" and "Balayage" of the commands present in the synoptics. | 3139 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E71 | Modification syno | The synoptic has been modified according to task 3138 | 3138 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
DG64 | Modification syno | Following the tests, the synoptic was modified as follows: SOR6024: chenged the unit measure (from ppm to ppb) SOR6023: moved in the coiffe section SOR6022: moved in the coiffe section SOR6011: moved in the remplissage avum section | 3140 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
DG60 | Modification syno | Inserted to Watchdog Timeout signal | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
W60 | Modification syno | Inserted to Watchdog Timeout signal | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
VG10 | Modification syno | Inserted to Watchdog Timeout signal | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E60 | Modification syno | Inserted to Watchdog Timeout signal | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
E72 | Modification syno | Inserted to Watchdog Timeout signal | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
CV0B X80 HVAC Bunker PLC | Modification syno | Inserted to Watchdog Timeout signals | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
CV0B X80 HVAC Gantry PLC | Modification syno | Inserted to Watchdog Timeout signals | 3142 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
DI: 73/74/75/76/77/78 | Modification syno | The descriptions of the alarms inside the "etat detection incendie" have been modified. | 3146 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
VG13/VG12/MG74 | Synoptics renamed | VG13 has been renamed as VG 12 ETAT WIRE API VG12 has been renamed as E66 Eclairage Ambiance Lanceur E66 has been renamed as MG74 Niveau Chateau eau VEGA. Has been modified the name of the nodes, the name of the .svg files and the title inside the synoptics. | 3135 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
VG06/VG08/VG07/VG08/VG09/VG11/VG12 | Synoptics renamed | VG06 AND VG08 synoptics have been deleted. The number of nodes has been updated and also the associated master alarms. Renamed the title inside the panels. For this reasons the following synoptics have been reneamed: VG07 has been renamed as VG06; VG08 has been renamed as VG07; VG09 has been renamed as VG08; VG11 has been renamed as VG09; VG12 has been renamed as VG10; | 3137 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification syno | The Following Synoptics Have Been Changed In Accordance With Sauvegarde: DG71 HVAC16 DI63 DI70 DI73 DI74 DI75 DI76 DI77 DI78 DI71 MG71 MG62 MG65 MG66 MG67 MG68 MG74 DI73 | 3160 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
| Modification Name Node | The Following Node Synoptics on Configuration Have Been Changed In Accordance With Sauvegarde: EI66 EI67 DI61 DI62 | 3160 | VDC_13 | VBRAIN_CONFIG_2022-03-10_20-45-35 | e7da32e77e481756211ed853635e6086
VG07 | Modification of the Description | The description "TGBT CAT. III A" was changed to "TGBT CAT. III B" | 3178 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
MG61,MG62,MG63,MG64,MG68,MG74 | Modification syno | The following synoptics have been modified, the default synthese alarm has been replaced with the single default alarm signal of the PLC. MG61,MG62,MG63,MG64,MG68,MG74 | 3178 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
MG61,MG62,MG63,MG68,VG10 | Modification syno | In the following synoptics, the ZZE6009 signal has been replaced with ZZE6010: MG61,MG62,MG63,MG68,VG10 | 3168 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
HVAC15 | Modification syno | Changing of the color of the symbols relating to the following signals when they are active: VZU6601D VZN6701D | 3169 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
DG71 | Modification syno | The measurement unit of the following measurements has been changed. They correspond to the oxygen level (%): SOR7001;SOR7002;SOR7003;SOR7004 | 3170 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
VM03 | Modification syno | VMC03 has been modified: SYNCER has been replaced with SCSI | 3179 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
HVAC | Modification syno | From the following synoptics have been removed the VSY6600W1, VSY6600W2, VSY6900W1 and VSY6900W2 alarms: HVAC03;Details Groupes Froids;HVAC04;HVAC05;HVAC06;HVAC07;HVAC08;HVAC09;HVAC10;HVAC11;HVAC12;HVAC13;HVAC14;HVAC15;HVAC16;HVAC17;HVAC18;VG09 | 3175 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
Lagrange switch | Modification syno | The Lagrange switch synoptic has been modified: has been inserted the for the Port. N2, the (Groupe électrogène) description. | 3176 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
Extin Bunker | Modification syno | In the following synoptics have been removed the Synthese Default PLC alarms: DI66:DG60DMA_MasterAlarm DI67:DG60DMA_MasterAlarm DI68:DG60DMA_MasterAlarm DI69:DG60DMA_MasterAlarm and VG10DMA_MasterAlarm DI71:DG60DMA_MasterAlarm | 3178 | VDC_14 | d7e4cda9b975fc1c2b7013db3120ce60
VG09 | Modification syno | The title of the VG09 syno has been changed. | 3169 | VDC_15.0 | WEB_20220430.zip | dbc3836887c8d06bfa84b7b6793bb43d
GE01 | Addition new syno | The GE01 synoptic has been inserted (node:Energy Lagange). | 3167 | VDC_15.0 | WEB_20220430.zip | dbc3836887c8d06bfa84b7b6793bb43d
HVAC16 | Modification syno | Changing of the color of the symbols relating to the following signals when they are active: VZU6601D VZN6701D | 3169 | VDC_15.0 | WEB_20220430.zip | dbc3836887c8d06bfa84b7b6793bb43d
GE01 | Modification syno | Modification of GE01 SYNPOTIC | 3167
GE01 | Modification syno | The GE01 synoptic has been changed after the test performed to Kourou. | 3167 | VDC_15.1 | WEB_20220519.zip | e2401121db146aeb82c6228488ffa7b3
E61 | Modification syno | Deleting "Synthese Defaut MX disjonteurs" object | 3173 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
E64 | Modification syno | Wrong txt inside the EUL6076DMA_MsterAlarm object "Synthese Defaut UL7005" -> "Synthese Defaut UL7006" | 3173 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
VG07 | Modification syno | Wrong txt: "TGBT CAT. (013/004/103)" --> "TGBT CAT. (013/004/103/002)" | 3173 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
VG09 | Modification syno | Deleting the following measures from the VG09 synoptic: ESY6930W;ESY6931W;ESY6940W;ESY6941W;ESY6950W;ESY6951W;ESY6960W;ESY6961W | 3174 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
VG09;E67 | Modification syno | Deleting the following measures from the synoptics: VG09;E67 ESY6970D;ESY6980D | 3174 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
MG65/VG04 | Modification syno | Correction of the units of measure for the following measures: 1) OOR6301: Remove the "%" symbol from the text box 2) ONR6302 : Remove the "%" symbol from the text box and replace it with "m" 3) ONR6301 :Remove the "%" symbol from the text box and replace it with "m" 4) ONR6355: Increased size of the relative discrepancy symbol | 3174 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
DG64 | Modification syno | Update of the syno DG64 as indicated by the sauvegarde | 3176 | VDC_16 | WEB_20220715.zip | A4A10C0E998C5AC8127FBF5CFF7CFD21
DG65 | Modification syno | DG65 synoptic update in according to VG-CP-SYS-1274-R0 - F044-00504-R1: SAV6107D, SAV6107M,SDU6042D,SDU6042W ,SDU6043D,SDU6043W,SOR6107 SOR6207 have been delated. |  | VDC_17.1 | WEB_20230126.zip | 2eb8d6b57f6f15ecfacd14bc02a18a9d
DG62/MG71/MG73 | Description changes | Only some descriptions within the synoptics have been changed as per AVIO Sauvegarde Remarks |  | VDC_17.1 | WEB_20230126.zip | 2eb8d6b57f6f15ecfacd14bc02a18a9d
MG71 | Description changes | Only the description of the button related to the SCE6011CM command has been changed as per AVIO Sauvegarde Remarks |  | VDC_17.2 | WEB_20230127.zip | 648C34EA73E94E0F7B70761679713C85
WIS | Creation WIS synoptics | Creation WIS synoptics |  | VDC_18 V1.0 | WEB_20230626.zip | A87DBE155FCE991AB34F0D6EDAB66EDB
VMC01 | Modification syno | VMC01 layout has been modified and has been added the VMC10-WIS node |  | VDC_18 V1.0 | WEB_20230626.zip | A87DBE155FCE991AB34F0D6EDAB66EDB
VMC10 | Creation VMC10 synoptic | VMC10 - WIS synoptic has been added |  | VDC_18 V1.0 | WEB_20230626.zip | A87DBE155FCE991AB34F0D6EDAB66EDB
WIS04,WIS07 | Modification syno | Wrong TXT : WIS04: CARNEAU OUST COTE OPR 6407->CARNEAU OUEST COTE OPR 6407 WIS07:H0 TRIGGER REDONDANT->H0 TRIGGER REDUNDANT |  | VDC_18 V1.0.1 | WEB_20230711.zip | 02950F966302E72C6168E752115355EA
WIS07 | Modification syno | WIS sequence automatic countdown measure has been added: ZZC6003M | TASK 12 | VDC_18 V1.1 | WEB_20230714.zip | B3F816AC8AD4A2B3640422E57D7516D8
WIS01/WIS02/WIS03/WIS05 | Modification syno | "Interface EAU ZLV" and "Interface AIR ZLV" texts have been replaced with Browser popus |  | VDC_18 V1.1 | WEB_20230714.zip | B3F816AC8AD4A2B3640422E57D7516D8
WIS03/WIS04/WIS05/WIS06 | Modification syno | Modified text from bar to barg | WIS-014 | VDC_18 V.1.2 | WEB_20231016.zip | F22F21CAD45E21B60F8F70B17030521D
WIS03/WIS05 | Modification syno | TEXT of OPR6401 and OPR6404 in not visible |  | VDC_19 V.1.0 | WEB_20240312.zip | 9C81679AB5A0BFB27E5BC66BCDDA8942
WIS07 | Modification syno | The following description must been modifed: Syno WIS07 : ETAT CHRONOLOGIE --> ETAT EN CHRONOLOGIE o WIS BONNE ETAT --> o WIS BON ETAT DECOMPTE EN COURSE --> DECOMPTE EN COURS |  | VDC_19 V.1.0 | WEB_20240312.zip | 9C81679AB5A0BFB27E5BC66BCDDA8942
VMC01 | Modification syno | The following description must been modifed: • Syno VMC01 : INFOS EC1 à INFOS EC10 --> ETAT DES MODULES DE LA CHAINE .... |  | VDC_19 V.1.0 | WEB_20240312.zip | 9C81679AB5A0BFB27E5BC66BCDDA8942
MG71 | Modification syno | The following description must been modifed: 1) SIRENE ZLV -> SIRENE TOIT PORTIQUE; 2)CENTRALE ALERTE EVACUATION -> ALERTE EVACUATION PORTIQUE/LAGRANGE/HA 3)CENTRALE ALERTE REPLI -> ALERTE REPLI PORTIQUE/LAGRANGE/HA 4)Arret Alerte Replì -> ARRET Alerte Replì LAGRANGE et HA; 5)Marche AR et SONO -> MARCHE Alerte Replì; 6) Arret AR et SONO -> ARRET Alerte Replì | SV23-281 | VDC_20 V.1.0 | WEB_20240704.zip | c318e62e2117229730201cae769156e4
DI65 | Modification syno | The following description must been modifed: 1) OF - LOCAL 701 - ZONE 95 -> SDF-LOCAL 701 -ZONE 95 2) OF-LOCAL 601 - ZONA 94 -> SDF-LOCAL 601 -ZONE 94 | SV23-281 | VDC_20 V.1.0 | WEB_20240704.zip | c318e62e2117229730201cae769156e4
DI79 | Addition new syno | For DI79 DI Newton, has been created a new node on VBrain HMI Configuration and a new synoptic | VG-CT-2-D-0008-FA | VDC_21 V.1.1 | FAT: WEB_20250519.zip; OSAT:WEB_20250826.zip | FAT: 4049156066aa5f722fcf665ca5616480 OSAT: 1FB58AA97009AD2C5AA12FB6F04B9715
LAGRANGE SWITCH | VMC | Enabling ports for the ALERT Duty Call network | ALERT DutyCall Installation | VDC_21 V.1.2 | WEB_202060203.zip | 156A93339863F210BBC8A65CB1A86285
PANDORA SWITCH | VMC | Enabling ports for the ALERT Duty Call network | ALERT DutyCall Installation | VDC_21 V.1.2 | WEB_202060203.zip | 156A93339863F210BBC8A65CB1A86285
VMC03 ETAT INTERFACE | VMC | Modification for SAAA comunication | ALERT DutyCall Installation | VDC_21 V.1.2 | WEB_202060203.zip | 156A93339863F210BBC8A65CB1A86285
E61-E62 | Energy | Typo in description |  | VDC_21 V.1.2 | WEB_202060203.zip | 156A93339863F210BBC8A65CB1A86285
DI80-DI86 | Addition new syno | New nods and new synoptics have been added to Pandora DI signals | VG-CP-0318-IPT-R0- F002-00518-D-R7 | VDC_21 V.1.3 | WEB_20260330.zip | B316D1167EADC58EF4898C447452717F
E80 | Addition new syno | New nods and new synoptics have been added to Pandora Energy signals | VG-CP-0318-IPT-R0- F002-00518-D-R7 | VDC_21 V.1.3 | WEB_20260330.zip | B316D1167EADC58EF4898C447452717F
HVAC24 | Addition new syno | New nods and new synoptics have been added to Pandora HVAC signals | VG-CP-0318-IPT-R0- F002-00518-D-R7 | VDC_21 V.1.3 | WEB_20260330.zip | B316D1167EADC58EF4898C447452717F
VMC06 Etat Pandora Front End | Addition new syno | New nods and new synoptics have been added to Pandora VMC signals | VG-CP-0318-IPT-R0- F002-00518-D-R7 | VDC_21 V.1.3 | WEB_20260330.zip | B316D1167EADC58EF4898C447452717F
PANDORA SWITCH | VMC | Enabling ports for the PLC PANDORA | VG-CP-0318-IPT-R0- F002-00518-D-R7 | VDC_21 V.1.3 | WEB_20260330.zip | B316D1167EADC58EF4898C447452717F
E61-E62 | E | TYPO in the description of "Synthese Default TM7004", "Synthese Default TM7001", "Synthese Default TM7003" |  | VDC_22_v1.1
Lagrange switch | Lagrange switch | Port.Nr1 -> Conf.Serv has been removed; Port Nr.8 has been dedicated to LALHWS and Port.Nr10 has been dedicated to modem and Port Nr.12 has been dedicated to LALWS |  | VDC_22_v1.1

## STATISTICS
|  | VDC_21 | GRWTH +50% | REQUIRED SPARE | SPARE | LGRNG PLC SPARE
| RES | 4248 | 6373 | 2125 | 1178 | DI | 42
| FIL | 894 | 1342 | 448 | 591 | DO | 20
| TIP | 528 | 793 | 265 | 1200 | AI
| TOTAL | 5670 | 8508 | 2838 | 2969 | TOT FIL | 62
| CAL | 848 | 1273 | 425
| INT | 663 | 995 | 332
| TOTAL | 7181 | 10776 | 3595 | 2969
|  | VDC_5 | SPARE
FIL | CR | 404 | 329 |  | 564
FIL | CT | 175.5 | 100.5
FIL | MA | 56
|  | 635.5 | 429.5